- PURCHASE SPECIFICATION

- FOR

- GENERAL ELECTRIC PG 7121(EA)

GAS TURBINE GENERATOR

Enron North America

Blue Dog Max

September 28, 2025

- Revision  - 0.1

Issued By:

Approved By:

- SPECIFICATION

GAS TURBINE GENERATOR

- TABLE OF CONTENTS

1.	General	4

2.	Work Included Under These Specifications	4

3.	Miscellaneous Materials and Services	5

4.	Work Not Included Under These Specifications	6

5.	Recommended Spare Parts	6

6.	Climatic Conditions	6

7.	Gas Turbine Generator Data Sheets	6

8.	Code Requirements	7

9.	Factory Assembly	8

10.	Coating and Surface Protection	8

11.	Tools	8

12.	Alignment and Balance	8

13.	Noise Level	9

14.	Piping	9

15.	Equipment Cooling Water	9

16.	Electrical	9

17.	Equipment and Structures Seismic Design	10

18.	Wind Design	10

19.	Fuels and Auxiliaries	10

20.	NOX Control Injection	10

21.	Lubrication	10

22.	Cooling Systems	11

23.	Starting System	11

24.	Compressor Wash System	11

25.	Fire Detection and Protection	11

26.	Inlet Air Filtration Equipment	12

27.	Gas Turbine Generator Control Systems	12

28.	Additional Generator Equipment	15

29.	Generator	17

30.	DATA SHEETS	18

- SPECIFICATION

- GAS TURBINE GENERATOR FOR PEAKING PLANT

# 1.	General

This section provides the general description, scope of the work, and supplementary requirements for equipment, materials, and services included for a gas turbine generator system.

In general, American standard specifications are quoted throughout the Contract documents, but alternative internationally recognized standards may be substituted if approved in writing by Purchaser.  Seller shall submit to Purchaser a detailed listing and description of the codes and standards, which the equipment will meet (Exhibit B-1 fulfills this requirement), and for which substitution is being requested.

# 2.	Work Included Under These Specifications

The work under these specifications shall include furnishing a gas turbine generator and providing miscellaneous materials and services complete as a stand alone electrical power generating facility.

All equipment, materials and services required for a complete gas turbine and generator unit shall be furnished, except as specified otherwise in these specifications.  The equipment and materials to be furnished shall include, but not necessarily be limited to, the following major items:

- Enclosed Gas Turbine

- Enclosed Packaged Generator

- Generator Lifting Attachments

- Enclosed Control Cabinet/Packaged Electric and Electronic Control Compartment (PEECC)

- EX-2000 Exciter and Voltage Regulator

- Generator Air Cooling System

- Generator Protective Relays And Metering System

- Instrumentation And Controls

- Lube Oil Unit (Complete With Pumps And Heat Exchanger) and Hydraulic System

- Dry Low NOx Combustion System For Natural Gas Fuel:  Natural Gas: 9 ppmvd NOx @ 15% O2

- Fuel Metering  System

- Inlet Air Filter, Inlet Ducting, Silencing (Stainless Steel Perforated Sheet) and Supports

- Optional provisions for inlet chilling and inlet system with coatings and materials for high humidity environments

- Turbine Exhaust Plenum Expansion Joint (right hand), and enclosure

- On-Line and Off-Line Compressor Water Wash System

- One (1) Off-Base Water Wash Skid (One per site)

- Provisions for customer supplied open cooling system

- Electric Motor Starting System

- Rotor Turning System

- Gas Turbine Mark V ™ Control System

- Peak Firing Capability

- AC Electrical Motor Control Center(s) Mounted in PEECC

- Battery And Dual 100% Chargers

- DC Electrical Motor Control Center(s) mounted in PEECC

- Fire Detection and CO2  Supply Systems

- Seller’s Standard Installation Maintenance Tools Set (One (1) per site)

Seller shall provide drawings and other engineering data; Seller's field services, instruction manuals, recommended spare parts list, and miscellaneous materials and services, and shall participate in design conferences, as required.

# 3.	Miscellaneous Materials and Services

Miscellaneous materials and services not otherwise specifically called for shall be furnished by Seller in accordance with the following:

- Piping integral to major rotating equipment compartments furnished under these purchase specifications, except as otherwise specified.

- Connections for the Purchaser's piping and instruments.

- Seller’s standard scope of supply for instrument, power and control wiring, and raceways integral to any equipment furnished under these specifications.  This shall include terminal blocks and internal wiring to these terminal blocks for equipment requiring external connection.

- Coupling guards for all couplings.

- Instruction book including drawings prints information, instructions, and other data in Vendor standard electronic or hard copy format.

- Detailed storage requirements and lubrication requirements (including frequencies) for use by the Purchaser's erection contractor.

- Inventory at the Delivery Point, as defined in the Purchase Contract.

- Operating and Maintenance manuals.

- Commissioning requirements including Seller’s function tests.

- Technical Direction of Installation (TDI).

- Gas turbine control interfaces to plant Control System, (PLC based).

# 4.	Work Not Included Under These Specifications

The following items of work will be furnished or caused to be furnished by Purchaser:

- Flashing between major compartment by others.

- Field erection of all equipment at the site.

- Motor controls and starters not otherwise specified to be furnished under these purchase specifications.

- Foundations including embedments.

- Grouting materials and the placing thereof.

- Permanent electric wiring to connect equipment terminal boxes to the plant electrical system.  Interconnection of off-base components.

- Lubricants and fuels for operation.

- Solvents and cleaning materials.

- Finish painting of all equipment except as specified herein.

- Operating personnel for start-up and tests.

- Interconnecting piping between rotating equipment skids and off-base equipment.

- Private Field office for four (4) people with HVAC equipment including suitable furnishings, sanitation facility, electrical outlets, four (4) direct telephone lines which seller will pay phone bill, for the Seller’s technical service representatives.

# 5.	Recommended Spare Parts

Seller shall provide one priced list of spare parts for each of the standard inspection requirements.

# 6.	Climatic Conditions

The gas turbine generator shall be designed for base load operation under ambient temperatures of 0°F to 102°F. (For Design Basis Conditions, see Exhibit A of the Agreement).

# 7.	Gas Turbine Generator Data Sheets

Data sheets for the gas turbine generator are attached at the end of this specification. They describe equipment performance and data.

# 8.	Code Requirements

Gas turbine generators and auxiliary equipment shall be designed and constructed at a minimum in accordance with the requirements of the codes and standards listed below, except where modified or supplemented by these specifications (Exhibit B-1); and in accordance with the applicable requirements of the US Federal "Occupational Safety and Health Standards."

| ABMA | The American Bearing Manufacturers Association. |
| --- | --- |
| AGMA | American Gear Manufacturers Association |
| AISC | American Institute of Steel Construction |
| AISI | American Iron and Steel Institute |
| ANSI | American National Standards Institute |
| ASME | American Society of Mechanical Engineers, including ASME PTC-22, Performance Test Code for Gas Turbines and ASME B133.1 through B133.12, Procurement Standards for Gas Turbines |
| ASTM | American Society for Testing and Materials |
| AWS | American Welding Society |
| HEI | Heat Exchange Institute |
| HI | Hydraulic Institute |
| IEEE | Institute of Electrical and Electronics Engineers |
| ISA | Instrument Society of America |
| NEC | National Electrical Code |
| NEMA | National Electrical Manufacturers Association |
| NFPA | National Fire Protection Association |
| PFI | Pipe Fabrication Institute |
| SSPC | Steel Structures Painting Council |
| TEMA | Tubular Heat Exchanger Manufacturers Association, including TEMA Standards for Class "C" Heat Exchangers |
| SBC | Standard Building Code |
| UBC | Uniform Building Code |
| UL | Underwriters Laboratories, Inc. |

Use of alternate codes and standards that deviate from those listed above will not be allowed unless such code and standard deviations are identified by Seller and accepted by Purchaser, and are equal to or more stringent than those listed above.  When there is a conflict, the more stringent shall apply.

# 9.	Factory Assembly

Unless otherwise stated in Exhibit B-1, equipment shall be shipped completely factory assembled, except when the physical size, arrangement or configuration of the equipment, or shipping and handling limitations make the shipment of completely assembled equipment impractical.

# 10.	Coating and Surface Protection

## 10.1.	Shop Coating

A prime coating system that is suitable for the environment present at the site of installation shall be applied in the shop to ferrous metal surfaces of equipment and materials.

## 10.2.	Electrical Equipment

Electrical equipment, including panels, switchgear, transformers, and motors shall be finish painted.  Interior and exterior surfaces shall be the manufacturer's standard color, unless otherwise noted.

## 10.3.	Structural Steel and Miscellaneous Metals

Structural steel and miscellaneous metals include items fabricated of carbon steel such as plates, shapes, ladders, handrail, stair stringers, ducts, hangers, equipment, pipe supports, and similar fabrications, and shall be coated with a primer or galvanized suitable for the environment present at the site of installation as agreed by the parties.

# 11.	Tools

Seller shall furnish and ship one set of special tools as described in Exhibit B-1.

# 12.	Alignment and Balance

Rotating parts shall be true and dynamically balanced on an individual basis as well as an assembled basis.  Rotating equipment shall be balanced at the factory on an individual basis as well as a packaged system.

The gas turbine shall be balanced at slow speed using a multi-plane process. Gas turbine installed and operating vibration criteria is 0.5 inch/sec (alarm) and 1.0 inch/sec (trip).

The generator installed and operating vibration levels shall not exceed 2 mils peak-to-peak (Overall).  Excessive levels of vibration shall be corrected before acceptance.

# 13.	Noise Level

See Section 10.6 of the Agreement.

# 14.	Piping

Piping will be designed per the requirements of ASME B31.3.

# 15.	Equipment Cooling Water

Open cycle cooling water (via purchaser supplied cooling water system) will be used for cooling bearings, drives, and other equipment.

# 16.	Electrical

## 16.1.	Control Power

Electrical power for control and instrumentation will be a nominal 125-volt direct current.  Seller shall provide any devices required for proper operation and protection of the equipment during electrical power supply and ambient temperature fluctuations described in the following paragraphs.

## 16.2.	Auxiliary Power

Auxiliary equipment, such as motors, transformers, and rectifiers, requiring electrical power shall be designed to operate from one of the nominal electrical power sources as follows:

| Volts | Phase | Hertz |
| --- | --- | --- |
| 4160 | 3 | 60 |
| 480 | 3 | 60 |
| 120/240 | 1 | 60 |
| 120/208 | 3 | 60 |
| 125 | DC | N/A |

Alternating current motor voltage ratings with relation to horsepower shall be in accordance with the following except as noted on the on-line diagram:

| Horsepower | Volts | Phase |
| --- | --- | --- |
| Less than 1.0 | 115 | 1 |
| 1.0 through 200 | 460 | 3 |
| 250 and above | 4000 | 3 |
| DC motors | 110 | DC |

Emergency motors shall be designed to operate from a nominal 125-volt DC supply.  Direct current motors shall be capable of continuous operation at any terminal voltage from 105 to 139 volts DC.

Variations from motor design voltages specified must be acceptable to Purchaser.

## 16.3.	Motor Control

Seller-furnished starters and breakers shall be furnished for all seller supplied motors rated at 480 volts and below.

## 16.4.	DC System

Each GTG package shall include a complete 125-v DC system comprising of:

- Two 100% capacity battery chargers

- 125-v DC battery

- DC motor control center

The battery shall be sized to operate GTG auxiliary loads from start-up through shutdown and cooldown cycle.  The MCC shall have 10% spare capacity (ampacity) and 10% spare space (empty cubicles).

# 17.	Equipment and Structures Seismic Design

Equipment and structures shall be designed to resist the seismic forces prescribed in UBC Seismic Zone 2A.

# 18.	Wind Design

Equipment, structures, piping, etc. shall be designed to resist the wind effects determined in accordance with the UBC.

The Basic Wind Speed shall be 100 mph.

# 19.	Fuels and Auxiliaries

The gas turbines will be fired on natural gas.  See Exhibit A-1 of the Agreement for the analysis of the natural gas fuel.

# 20.	NOX Control Injection

Seller shall provide a DLN combustion system capable of burning natural gas without the use of water or steam injection to control NOx emissions to those limits defined in the Data Sheets.

# 21.	Lubrication

The lubrication of each turbine, generator, and exciter (if required) shall be accomplished by a continuous flow of oil supplied by common lubrication systems consisting of, but not limited to, a main oil circulating pump (100% capacity), auxiliary AC motor driven oil pump (100% capacity), emergency DC motor driven oil pump, supply and return piping, reservoir, filters, strainers, oil cooler, pressure gauges and thermometers, and necessary on-base oil piping.

Oil coolers shall be liquid cooled (water) by shell and tube or plate and frame type heat exchangers.

Liquid coolers shall employ a dual system; each oil cooler shall have sufficient capacity to cool the entire oil supply to the machine over the complete operating range of the gas turbine generator at site conditions

# 22.	Cooling Systems

Each unit shall include an on-base cooling system supplied by Seller for cooling lubricating oil and for cooling other systems as required by the manufacturer's design. The Purchaser will supply cooling water from a cooling tower to the skid edge (Purchaser connection points) at 115°F maximum.  Temperature controlled bypasses shall be provided by the Seller where necessary. The off-base cooling water system (cooling tower, pumps, off-base supply and return piping, off-base instrumentation/controls) shall be supplied by the Purchaser.

# 23.	Starting System

The gas turbine generator units shall be furnished with equipment, materials, and accessories required for starting.  The gas turbine starting system shall be of the electric motor type and be furnished as a complete system except motor starters (by others), and shall be capable of starting the entire GTG train.  Control equipment required to start and stop the gas turbine shall also be provided by Seller.  The starting system shall be capable of three (3) consecutive start attempts without overheating or damage.

# 24.	Compressor Wash System

A single skid-mounted on-line and off-line compressor wash system shall be furnished to remove blade deposits and restore compressor performance.  The wash system shall be furnished complete with required pumps, storage tanks, immersion heaters, piping, nozzles, instruments, and controls.

# 25.	Fire Detection and Protection

A skid mounted carbon dioxide (CO2) fire protection system shall be furnished for each gas turbine unit in accordance with NFPA standards.  The systems shall be designed to detect and extinguish fires within the turbine enclosures.  Detectors and alarms shall be furnished for enclosed areas.  The skid-mounted packages shall be complete with low-pressure CO2 tank, manifold, release mechanism, controls and instrumentation.

# 26.	Inlet Air Filtration Equipment

The inlet air filtration equipment shall be designed to filter out harmful contaminants, which could shorten the life of the gas turbine.  The inlet air filters shall be suitable for the operating environment described in the data sheets.  The inlet air filter shall be of the two stage barrier type with the appropriate alarm and trip instrumentation to protect the gas turbine and inlet air filter.  The inlet system shall include a stainless steel perforated sheet in the inlet silencer.  The inlet system shall also include the appropriate materials and coatings for high humidity environments (100% humidity and condensation associated with inlet chilling or inlet fogging.)

Seller will provide an option for the inlet air filter compartment and structural support steel to be appropriately sized for the future addition of inlet chilling down to 45F compressor inlet temperature when the ambient conditions are 95F Dry bulb and 80F wet bulb.

# 27.	Gas Turbine Generator Control Systems

## 27.1.	General

Each local control system shall combine control of the gas turbine and generator as an integrated function.  The gas turbine control system shall be SPEEDTRONIC Mark V Control.  The system shall be the Seller’s standard except as modified by the requirements stated herein.  The Mark V’s shall have Ethernet capable HMI servers (two local and one remote HMI servers).  Ethernet capable HMI Viewers shall be supplied; capable of supervising control and monitoring the GTG unit and interfacing with the balance of plant controller (PLC by others).  An HMI Historians shall be supplied to collect and store data from the Mark V’s and the balance of the plant controller.  Historian data for display by the HMI’s shall be passed over the Ethernet data highway.

Complete information on the control system is provided in Exhibit B-1.

Each GTG control system shall have 16 digital and 16 analog hardwired input/ output for remote control of the units.

An alarm and trip point list shall be developed for the gas turbine generator on the basis of the points listed herein.  Trip and alarm conditions shall be communicated to the plant control system for display at the station control room.

- GAS TURBINE GENERATOR ALARM AND TRIP POINTS

The functions below are accomplished in one of the following pieces of equipment: Generator Control Panel, Turbine Control Panel, EX-2000 Excitation Equipment or the Digital Generator Protection Equipment:

(A = Alarm only; A & T/A = Alarm on one level, trip and alarm on next level; T/A = Trip and alarm.)

Manual emergency trip (T/A).

Manual stop (A).

Turbine and generator high bearing metal temperatures (A & T/A).

Turbine and generator high vibration (A & T/A).

Flame out (T/A).

Inlet air filter high differential pressure (A & T/A).

Fuel supply pressure low (A & T/A).

Lube oil level low (A & T/A).

Lube oil high temperature (A & T/A).

Lube oil low temperature (A).

DC lube oil pump running (A).

DC lube oil pump overload (A).

High lube oil filter differential pressure (A).

Hydraulic oil pressure low (A & T/A).

Turbine over speed (T/A).

Loss of turning gear (A).

Loss of governor control power (where applicable) (A/T).

Fire extinguishing system actuated (A/T).

Fire extinguishing system disarmed (A).

Governor control system failure (T/A).

Igniter trip (T). (Failure to fire)

Igniter trouble (A). (Failure to fire)

Generator differential (T/A).

Generator rotor ground (A).

Generator ground (T/A).

Exciter field overcurrent (T/A).

Voltage regulator power supply failure (T/A).

Negative phase sequence (T/A).

Loss of field (T/A).

Generator stator high temperature (A & T/A).

Generator air filter differential (A).

Regulator on minimum excitation limit (A).

Regulator overexcitation (T/A).

Regulator underexcitation (T/A)

Main bus ground (T/A).

Unit overfrequency and underfrequency (A&T/A).

480-volt motor control center trouble (A).

Vibration (A & T/A).

Regulator loss of control power (T/A).

Regulator operating on backup AVR (if required) (A).

Reverse Power (T/A)

Out of Step Blocking (T/A)

Voltage Controlled Overcurrent (T/A)

Under/Over Voltage (T/A)

V/Hz trip (T/A).

Starting package system (A).

Air systems (A).

A final list of and setting of alarms and/ or trips shall be mutually resolved in the controls design finalization meeting.

## 27.2.	Starting System Controls

Each unit shall be provided with equipment and controls required to automatically sequentially start the unit, run it up to synchronizing speed, apply generator field, attain generator synchronizing voltage, synchronize to the system, and close the main generator breaker ready for loading the unit.

## 27.3.	Vibration Monitoring System

A vibration monitoring and protection system for each turbine and generator shall be furnished.  The system shall include both alarm and trip set points and indication of the vibration magnitude.  Probes on the X and Y-axes of each turbine and generator bearing shall be furnished.  Proximity probe pickup points shall be provided with key phasers.  The vibration monitoring system shall be Bently Nevada Series 3300 or acceptable equal.

# 28.	Additional Generator Equipment

Each generator shall be furnished with the following additional equipment:

A.	 Generator leads with flanged enclosure to interface with a non-segregated phase bus duct.

B.	Eighteen current transformers: for generator differential relaying, for general purpose protective relaying, one for the voltage regulator, and for metering.  Metering accuracy shall be at least ANSI 0.3B-1.8 Class.  Relaying accuracy shall be at least C400.

C.	One generator neutral grounding unit complete dry type or cast resin distribution transformer, secondary resistor and interconnection to the generator neutral.

D.	The protective relaying system for the generator shall consist of the following functional devices.  Protective relays necessary for proper operation and protection of the generator and exciter shall be included.  Each protective relaying system shall include, but not be limited to, the following functions (these functions may be handled either by mechanical or digital devices and may be located in the turbine control panel, generator control panel, digital generator protective panel, or the EX-2000 excitation system:

Generator protective relays:

Generator bus ground fault relay

Generator bus volts/ Hz protection with timer

Generator lockout relays (two)

Field ground detection system

Reverse power relay

Loss of field relay

Negative sequence relay

Phase over voltage & under voltage relays

VT fuse-loss detection and blocking

Under/ over frequency relay

Generator phase differential, three-phase unit

Generator neutral ground relay

95% stator ground fault relay

Voltage-controlled three-phase overcurrent

Out-of-step blocking relay

Voltage balance

E.	One set of generator metering and data transmission.  Metering and data transmission necessary for proper operation of the generator and exciter to properly load the plant and verify the load match was completed.  Metering and data transmission shall be included but not limited to, the following:

Watt transducer for turbine control

Watt/VAR transducer for turbine control

Watt transducer, 4 - 20 mA, for the Purchaser's use

VAR transducer, 4 - 20 mA, for the Purchaser's use

Digital Multimeter (DMM) incorporating the following functions:

Displays: V, A, Hz, W, VAR, p.f., VA, VARh, Wh

Pulse Outputs: Wh (out), VARh (incl, VARh out)

Analog (4-20mA) Outputs: W, VAR, p.f., Hz

Generator exciter field volts

Synchronizing scope, frequency meters, and voltmeters for synchronizing (provided digitally in Mark V)

F.	One assembly consisting of three surge arresters and capacitor connected to the generator leads.

G.	An automatic synchronizing equipment package shall be supplied with the turbine generator unit and shall include, but not be limited to, the following:

- Automatic synchronizing with breaker closure based on phase angle, slip, rate of change of slip and the response time of the breaker, which is in the system memory.

- Speed matching.

- Voltage matching.

- Voltage acceptance.

- Synchronizing check

- Provision for automatic and manual synchronizing.

The control system will include metering and equipment to monitor generator frequency, voltage, current, watts, vars, kWh, speed of turbine, temperatures, vibration, and pressures.

# 29.	Generator

The generators shall be an open-ventilated, air-cooled design.  Each three phase synchronous generator shall be rated to exceed the maximum turbine output in the 0° F to 102° F ambient temperature range at lagging 0.85 power factor to 0.95 leading power factor at Basis conditions.

# 30.	DATA SHEETS

## 30.1.	APPLICATIONS

### 30.1.1.	Power Generation

#### 30.1.1.1.	Number of Units: 2

#### 30.1.1.2.	Net Power Rating: 77.80 MW/ unit @ Basis Conditions

#### 30.1.1.3.	Starts per Year: 150

#### 30.1.1.4.	Generator Voltage: 13.8 kV

#### 30.1.1.5.	Generator Speed: 3,600 rpm

#### 30.1.1.6.	System Frequency: 60 Hz

#### 30.1.1.7.	Type of enclosure: Thermal & sound for outdoor installation.

#### 30.1.1.8.	Dry Low NOx Combustion System

#### 30.1.1.9.	Site Elevation above AMSL: 250 feet

### 30.1.2.	Gas Turbine Type: Industrial for Simple Cycle Power Generation

### 30.1.3.	Black Start: Not required.

### 30.1.4.	Fuels

#### Natural Gas is the project fuel. (See Exhibit A of the Agreement for detailed analysis).

#### Fuel Temperature Range:

Natural Gas: 50° to 90° F

### 30.1.5.	Mechanical Equipment

#### 30.1.5.1.	NOx Control Diluent: None

#### 30.1.5.2.	Lube Oil & Hydraulic System:

- Shaft driven Main Pump

- AC Motor Driven Auxiliary Pump 100% Capacity, 20 HP

- DC Motor Driven Emergency Pump, 7 ½ HP

- Coolers:	Shell & Tube

- Filters:	Duplex (Two, full flow)

- Coolant:	Water (straight tube coolers for an open cooling system)

#### 30.1.5.3.	Couplings: Seller's Standard

#### 30.1.5.4.	Fire Protection: Seller’s Standard

#### 30.1.5.5.	Inlet System Scope:

- Ductwork

- Two Stage Barrier type Inlet filters and filter house with optional provisions for inlet chilling  (97F Dry Bulb, 80F Wet Bulb Ambient conditions chilled down to 45F CIT) (coils by purchaser at later date)

- Alarm and Trip functions as appropriate to protect gas turbine and inlet system

- Inlet System with materials and coatings for high humidity environments.

- Inlet bleed heating system for NOx control (Down to 60% GT load)

- Silencers as needed to comply with the noise requirements.

#### 30.1.5.6.	Exhaust System Scope:

- Exhaust Expansion Joints

- Exhaust System Plenum

- Exhaust Orientation:  Right Side

#### 30.1.5.7.	Open Loop Cooling System (Purchaser supplied cooling water):

- Cool Side: 	115°F Water

- Total Flow Required for all Sources on GTG:   approximately 1000 gpm

- Coolant: 	Water

#### 30.1.5.8.	Compressor Cleaning System:

- semiautomatic on-line/off-line

#### 30.1.5.9.	The Gas Turbine Generator unit shall operate without the loss of component life within the specified time-frequency limits:

| Frequency range | Duration of Excursion |
| --- | --- |
| +2% | Continuous Operation |

## 30.2.	AUXILIARY POWER REQUIREMENTS

30.2.1.	Total Estimated Electrical Load for Auxiliaries Furnished with Turbine-Generator during Normal and Start-Up Operation—AC Load (kW)

- Natural Gas: 345 kW (Normal Operation) / 1087 kW (Start-up)

- Note: Seller shall also provide detailed list of all auxiliary loads listed above.

  - LOADING RATE

| Type of Start | Cold | Warm | Hot |
| --- | --- | --- | --- |
| Time required to initiate start and reach Full Speed No Load (FSNL) with no extended purge (min) | 7.5 | 7.5 | 7.5 |
| Estimate time required to synchronize (min) | Approx. zero | Approx. zero | Approx. zero |
| Time required to attain 100% load after synchronizing (min) | 12 | 12 | 12 |
| Estimated Total Time required from Initial Start to attaining 100% load (min) | 19.5 | 19.5 | 19.5 |

## 30.4.	STARTING CAPACITY

### 30.4.1.	Starting Device			Electric Motor

### 30.4.2.	Size				800 HP rated

### 30.4.3.	Type				Torque Converter

### 30.4.4.	Voltage			4160 V

### 30.4.5.	Power factor			0.85

## 30.5.	TURNING GEAR			Hydraulically operated torque converter using HP oil from the lube/hydraulic system

### 30.5.1.	Motor Horsepower		1 hp

### 30.5.2.	Speed, rpm			later

## 30.6.	GENERATOR DATA

| 30.6.1 | ### Rated MVA |  |  | 100.700 |
| --- | --- | --- | --- | --- |
| 30.6.2. | Rated Terminal Voltage, kV |  |  | 13.8 |
| 30.6.3. | Rated Power Factor at the generator terminals |  |  | 0.85 lagging to 0.95 leading |
| 30.6.3a | Rated Active Power at generator terminals must be continuously available over a GTG speed range of |  |  | 99-101% |
| 30.6.3b | Not used. |  |  |  |
| 30.6.3c | Reactive Power output under steady state conditions should be fully available at all rated voltage levels within the range of: |  |  | +5% |
| 30.6.4. | Type of Unit |  |  | Synchronous |
| 30.6.5. | Hydrogen Pressure and Purity (if H2 Cooled) |  |  | N/A |
| 30.6.6. | Speed, rpm |  |  | 3600 |
| 30.6.7. | Field Current (at rated MVA, kV, and P.F.), amp |  |  | 4213 |
|  | Field Voltage (at rated MVA, kV, and P.F.), volts |  |  | 240 |
| 30.6.8. | Field Resistance — at 125C |  |  | 0.275 ohm |
| 30.6.9. | Not used. |  |  |  |
| 30.6.10. | Short Circuit Ratio (rated) |  |  | 0.54 |
| 30.6.11. | Impedance and Constants (on rated MVA base) |  |  |  |
|  | a. | Xd (sat) | 2.02.036 |  |
|  | b. | Xd (unsat.) | 2.036 |  |
|  | c. | Xq | 1.941 |  |
|  | d. | X' (sat.) | 0.216 |  |
|  | e. | X' (unsat.) | 0.290 |  |
|  | f. | X1q | 0.443 |  |
|  | g. | X''d (sat.) | 0.15 |  |
|  | h. | X''d (unsat.) | 0.202 |  |
|  | i. | X2 (sat.) | 0.143 |  |
|  | j. | X2 (unsat.) | 0.193 |  |
|  | k. | Xo (sat.) | 0.95 |  |
|  | l. | Xo (unsat.) | 0.116 |  |
|  | n. | r1 | 0.004 |  |
|  | o. | r2 | 0.015 |  |
|  | p. | r0 | 0.007 |  |
|  | q. | T'do (sec.) | 5.623 |  |
|  | r. | T'qo (sec.) | 0.457 |  |
|  | s. | T''do (sec.) | 0.022 |  |
|  | t. | T''qo (sec.) | 0.046 |  |

30.6.12.	Three-Phase Capacitance to Ground (fd) Micro Farad	1.139

30.6.13.	Reactive Capability Curve (Curve no.)	D265T139-2

30.6.14.	Saturation Curve (Curve no.)	265T139-1A

30.6.15.	V-Curves (Curve no.)					D265T139-3A

30.6.16.	Maximum Continuous Load without 			N/A

Stator Coolant (kW)

30.6.17.	I2T	10.0

30.6.18.	Insulation Class Rating	Class F

30.6.19.	Temperature Rise Limit				Class B

30.6.20.	Maximum Allowable Temperature and Temperature Rise	per ANSI C50-10

and C50-13 for Class F insulation and Class B temperature rise

30.6.21.	Allowable Vibration for Continued

Operation/Absolute or Relative mil		Per ISO 7919-4

30.6.22.	Spinning Inertia – WR2 (lb – ft2)			209,000 (combined)

30.6.23.	Generator Output vs. Tamb (Curve no.)		H.E.P. 16621

## 30.7.	EXCITER DATA

### 30.7.1.	Type (state Seller standard)				Brushless

## 30.8.	Guaranteed Performance and Emissions Data

See Section 10 of the Agreement