5.1.2.	Transformer Accessories

Each transformer shall be equipped with all normally furnished standard accessories.  All dial type indicating devices shall be easily read from base level.  These accessories shall include, but not be limited to, the following:

- A magnetic liquid level indicator.

- A dial type thermometer, equipped with two pointers, one to indicate top liquid temperature at the time of reading, and the other to indicate the maximum temperature reached since the last resetting.  High temperature alarm contact shall be provided.

- A non-adjustable liquid level gauge with low level alarm contacts shall be provided to alarm when the oil level drops below normal operating level.  For contact rating see Section 9.6.

- A pressure/vacuum gauge with alarm contact and a pressure/vacuum bleeder with sampling valve, mounted on the transformer tank and piped to the gas space above the liquid.

| 9.1 GENERAL |  |  |
| --- | --- | --- |
|  | Customer | E-Next Generation LLC |
|  | Elevation Feet above MSL | <3300 Feet |
|  | Minimum/Maximum Ambient Temperature (°C) | -13.3/46 |
|  | Humidity | 100% |
|  | Wind Velocity | 100 mph |
|  | Sound Level (87/109/136 MVA) | 73 dBA |

| 9.2 | RATINGS |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | H Winding MVA @ 65°C X Winding @ 65°C Y Winding @ 65°C |  |  |  | Rev 1 136 84.4 51.6 |  |  |
|  | Type |  |  |  | Oil Filled |  |  |
|  | Type (Cooling) |  |  |  | FOA |  |  |
|  | High Voltage, kV |  |  |  | 138 |  |  |
|  | Low Voltage, kV |  |  |  | X 13.8 Y 13.8 |  |  |
|  | Number of Phases |  |  |  | 3 |  |  |
|  | Frequency, Hertz |  |  |  | 60 |  |  |
|  | Oil Preservation System (Sealed tank, Inert gas, Conservator) |  |  |  | Conservator |  |  |
|  | Insulation/Coolant (Mineral oil, askarel) |  |  |  | Mineral Oil |  |  |
|  | Impedance - % (H-X) on FOA base (84.4 MVA base) Impedance - % (H-Y) on FOA base (51.6 MVA base) |  |  |  | 20.3% 20.3% |  |  |
|  | Impedance will be rated at the listed percentage at rated (MVA) voltage and forced-cooled MVA. |  |  |  |  |  |  |
|  | System Fault Current RMS Symmetrical, kA |  |  |  | ANSI C57.12.00 Sec 7.1.5 |  |  |
|  | Grounding |  |  |  |  |  |  |
|  | HV Winding |  |  |  | Grnd wye |  |  |
|  | LV Winding |  |  |  | X Delta Y Delta |  |  |
|  | Insulation: The winding terminal insulation classes and withstand test for which they are designed shall be as follows: |  |  |  |  |  |  |
|  |  | High H Line |  | Low X,Y |  |  | (Ho) Neutral |

| 9.4.2 | Low Voltage |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Overhead Line |  |  |  |  |  |  |  |  |  |  |  |
|  | Underground Cable |  |  |  |  |  |  |  |  |  |  |  |
|  | Bus |  |  |  |  |  |  | Nonsegregated Phase Bus-Flange Connection X and Y |  |  |  |  |
| 9.5.1 | Phase Current Transformers - (Yes/No) |  |  |  |  |  |  |  | Yes |  |  |  |
|  | Item |  |  |  | HV |  | Rev 1 LVX |  |  |  | Rev 1 LVY |  |
|  | Relaying |  |  | 3 per phase 1200:5,MR,C800 |  |  | 2 per phase 5000:5,MR,C800 |  |  |  | 2 per phase 4000:5, MR,C800 |  |

| 9.5.5 | Surge Arrestor Required - (Yes/No) | Yes |
| --- | --- | --- |
|  | Rating | Rev 1 88 kV MCOV |
|  | Type | Metal-Oxide |

| 10. VENDOR DATA SHEETS |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | These data sheets are supplementary to the data sheets in Attachments A, B, and C, if attached. |  |  |  |
|  | Equipment No. | HU-Enron-2D-LS Low Sound |  |  |
|  | Vendor | ABB Neg#FC011400-2D-LS |  |  |
|  | Purchase Order No. |  |  |  |
|  | Item No. |  |  |  |
|  | Factory Location | St. Louis, MO |  |  |
|  | Factory Address |  |  |  |
|  | Vendor’s Requisition No. |  |  |  |
|  | Serial No. |  |  |  |
|  | Shop Order No. |  |  |  |
|  | Unit Purchase Price (If not given on Purchase Tender) |  |  |  |
|  | Instruction Book No. |  |  |  |
|  | Replacement Parts Book No. |  |  |  |
|  | Voltage Rating | 138,00 |  |  |
|  | KVA Rating at 55°C | N.A. |  |  |
|  | KVA Rating at 65°C | Rev 1 136,000 |  |  |
|  | Voltage Tap Settings (No Load) |  |  |  |
|  | BIL |  |  |  |
|  | Pri. | 650 KV |  |  |
|  | Sec. | 110 KV |  |  |
|  | Form: |  |  |  |
|  | Core | Core |  |  |
|  | Shell |  |  |  |
|  | Outline Drawing No. |  |  |  |
|  | Control Diagram Drawing No. |  |  |  |
|  | Elementary Diagram Drawing No. |  |  |  |
|  | Connection Diagram Drawing No. |  |  |  |
|  | No-Load Loss at Rated Voltage – KW | Rev 1 45 = N.L. 640 = L.L. @ 136 MVA |  |  |
|  | Total Losses, Including Auxiliary Losses at Full Load-KW Equal to 115.6 MW at 0.85 pf, or 136 MVA. | Rev 1 705 = Total Losses |  |  |