AEP Renewable Generation Transmission Projects

# Projects have been presented and reviewed by to the ERCOT West Texas Regional Planning Group on March 20, 2001

Thursday, July 19, 2001	Page 1 of 11

From August 1999 through July 2000 there have been requests for 900 MW of wind generation to be interconnected into the West Texas Utilities Transmission system in and around the Rio Pecos region with generation in-service dates between 2/1/01 and 03/01/02. Of the 900 MW requested, there have been interconnection agreements executed for 725 MW and another 60 MW facility is currently being negotiated.. This brings the total amount of generation requesting to be interconnected to 785 MW with all generation being in-service no later than 03/01/2002.

At present there is 231 MW of generation in-service in the Rio Pecos region, which has a non-coincident  peak load of 138 MW with a current load projection of 162 MW by year 2010. Of the 231 MW of generation, 140 MW is conventional natural gas power located at Rio Pecos, 75 MW is wind generation located on the North Mc Camey to Big Lake 138 kV line, and the last 16 MW is made up of small internal combustion plants and a small combustion turbine located southwest of Rio Pecos.

Today the Rio Pecos region is made up of two 138 kV paths and three 138 kV radial lines. One 138 kV path runs eastward from Rio Pecos to the Twin Buttes 345 kV corridor while the second 138 kV path runs northward from Rio Pecos to the Odessa 345 kV corridor.  Two of the 138 kV radial paths run southwesterly  from Rio Pecos to Ft. Stockton and to 16th Street station with the third radial path running southeasterly from Rio Pecos to Ft. Lancaster.

In order to accommodate the generators’ requests to inject 785 MW into the Rio Pecos region, the study was broken into two parts.  The first part focuses on building the necessary infrastructure required to accept the 785 MW of generation into the local network, and the second focuses on building the necessary bulk transmission paths to transport the generation from the local network to the two 345 kV corridors at Odessa and at Twin Buttes.  Full compliance is maintained with all Transmission Planning Reliability Criteria and Standards set forth by American Electric Power (AEP), Electric Reliability Council of Texas (ERCOT), and the North American Electric Reliability Council (NERC).

The local network improvements can be broken into three triangles: (refer to attached drawing)

- Rio Pecos to Crane to North Mc Camey to Rio Pecos

- Rio Pecos to Ft. Stockton to 16th Street to Rio Pecos

- Rio Pecos to Mesa View Switch Station to West Yates Switch Station to North McCamey to Rio Pecos

The first triangle requires all three legs to be re-conductored.  The second triangle requires the first leg from 16th Street to Ft. Stockton be converted to 138 kV.  The third triangle requires the first two legs from Rio Pecos to Mesa View Switch and Mesa View Switch to West Yates Switch Station to be re-conductored, and the last leg from West Yates Switch Station to Rio Pecos to be converted to 138 kV.

The intent of the improvements listed here are to ensure that adequate transmission capacity exists in each of the three triangles to allow the injection of generation into the local network, while maximizing the use of the existing network by minimizing the need for new right-of-way and the need for CCN’s (Certificate of Convenience and Necessity).

Two alternatives were considered for transferring the power from the local network to the 345 kV corridors at Odessa and Twin Buttes. The first alternative added 345 kV lines from Rio Pecos to Twin Buttes, Rio Pecos to Permian Basin, Permian Basin to Moss, and Moss to Odessa. This alternative would require two 138 / 345 kV Autos at Rio Pecos and one 138 / 345 kV Auto at Permian Basin. This alternative is estimated to cost $183 million including the cost of the improvements required for the local network.

The second alternative required re-building two 138 kV paths from Rio Pecos to Odessa, re-building an existing 138 kV line from Rio Pecos to Twin Buttes and adding a third bulk 138 kV path from Rio Pecos to Twin Buttes. The additional bulk path requires two new 138 kV legs from Ft. Lancaster to Friend Ranch and Friend Ranch to Twin Buttes. This alternative is estimated to cost $152 million including the cost of the improvements for the local network.

Given the in-service dates for all wind power generating units is no later than 03/01/02, and the time associated with certifying and building a new 345 kV line and the associated cost, alternative one was neither feasible nor cost effective.  Therefore, the second alternative was selected as the preferred plan, since it provides for timely incremental transmission capacity at an overall lower cost.

The following information details the criteria violations that result from the interconnection of 785 MW wind farm generation into the Rio Pecos region, and the specific transmission system improvements, and their associated schedule, that have been determined to be necessary to relieve the criteria violations.

Prepared by AEP Texas Transmission Planning

Thursday, July 19, 2001	Page 2 of 11

__________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

__________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Project Number 	Title	TP/PM	Type	TSP	Status

TP-2001-011	National Wind Power Wind 	GR	/	BM	IPP	WTU	Proposed

Generation Interconnection

=============================================================================================================

Contingency	Problem	Solution

Rio Pecos to Fort Lancaster 138 kV 	Yates Field area voltages fall 	Addition of a Ft. Lancaster to Friend Ranch 1272

line and SW Mesa Tap to Big Lake 	below 90% and McCamey to 	ACSR 138 kV line

138 kV	Rankin 69 kV line exceeds its

emergency rating

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description	CI IDs	Mileage 	CCN	In-service date

Interconnect National Wind Power's 125 MW	ETN100716	Exempt Line	6/1/01

10472

Over current relay Illinois to Ft. Lancaster	ETN101846	n/a	6/1/02

10458

Add new 138 kV Terminal @ Ft. Lancaster	ETN101847	n/a	9/1/05

9948

Add new 40 mile 138 kV Ft. Lancaster to 	ETN101848	40	To be filed	9/1/05

Friend Ranch (1272 ACSR)	9913

System protection and interrupting devices as 	ETN101849	n/a	9/1/05

result of re-conductors and new lines	9736

Prepared by AEP Texas Transmission Planning

Thursday, July 19, 2001	Page 3 of 11

_________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

_________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Project Number 	Title	TP/PM	Type	TSP	Status

TP-2001-012	Woodward Wind Generation 	GR	/	BM	IPP	WTU	Proposed

Interconnection

=============================================================================================================

Contingency	Problem	Solution

FPL Energy Power Partner's 	Interconnection	FPL Energy Power Partner's Woodward#1 Wind

Woodward#1 wind farm	Farm generation in Pecos County

____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description	CI IDs	Mileage 	CCN	In-service date

Add new 138 kV Terminal at Ft. Stockton	ETN101845	n/a	3/1/03

10478

Interconnect FPL Energy Power Partner's 80 	ETN101850	Exempt Line	4/1/01

MW wind generation facility with RTU / 	10438

Motorized Switch at generation line switch tap

Add new 138 kV line terminal @ Rio Pecos	ETN101855	n/a	9/1/05

10476

=============================================================================================================

Contingency	Problem	Solution

Addition of 785 MW of wind 	WTU Crane to TU Crane 138 kV 	Reconfigure WTU/TU Crane substation to a

generation in West Texas - SW Mesa	bus tie  exceeds its emergency 	breaker and half scheme and Replace 138/69

to Big Lake 138 kV	rating				        kV auto 125 MVA

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description	CI IDs	Mileage 	CCN	In-service date

Reconfigure WTU/TU Crane substation to a 	ETN101854	n/a	3/1/03

breaker and half scheme and Replace 138/69 	9950

kV auto 125 MVA

=============================================================================================================

Contingency	Problem	Solution

Addition of 785 MW of wind 	WTU Crane to Rio Pecos 69kV 	Convert 69 kV North  McCamey to WTU Crane line

generation in West Texas - Rio 	line exceeds its emergency rating	to 138 kV with 1272 ACSR conductor

Pecos to Crane 138 kV line

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description	CI IDs	Mileage 	CCN	In-service date

Over current relay Rio Pecos to WTU Crane  	ETN101851	n/a	6/1/02

69 kV	10429

System protection and interrupting devices as 	ETN101852	n/a	6/1/02

result of re-conductors and new lines	10430

Convert 25 miles of 69 kV from North Mc 	ETN101853	25	To be filed	9/1/05

Camey to WTU Crane to 138 kV (1272 ACSR)	9915

and double circuit from Mc Elroy to WTU

Crane (795 ACSR)

Convert Spudder Flat 69 kV substation to 138 	ETN101856	n/a	9/1/07

kV	10372

Prepared by AEP Texas Transmission Planning

Thursday, July 19, 2001	Page 4 of 11

_________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

_________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Project Number 	Title	TP/PM	Type	TSP	Status

TP-2001-013	King Mnt Wind Generation 	GR	/	BM	IPP	WTU	Proposed

Interconnection

=============================================================================================================

Contingency	Problem	Solution

Upton Wind (King Mountain) Wind 	Interconnection	Upton Wind (King Mountain) Wind Farm generation in

Farm generation	 Crane County

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description	CI IDs	Mileage 	CCN	In-service date

Interconnect Upton Wind (LP)'s 80 MW King 	ETN101857	Exempt Line	5/1/01

Mnt NW and  80 MW King Mnt SW	10447

Interconnect Upton Wind (LP)'s 80 MW King 	ETN101858	Exempt Line	6/1/01

Mnt NE and  40 MW King Mnt SE	11472

=============================================================================================================

Contingency	Problem	Solution

Addition of 785 MW of wind 	WTU Crane to Rio Pecos 138 kV 	Re-conductor 138 kV WTU Crane to Rio Pecos line

generation in West Texas - Rio 	line exceeds its emergency rating	with 1272 ACSR conductor

Pecos to North McCamey 138 kV

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description	CI IDs	Mileage 	CCN	In-service date

Re-conductor 11.5 miles of 138 kV from King 	ETN101861	11.5	Exempt Line	9/1/07

Mnt West Tap to WTU Crane 138 kV (1272 	10404

ACSR)

=============================================================================================================

Contingency	Problem	Solution

Addition of 785 MW of wind 	Big Lake 69/138 kV 	Reconfigure Big Lake 138 kV to ring bus

generation in West Texas - Big Lake 	autotransformers exceed their

138 kV Bus Tie	emergency rating

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description	CI IDs	Mileage 	CCN	In-service date

Reconfigure Big Lake substation 138 kV bus to	ETN101862	n/a	3/1/04

five position ring	10482

Prepared by AEP Texas Transmission Planning

Thursday, July 19, 2001	Page 5 of 11

=============================================================================================================

Contingency	Problem	Solution

Addition of 785 MW of wind 	North McCamey to SW Mesa 138	Re-conductor 138 kV North  McCamey to SW Mesa

generation in West Texas - Friend 	 kV   line exceeds its emergency 	line with 1272 ACSR

Ranch to Ft. Lancaster 138 kV	rating

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description	CI IDs	Mileage 	CCN	In-service date

System protection and interrupting devices as 	ETN101859	n/a	6/1/02

result of re-conductors and new lines	11474

Re-conductor 3.85 miles of 138 kV from SW 	ETN101864	3.85	Exempt Line	3/1/04

Mesa to King Mnt East Tap (1272 ACSR)	11473

Re-conductor 2.0 miles of 138 kV from SW 	ETN101865	2	To be filed	3/1/04

Mesa including King Mnt East Tap at 138kV 	10392

double circuit (795 & 1272 ACSR) to North

McCamey (795 ACSR)

Reconfigure North Mc Camey 138 kV 	ETN101866	n/a	9/1/05

substation to Ring Bus (five position)	10466

=============================================================================================================

Contingency	Problem	Solution

Addition of 785 MW of wind 	SW Mesa to Big Lake 138 kV  line	Re-conductor 138 kV SW Mesa to Big Lake line with

generation in West Texas - TU Crane	 exceeds its emergency rating	1272 ACSR conductor

to Odessa EHV 138 kV

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description	CI IDs	Mileage 	CCN	In-service date

Install Line Monitoring Equipment on the North 	ETN101860	n/a	3/1/02

Mc Camey to Big Lake 138 kV line	11475

Re-conductor 40.94 miles of 138 kV from SW 	ETN101863	40.9	Exempt Line	9/1/07

Mesa to Big Lake (1272 ACSR)	10384

Prepared by AEP Texas Transmission Planning

Thursday, July 19, 2001	Page 6 of 11

_________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

_________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Project Number 	Title	TP/PM	Type	TSP	Status

TP-2001-014	Indian Mesa I Wind Generation 	GR	/	BM	IPP	WTU	Proposed

Interconnection

=============================================================================================================

Contingency	Problem	Solution

Indian Mesa Power Partners I Wind 	Interconnection	Indian Mesa Power Partners I Wind Farm generation

Farm generation	in Pecos County

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description	CI IDs	Mileage 	CCN	In-service date

Interconnect Indian Mesa Power Partner's I    	ETN101867	Exempt Line	5/1/01

25 MW wind generation facility	10450

=============================================================================================================

Contingency	Problem	Solution

Addition of 785 MW of wind 	Ft. Lancaster 69/138 kV 	Convert 69 kV North McCamey to Mesa View line to

generation in West Texas - Rio 	autotransformer  exceeds its 	 138 kV with 1272 ACSR conductor, add new

Pecos to Mesa View 138 kV	emergency rating	switching station at Mesa View, add switching station

at West Yates Tap, and move North McCamey

138/69 kV autotransformer to West Yates Switch Sta.

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description	CI IDs	Mileage 	CCN	In-service date

Install Line Monitoring Equipment on the North 	ETN101868	n/a	3/1/02

Mc Camey to Big Lake 138 kV line	11460

System protection and interrupting devices as 	ETN101869	n/a	6/1/02

result of re-conductors and new lines	11456

Over current relay West Yates Tap to Air 	ETN101870	n/a	6/1/02

Products Tap 69 kV	11449

Add new West Yates 138 kV Switching Station 	ETN101871	Exempt 	9/1/03

(five position ring) and move North Mc Camey	10483	Substation

69/138 kV auto to West Yates

Add new Mesa View 138 kV Switch Station 	ETN101872	Exempt 	9/1/03

(five position ring)	10480	Substation

Convert Mc Camey 69 kV substation to 138 	ETN101873	n/a	9/1/03

kV	11459

Convert Tippet 69 kV substation to 138 kV	ETN101874	n/a	9/1/03

11463

Re-build 5.57 miles of 138 kV from Mesa View 	ETN101875	5.57	Exempt Line	9/1/05

to Mesa View Switch Station to 138 kV (1272 	11451

ACSR)

Convert 9.98 miles of 69 kV Tippet to West 	ETN101876	9.98	Exempt Line	9/1/03

Yates Switch Station 138 kV (1272 ACSR)	11462

Add new 1.0 mile 138 kV (1272 ACSR) line 	ETN101877	1.0	To be filed	9/1/03

between Yates Pump to Mesa View	11457

Convert 4.23 miles of 69 kV from West Yates	ETN101878	4.23	Exempt Line	9/1/03

Switch Station to Yates Pump to 138 kV   	11458

(1272 ACSR)

Convert  West Yates Pump 69 kV Substation 	ETN101879	n/a	9/1/03

to 138 kV	11461

Re-build 13.46 miles of 69 kV from North Mc 	ETN101880	30	Exempt Line	8/1/03

Camey to Tippet to 138 kV  (1272 ACSR)	10423

Prepared by AEP Texas Transmission Planning

Thursday, July 19, 2001	Page 7 of 11

=============================================================================================================

Contingency	Problem	Solution

Addition of 785 MW of wind 	Rio to WTU Crane 69 kV line 	Convert 69 kV Rio Pecos to WTU Crane line to 138

generation in West Texas - WTU 	exceeds its emergency rating	kV with 1272 ACSR

Crane to Rio Pecos 138 kV

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description	CI IDs	Mileage 	CCN	In-service date

Convert 23 miles of 69 kV from Rio Pecos to 	ETN101881	22.98	Exempt Line	9/1/07

WTU Crane 138 kV (1272 ACSR) build .12 	10366

miles of double circuit Crane Tap 1 to WTU

Crane

Prepared by AEP Texas Transmission Planning

Thursday, July 19, 2001	Page 8 of 11

_________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

_________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Project Number 	Title	TP/PM	Type	TSP	Status

TP-2001-015	Indian Mesa II Wind Generation 	GR	/	BM	IPP	WTU	Proposed

Interconnection

=============================================================================================================

Contingency	Problem	Solution

Addition of 785 MW of wind 	SW Mesa to Big Lake 138 kV  line	Construct 138 kV Friend Ranch to Twin Buttes line

generation in West Texas - TU Crane	 exceeds its emergency rating	with 1272 ACSR conductor

to Odessa EHV 138 kV

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description	CI IDs	Mileage 	CCN	In-service date

Over current relay Rio Pecos to Mc 	ETN101883	n/a	6/1/02

Camey 69 kV	11471

Add one new 138 kV terminal at Twin Buttes	ETN101884	Exempt 	9/1/05

10475	Substation

Add two new 138 kV terminals at Friend Ranch	ETN101885	n/a	9/1/05

10477

Add new 70 mile 138 kV line from Friend 	ETN101886	70	To be filed	7/1/05

Ranch to Twin Buttes (1272 ACSR)	10449

=============================================================================================================

Contingency	Problem	Solution

Indian Mesa Power Partners II Wind 	Interconnection	Indian Mesa Power Partners II Wind Farm generation

Farm generation	 in Pecos County

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description	CI IDs	Mileage 	CCN	In-service date

Interconnect Indian Mesa Power Partner's II   	ETN101882	Exempt Line	10/1/01

135 MW wind generation facility	11470

Prepared by AEP Texas Transmission Planning

Thursday, July 19, 2001	Page 9 of 11

_________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

_________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Project Number 	Title	TP/PM	Type	TSP	Status

TP-2001-016	Capital Hill Wind Generation 	GR	/	BM	IPP	WTU	Proposed

Interconnection

=============================================================================================================

Contingency	Problem	Solution

Addition of 785 MW of wind 	Rio to North McCamey 138 kV 	Re-conductor 138 kV Rio Pecos to North McCamey

generation in West Texas - Ft. 	line exceeds its emergency rating	line with 1272 ACSR conductor

Lancaster to Mesa View Switching

Station 138 kV line

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description	CI IDs	Mileage 	CCN	In-service date

Re-conductor 9.67 miles of 138 kV from Rio 	ETN101894	9.67	Exempt Line	9/1/03

Peocs to North Mc Camey (1272 ACSR)	10387

=============================================================================================================

Contingency	Problem	Solution

Addition of 785 MW of wind 	Rio to Mesa View 138 kV line 	Re-conductor 138 kV Rio Pecos to Mesa View

generation in West Texas - Rio 	exceeds its emergency rating	Switching Station line with 1590 ACSR conductor

Pecos to Capital Tap 138 kV line

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description	CI IDs	Mileage 	CCN	In-service date

System protection and interrupting devices as 	ETN101888	n/a	3/1/02

result of re-conductors and new lines	11440

Add 25 MVAR 138 kV Capacitor Bank @ Rio 	ETN101890	25 MVAR 	n/a	3/1/03

Pecos	11439	cap

Upgrade Indian Mesa substation bus to 1590  	ETN101892	n/a	9/1/05

ACSR	11441

Re-conductor 27.13 miles of 138 kV from Rio 	ETN101893	27.13	Exempt Line	12/1/05

Pecos to Mesa View Switch Station ( 1590 	10388

ACSR)

=============================================================================================================

Contingency	Problem	Solution

Addition of 785 MW of wind 	Mesa View Switching Station  to 	Re-conductor 138 kV Mesa View Switching Station to

generation in West Texas - Rio 	Ft. Lancaster 138 kV line exceeds	 Ft. Lancaster line with 1272 ACSR conductor

Pecos to Indian Mesa 138 kV	 its emergency rating

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description	CI IDs	Mileage 	CCN	In-service date

Re-conductor 19.8 miles of 138 kV from Mesa 	ETN101895	19.8	Exempt Line	12/01/06

View Switch to Ft. Lancaster (1272 ACSR)	10396

Prepared by AEP Texas Transmission Planning

Thursday, July 19, 2001	Page 10 of 11

=============================================================================================================

Contingency	Problem	Solution

Addition of 785 MW of wind 	Indian Mesa area voltages fall 	Add 15 MVAR Capacitor Bank @ Mesa View

generation in West Texas - Rio 	below 90%	Switching Station 138 kV, 15 MVAR Capacitor Bank

Pecos to Indian Mesa 138 kV line	@ West Yates Switching Station 138 kV, and 15

MVAR Capacitor Bank @ Ft. Lancaster 138 kV

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description	CI IDs	Mileage 	CCN	In-service date

Add 10 MVAR and 15 MVAR 138 kV Capacitor 	ETN101889	15 MVAR 	Exempt 	9/1/03

Banks @ West Yates	10360	cap	Substation

Add 10 MVAR and 15 MVAR 138 kV Capacitor 	ETN101891	15 MVAR 	Exempt 	9/1/03

Banks @ Mesa View Switch	10410	cap	Substation

Add 10 MVAR 69 kV Capacitor Bank @ Ft. 	ETN101911	10 MVAR 	n/a	3/1/03

Lancaster	10417	cap

=============================================================================================================

Contingency	Problem	Solution

Capital Hill Wind Farm	Interconnection	Capital Hill Wind Farm generation in Upton County

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description	CI IDs	Mileage 	CCN	In-service date

Interconnect Capital Hill 60 MW wind 	ETN101887	Exempt Line	3/1/02

generation facility	10386

Prepared by AEP Texas Transmission Planning

Thursday, July 19, 2001	Page 11 of 11