Exhibit D- Acceptance and Performance Evaluation Testing Protocol

Acceptance Performance Testing

Acceptance testing for each new and clean 2 or 2.4MW plant will be done following a period of plant startup, tuning, and general shakedown testing.  Acceptance performance testing must include provisions to accurately determine overall plant performance for the purpose of determining compliance with contractual guarantees as well as provisions to determine plant internal component performance to serve as the basis of comparison for all future performance testing of the plant.

Warrantee Compliance Performance Testing
Warranty compliance performance testing can be done at any time during plant operation to assess plant performance and determine plant and internal plant component performance degradation.  Warrantee compliance performance testing must include provisions to accurately determine which components of the plant are contributing to any measured decay in overall plant performance and by what amount.

Overall plant performance shall be determine in accordance with the following general equations:

Power output decay = (1-(Maximum Unit Output at start of operations – Maximum Unit Output at time of performance test)/(( Maximum Unit Output at start of operations))/100

Efficiency decay = (1-(efficiency at start of operations – efficiency at time of performance test)/((efficiency at start of operations))/100.  For purposes of these calculations efficiency is expressed as a percentage.

Performance Test
All performance testing (for Acceptance or for Warrantee Compliance) shall be done to a mutually agreed upon test plan and procedures between Purchaser and Seller.  The agreed upon procedures (“Performance Test Procedures”) [note: we need to add this to the definitions section] will specify procedures for determining overall plant power and heat rate, internal plant component performance, data evaluation, and determination of instrument and overall performance test uncertainty.   Performance Test Procedures shall be based on the applicable sections and guidelines of ASME PTC 46-1996, and more specifically on ASME PTC 50 (“Fuel Cell Power Systems Performance”) if already published by the ASME at the time of the testing.

Performance Test Procedure Requirements
Performance Test Procedures will include, as a minimum:

- Identification of all parameters to be measured

--  determine if station instrument or temporary test instrument are to be used

- Method of correcting measured performance at test conditions to Guarantee Basis Conditions

- Method to determine unit internal component performance (e.g., Fuel Cell Module, Inverter, applicable BOP subsystems) for the following purposes:
A)  In the case of the Acceptance Test:  To establish a detailed baseline of unit performance when “new and clean”.  This is to serve as the basis for comparison for all other life cycle performance testing.
B)  In the case of the Warranty Test:  To accurately account for each unit component contribution to overall unit degradation.

- Method of verification that unit is at Maximum Unit Output – identification of parameters (such as fuel cell stack temperature, anode exhaust oxidizer catalyst temperature) which determine when a unit cannot be ramped further.

- Method of verification that conditions are stable

- Number of tests and duration of each test (minimum number of tests, 1-hour each)

- Means of verifying instrumentation calibration

- Sample performance analysis

- Sample instrumentation uncertainty analysis 

In the case of the Acceptance Performance Test, the performance test procedure shall also include the following:

- Definition of “new and clean”

- Prerequisites to commencing the test
--  Functional tests (electrical and mechanical)

- Method of verification that simultaneous specific performance is satisfied

-- Compliance with emissions and noise guarantees

Performance Test Approach
The general approach to all performance testing is as follows:

- Conduct a pre-test review of procedures and expected accuracy for Purchaser and Seller approval. A post-test uncertainty analysis be used to determine compliance with guarantee points.

- Verify that basic input conditions are stable (ambient conditions, fuel composition, water quality).

- Ramp the powerplant up to the Maximum Unit Output as measured at the 480V side of inverter.  This is a net output consisting of the fuel cell DC power generation minus losses due to:

Power conditioning

Step up of voltage to 480V

Parasitic power usage within plant (blowers, etc)

Auxiliary power usage for equipment within FCE scope (HVAC, lighting, control system power, water treatment, pumps, if any)

The plant control system will measure and report the appropriate net ac power directly.  It can be independently verified by measuring power output with another device (provided by Purchaser).  If that device is located after transformation to a higher voltage than 480V, a correction must be made to account for the additional step-up loss.

- Verify stable operation at Maximum Unit Output

- Determine efficiency

- Measure fuel input composition at interconnecting point to FCE supplied equipment using gas chromatograph (Purchaser supplied, not part of permanent plant instrumentation) or sample tested by independent laboratory.  This is used to calculate fuel heating value.  Fuel Heating value shall be obtained in accordance with ASTM D 1945 and ASTM D 3588.

- Measure fuel input rate.  The plant control system measures and reports input flow rate, but this can be measured independently with additional Purchaser supplied instruments at the fuel inlet line to each unit if desired.  Fuel density at the flow meter shall be calculated from the fuel composition obtained from the gas chromatograph or from the independent laboratory fuel analysis.

- Using fuel LHV heating value and input rate as the energy input and Maximum Unit Output as the output, calculate unit efficiency.

- Apply any corrections needed for basis conditions

- Corrections to include

--   Fuel Composition (% CH4, diluents, allowable contaminants)

--   Fuel pressure/temperature

--   ambient temperature and humidity

--   power factor

--   operating history (thermal cycles, etc)

- Conduct a post-test uncertainty analysis to verify accuracy of the measured efficiency, power output, and internal component performance.

Emissions Test

- Unit emissions compliance shall be demonstrated simultaneously with the Unit Acceptance Performance Test.

- Emissions compliance shall be determined

- during stable operation at Maximum Unit Output.

- Unit exhaust shall be analyzed

- to determine composition of NOx, SOx, CO, and PM10 particulate.

- Emissions Test Procedures shall be agreed upon, based on applicable existing guidelines as modified appropriately for the fuel cell application.

- The accuracy of these procedures will be assessed and this accuracy allowance will be used to determine compliance with guarantee points.

- Determine water consumption and wastewater quantity and quality.

- Water uptake and discharge will be measured.  Wastewater quantity and quality will be monitored and compared with guarantee.

Noise Test
Unit compliance with noise guarantees shall be demonstrated prior to unit Acceptance.

- Noise test – Far Field
Prior to operation of the powerplant a baseline noise measurement must be made.  If noise measurement at partload is desired, this can be done during the initial ramp to Maximum Unit Output.  Noise measurements will be taken at selected locations (mutually agreed upon before the test) based on accessibility and relevance to local regulations.  Corrects of data to the 100 foot guarantee specification can be made if needed to determine guarantee compliance. Noise measurements will be adjusted for the pre-operation baseline to determine the plant maximum noise level.

- Noise test – Near Field

Prior to operation of the powerplant a baseline noise measurement must be made.  Once the powerplant is operating at Maximum Unit Output, noise measurements will be taken at selected locations on the locus of points 3 feet from the equipment, 5 feet above any working level.  Measurements will be taken at loads of 25-100%.  Noise measurements will be adjusted for the pre-operation baseline to determine the plant maximum noise level.

# Reliability Test

- Reliability Test – continue plant operations until a total of 72 consecutive hours at maximum guaranteed output and complying with all noise and emissions permit conditions has been logged without unplanned outages. (Commercial agreement will define terms).