Aquila Questions & Answers: Gleason & Wheatland Plants

October 20, 2000

1) Are the units started in parallel or sequence? (Could you please provide a diagram of the ramp-up sequence to include timing).

These units can be started either in parallel or in sequence.  Additional information will follow. (Chris Norris information)  In sequence is the normal procedure of the units.  Upon “start” the units will progress to 3600 RPM in 9-10 Minutes.  If “Auto” synch is selected the unit will synch within 1-2 Minutes maximum.  Upon synchronization (8 MW at synchronization) the unit is typically loaded to a preset load or base at 8 MW/minute.  Maximum load rate is 13.9 MW/minute.  Total time to base (using 120 MW) is 26 minutes.

2) How much start up power is required?

# To be provided on Monday.

3) Is start up power purchased from Cinergy &/or IPL?  At what tariff rate?

See 01.02.27 A and 01.02.27 B in DealBench

4) How many Mwh are produced during start up? (May include as part of #1)

To be provided on Monday.

5) How much fuel is burned (MMBTU's) during start up? (May include as part of

#1)

Approximately 100 MMBtu/turbine is burned per start up.

THE INFORMATION CONTAINED HEREIN IS BEING PROVIDED TO YOU PURSUANT TO AND SHOULD BE GOVERNED BY THAT CERTAIN CONFIDENTIALITY AGREEMENT ENTERED INTO AS OF SEPTEMBER 2000 BY AND BETWEEN ENRON NORTH AMERICA  CORP. AND YOUR COMPANY.