Lost Creek Gathering Company, L.L.C.

Modifications to Contract Exhibits

Changed “Red Desert” to “Lost Creek” through out the documents.

Exhibit A

1.1 Overview

Changed location of compressor station to the Wamsutter site.

1.4 Design conditions

Corrected table column heading to “Discharge Pressure”.

For “Future” condition changed Discharge Pressure to 1000 PSIG.

Exhibit B

Section A, Substation

Data Sheet-“See attached one-line diagram” was checked.  This was in error and this diagram is to be furnished by Contractor.

Section C, Variable Frequency Drive

Data Sheet, Design Data-Nameplate horsepower was shown as 3800 HP.  This horsepower is to be determined by the Contractor based on the data in Exhibit A.

Section D, Variable Speed Medium Voltage Motor

Data Sheet, Enclosure-TEFC was checked.  We are advised that this may not be available for motors of  the size required in this application.