# Conference Call Notes

SUBJECT:		ABB Transformers for Las Vegas

Requirements Review

DATE:			September 28, 2000

PARTICIPANTS:	Mike Sandridge, ABB in Houston

J.Y. Davis, ABB in St. Louis

Chi Ho, ABB in St. Louis

Bruce King, Power Engineers in Boise

Don Hammond, Enron NA in Portland

This call was initiated to coordinate requirements for the two generator step-up transformers to be supplied by ABB for the expansion of the Las Vegas Cogeneration plant in North Las Vegas. Power Engineers, engineering subcontractor to the EPC contractor, has completed engineering necessary to determine parameters for the transformers.

The Purchaser Data Sheets for the units, ABB Design HU-Enron-2D-LS, were the basis for the conference call review. The following summarizes changes and additions to the information on the data sheets:

- Minimum/Maximum Ambient Temperature (ºC)			5/46

(maximum ambient revised from 40 to 46 to conform to

the 115 ºF Design Basis)

- Seismic Zone (per UBC – 1997)						2B

- Equipment Number							GSU-2A

## GSU-3A

(Equipment numbers to conform to Power Engineers

plant numbering system)

- Power for Auxiliary Devices

### Fans:		Volts / Phase						480 / 3

Pumps:	Volts / Phase						NA / NA

(Separate 120-volt single-phase and 480-volt three-phase

supplies will be brought to the transformer control cabinet)

- Impedance - % on OA base (84 MVA base)				13 %

- Surge Arrestor Required – (Yes / No)					Yes

#### Rating:									115 kV MCOV

Type:									Metal-Oxide

ABB – EXLIM

Action items:

- ABB to provide Enron NA a written confirmation of changes and a proposal for the contract revisions to implement

- Enron NA to provide ABB the location and carrier for nearest rail siding to the site for delivery planning

- ABB to provide Enron NA updated data sheets for the transformers indicating weights and dimensions for preliminary engineering