FIELD ACTION REQUEST

| Originator: ## Section A: ## X URGENT ROUTINE #### FAX to: (661) 823 - 6466 Date / Time: Site / Row / Pad #: Return FAX #: Return Phone #: | Matt Allsup |
| --- | --- |
|  | 5/30/02 1400 |
|  | Desert Sky / Curtailment PC |
|  | (915) 652-8634 |
|  | (915) 652-8650 / 638-3125 |

## Section B: To be completed by the originator.

| CONDITION The curtailment computer installed by Joe Chapman controls the turbines based on 10 minute average data and real-time data. By contract, we have 10 minutes to respond to a City Public Service curtailment request. Depending on the time of day we start a curtailment, the program can take up 10 minutes to respond to a request. If it takes this long and it does not shut down turbines fast enough, we could incur penalties from CPS (by contract). The biggest problem with the 10 minute average is that when a curtailment is officially lifted (when our SCADA operator or, in the near future, a CPS operator clicks the End Curtailment key) the program can take up to 10 minutes to respond. Since the curtailment is officially over, AEP is no longer getting paid for curtailed production OR PTC’s. We are curtailed almost every time we can produce more than 70 MW. That means that usually half the site is shut down. If the turbines are started on paper, but not producing until minutes later, neither us or AEP can capture that lost production. These large chunks of time, daily, for a whole month will be a huge amount of lost income for AEP. |  |  |  |
| --- | --- | --- | --- |
| LIST ATTACHMENTS: |  |  |  |
| REQUESTED ACTION: Rewrite the software so it responds in real time. |  |  |  |
| EW Part #: |  | Vendor: |  |

| Originator’s Signature: | Matt Allsup |  |
| --- | --- | --- |

Field Action Request

## Section C: To be completed by Project Coordinator.		Reference Number:     _______________

| INITIAL RESPONSE: |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Project Coordinator: |  | Date: |  | Time: |  |

## Forwarded to:	 Engineering  Quality      Manufacturing      Field Op. Group ______________

## Section D: To be completed by Originator and faxed back to Project Coordinator after receipt of the FARR.

Are you satisfied with the FARR?	 Yes, I am satisfied.      No, I am not satisfied for the following reasons.

| List of Reason(s): |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Originator: |  | Date: |  | Time: |  |