In accordance with the ISO Tariff and Metering Protocol (Section MP 4.2.1 Requirement for Audit Testing, (a) Audit and Testing by SC) states that each SC (Scheduling Coordinator) shall at least annually conduct (or engage an independent, qualified entity to conduct) audits and tests of Metering Facilities of the SC Metered Entities that it represents and the Meter Data provided to the SC in order to ensure compliance with all applicable requirements of any relevant Local Regulatory Authority (LRA).  SCs shall undertake any other actions that are reasonable and necessary to ensure the accuracy and integrity of the Settlement Quality Meter Data provided by them to the ISO. The following is a description of the review conducted in accordance with the ISO Tariff and Metering Protocol.

BACKGROUND Enron Energy Services LLC, a Delaware limited liability company, (EES) is a majority owned subsidiary of Enron Corp., an Oregon Corporation (Enron). Enron Power Marketing Inc. (EPMI) is also a majority owned subsidiary of Enron. EES is an Energy Service Provider (ESP) and utilizes EPMI as its Scheduling Coordinator (SC) for electricity. EES is responsible for activities including meter installation, testing, maintenance, testing and calibration for its customers. EES has outsourced these functions to a third party service provider. In addition, the third party has sub-contracted certain meter facility activities to Meter Service Providers (MSPs). An understanding of the procedures in place surrounding the meter facility process was obtained through a series of discussions with representatives of the above mentioned companies. EES is responsible for the functions relating to meter reading, VEE of meter data per LRA standards, and posting or transferring of meter reads per LRA standards. EES currently receives meter data by either polling EES meters directly, or by downloading data from the UDC MDMA Web-server. For meter data received via the UDC MDMA Web-server, the UDCs are responsible for the VEE of meter data prior to posting consumption data on the applicable UDC MDMA Web-server. Since these procedures are not under the control or supervision of EES, we must rely on the procedural information provided to us by the respective UDCs. As such, we requested and received copies of the relevant meter procedures from all involved UDCs [(Pacific Gas and Electric (PG&E), Southern California Edison (SCE), and San Diego Gas and Electric (SDG&E)]. The procedures we received also conveyed the process of meter reading, the meter reading schedules followed, VEE procedures and meter read posting. For meter data polled directly by EES, VEE of meter data is performed by AMR personnel utilizing programmed validation checks in the MV-90 or MAPS systems. MV-90 reads phone based meters and MAPS reads wireless meters. Once the meter data passes all validation checks, the meter data is transferred into the EES Cheops system, a meter data management system. All meter usage data is downloaded into Cheops from UDC websites and EES’s MV-90 server on a daily basis. The meter data is processed through the Cheops system where Load Profiles (“LP”) and Distribution Loss Factors (“DLFs”) are applied to meter data to determine SQMD usage by UDC demand zone in a CSV format. The SQMD usage in CSV format is converted into an MDEF format and submitted to the ISO on a daily basis - ISO CONTROL OBJECTIVE: METER FACILITY ISO Objectives: - Appropriate meter installation. - Meter testing is performed when required. - Meter maintenance is being performed when required. - Meter calibration is performed as required. Procedures in Place: ##### Procedures in place to ensure that Enron-metered and Utility Distribution Company (UDC)-metered accounts are properly identified and communicated: - Meter Field Operations (MFO) obtains pre-service request account data summaries and change requests from EES’ Operations and Maintenance Desk (OMD). The account data summaries are generated from data received from the applicable UDC (via the Sales/Account team). The change request initiates the meter pre-screening process, in which account history information is used to determine accounts over the specified Enron/Utility installation threshold. - MFO notifies Customer Set-up which accounts are to use Enron meters and which accounts are to use existing utility meters through a Metered Account and Relationship Listing form. Metered account data is loaded into MFO’s Scheduling Database. - Customer Set-up submits a Direct Access Service Request (DASR) to the applicable utility. Once a response DASR is received from the UDC, MFO captures the Enron Account Number from STAT, the company’s billing system. The Enron Account Number is applied to the appropriate customer in the Scheduling Database. - After the utility sends a Meter Investigation (MI) report to MFO, a project manager verifies that appropriate direct access service relationships are present and that the service request has been approved, using the Customer Set-up System. - Procedures in place to ensure that meter installations are properly communicated and monitored with MSP’s and tracked in meter management systems: - MFO schedules meter installations with two sub-contracted MSP’s. Required meter specifications (i.e. wireless/phone-based, configurations, etc.), MI reports and implementation plans are communicated to the applicable MSP using work orders. - MSP personnel communicate meter attributes (Current Transformer (CT), Potential Transformer (PT), meter type, communication specifications, etc.) to Automated Meter Reading Operations (AMR) personnel for update into MV-90 or MAPS, as applicable, the systems used for meter reading. Communication with the AMR center is established during meter installation, and a test read is performed while the MSP personnel are on-site. Meters are not considered installed unless communication can be established between AMR and the meter. In the event that communication cannot be established and a test read performed, the old meter is placed in service again and a new meter installation request is generated. - MFO field engineers monitor MSP records and accompany MSP personnel during meter installation on a discretionary basis as a quality control procedure. - MFO updates its Scheduling Database with the installation date and work order status, as necessary. - Procedures in place to ensure that documentation of meter specifications and meter installation are properly captured within meter-reading systems and communicated to the UDC: - Once a meter is installed, the meter serial number and multipliers are recorded on the installation work order. MSP personnel complete a Meter Installation/ Removal Notification (MIRN) and return the MIRN and completed work order to MFO for filing. Completed documentation is forwarded to AMR and the applicable UDC. - When AMR receives a MIRN, personnel compare the information contained therein with data previously captured in MV-90 or MAPS, as applicable. In the event that there are discrepancies, the MIRN supercedes any prior verbal communication. ##### Procedures in place to ensure that meters are properly tested during installation: - During meter installation, MSP personnel perform voltage, polarity, and connectivity tests to ensure proper installation. - Procedures in place to ensure that all meters are calibrated prior to installation at customer locations: - The California Public Utility Commission (CPUC) requires that meter manufacturers provide purchasers with certified documentation evidencing that the meters comply with all related calibration and accuracy requirements per related regulatory standards. - Process in place to ensure that scheduled meter testing/calibration is conducted per related CPUC requirements: - The CPUC requires that all accounts with usage greater than 2 million kwh/year are scheduled for testing on an annual basis. Accounts with usage ranging from 720,000 kwh/year to 2 million kwh/year are required to be scheduled for testing every two years. Accounts with usage less than 720,000 kwh/year are required to be tested annually on a sample basis. - Bi-annually, MFO develops testing schedules to meet CPUC requirements. Historical consumption data is obtained from AMR for analysis of maintenance requirements. MFO then develops implementation plans with the MSPs to test meter accuracy and replace meter batteries, as needed. - History of scheduled maintenance is maintained in the MFO meter management system. - Procedures in place to ensure that unscheduled meter maintenance is performed as required: - Unscheduled meter maintenance is performed when AMR has failed to communicate with a meter for three consecutive days or meter reads lie outside of the expected range when compared to historical data. In these instances, AMR contacts MFO to schedule field visits. - Meter data for meters requiring field visits are placed on a spreadsheet that is updated daily. The MFO project manager schedules a MSP to visit the customer location. Field visits are prioritized by bill cycle read date.

- ISO CONTROL OBJECTIVE: METER READING ISO Objectives - Meter reading schedules are being followed. - Validating, Editing, and Estimation (VEE) is being performed per Local Regulatory Authority (LRA) standards. - Posting of meter reads (where applicable) or transferring the meter reads are being performed per the LRA standard. Procedures: #### Procedures in place to ensure that all metered data is captured in meter reading systems: - MAPS and MV-90 are scheduled to automatically contact all interval meters daily. In addition, meters are contacted at the end of the applicable billing cycles. - MV-90 produces exception reports for meters that do not have meter reads. In the event that MV-90 has not received data from a phone-based meter for 3 consecutive days, a field visit and manual field read are scheduled. - MAPS records communication errors with wireless meters. Communication failures over a sustained period are investigated and scheduled for a field visit and manual read. ##### Procedures in place to ensure compliance with CPUC data validation requirements: - Data validation procedures are performed within MV-90 at the time data is received. Phone-based pulse counts are received and validated daily. Wireless pulse counts are validated monthly at the end of each bill cycle as data is downloaded from MAPS into MV-90. MV-90 data validations include the following checks per CPUC requirements: - Gap - Sum - Zero - Pulse overflow - High/low usage - Spike - Time stamp check of meter and meter reading device - MV-90 generates meter statistics reports for daily reads. From these statistics, AMR monitors expected versus actual meter reads as well as validation status. - Procedures in place to resolve failed data validations: - On a daily basis, MV-90 performs a time synchronization check between the meter and meter reading device. The meter time stamp should be time-synched with MAPS or MV-90, as applicable, within +/- 3 minutes. If phone-based meter time is within three minutes, MV-90 reads the meter and automatically resets the meter clock. Wireless meters must be reset manually by the operators. In the event that meters are greater than +/- 3 minutes out of sync, a field visit is scheduled. - MV-90 generates an exception report for each customer account. AMR personnel review the exception reports in order to investigate failed validations. The procedure for resolving a failed validation depends upon the nature of the failure. These procedures include activities such as field visits, comparison to historical data and communication with the customer. - Procedures in place to ensure compliance with related CPUC data validation record keeping requirements: - Post-VEE meter data is posted to the MDMA server and retained for at least twelve months, per CPUC standards. - Raw meter data is retained for a minimum of three years, per the related CPUC standards. It is noted that three years of data has not yet accumulated as the electricity market has only been open for competition for approximately two years. - Procedures in place to ensure compliance with related CPUC estimation requirements: - In certain circumstances, AMR estimates meter data five days after the end of bill cycle (estimates are flagged as such during data transmission). Estimates are performed manually within MV-90. - When the interval data to be estimated is two hours or less, data is estimated using point-to-point linear interpolation, per related CPUC specifications. - When the interval data to be estimated exceeds two hours, data is estimated using like days and times during the same period, like days and times within the past 90 days, or like days and times from the prior year. - AMR routinely reports the number of accounts and number of intervals containing estimated data via weekly “Percent Estimated Data” reports and graphs. AMR personnel use these reports to determine whether EES is complying with the CPUC requirement that no more than 10% of the accounts or 1% of the data intervals read monthly contain estimated data. - Procedures in place to ensure that all customer accounts are appropriately included in meter read transfers: - EES runs a sync up query with STAT, EES’s customer billing system, on a daily basis. The query identifies customer identification discrepancies, if any, between the STAT billing and CHEOPS meter systems. New customer account data (customer name, UDC account number, Enron account number, street address, load zone, and rate class) is downloaded into CHEOPS. Existing customer modifications (i.e. name, account number) are updated in CHEOPS. - At the end of each meter’s billing cycle, MV-90 posts consumption data into CHEOPS. Completeness of Enron-metered data transfer from MV-90 to CHEOPS is monitored by confirming that the expected number of interval counts for the applicable bill cycle has been exported. - To ensure integrity of meter read transfers, MV-90 transfers actual usage data to CHEOPS for settlement processing only after all validation checks have been passed. - UDC-metered data is downloaded from the applicable UDC via an EDI hub, and manually batch imported into CHEOPS. Import logs are monitored for transmission errors, and unusually large errors are investigated. - Procedures in place to ensure that Enron-metered interval data is posted to the MDMA server in a timely manner. - AMR generates performance reports, including a weekly “On-Time Meter Reads” report and graph, to identify how timely this data is posted to the MDMA server. These reports are reviewed to determine whether this data is being posted per the following CPUC requirements: - 80% of the meter data for reads scheduled to occur on a given date [i.e. Scheduled Read Date(SRD)], should be posted to the server on the day after the SRD. - 90% of the meter data should be posted to the server within two days after the SRD. - 99% of the meter data should be posted to the server within five days after the SRD. Findings: When MV-90 generates an exception report for each customer account detailing failed customer meter validations, there is no formal process in place to ensure that all validation resolutions are adequately documented. The system prompts the user to document all meter resolutions but does not require a user response. Response to Findings: EES’s new meter reading and management system MDMA 2.1, an upgraded meter reading and management system that is scheduled to be installed by mid 2000 for data validity tests in parallel with Cheops, will require a system user to document meter resolutions in the system. The system will automatically track the time and user ID for all changes made and will require a written response to document meter resolutions when installed.

C. ISO CONTROL OBJECTIVE: SETTLEMENT METER DATA PROCESSING ISO Objectives: - All SC Metered Entities represented are included in the SC’s SQMD file. - Load Profiles are applied properly (i.e. use of correct times and dates, and applied to the correct rate class). - DLFs are properly applied (i.e. use of correct times, dates, and voltage class). - Aggregation of meter data to the proper scheduling point. - Proper creation of the SQMD file. - Any estimation performed by the SC is documented and controlled. - Any calculations, in order to support Existing Contracts or logical (pseudo meters), are performed per the contracts. All meter data used in the calculation is reviewed in the same manner as any other load generation entity. #### Processes in Place - On a daily basis, the company downloads meter usage data from UDC EDI hubs and EES’s MV-90 server. For UDC usage, EES manually prepares an import log that details the number of records available on the hub and the number of records properly downloaded into the Cheops system. In the event that the percentage of records downloaded is not consistent with the prior day, EES contacts the appropriate UDC to resolve the discrepancy. - At the beginning of each day, static load profiles are manually imported into Cheops from UDC websites via an web server. The server downloads all new files posted to the UDC website since the date of the last read. A count of the number of UDC files opened and closed is logged. - On the first and fifteenth of each month, DLF’s are downloaded from the PGE, SCE, and SDG&E websites into Cheops via an EES web server. - When processing meter data, in the event that DLFs are missing from data downloaded from PGE, Cheops defaults the DLF value to one. This control ensures that usage data will be processed and included in the SQMD file. - After meter processing is complete, Cheops aggregates usage by Demand Zone based on information entered during the meter set up process. - CHEOPS automatically processes an SQMD file each night based on the date argument (day-39). - System-generated SQMD process logs are generated each night and examined the morning after the SQMD file is created. - EES personnel review the SQMD file for obvious errors such as reported volumes in MWH versus KWH. - After the SQMD file is sent to EPMI, reported usage is graphed against MDMA usage prior to application of load profiles and distribution loss factors. The reported usage is also graphed against the weekday specific average of MDMA usage prior to application of load profiles and distribution loss factors for the prior 4 weeks. (I.e. if reported usage is on a Monday, EES will compare the average usage for the prior 4 Mondays.) Abnormal usage trends and inconsistencies between reported usage and MDMA usage are investigated. In the event that the reported SQMD file is determined to be materially incorrect, SQMD files are resubmitted to the ISO with corrected data. - On a monthly basis, Cheops usage data is compared to STAT billing usage in total for reasonableness. Significant discrepancies and researched and resolved. - At trade date plus 39 days, EPMI receives SQMD usage files from its customers. EPMI’s FTP server automatically converts the customer usage into MDEF format and submits the document to the ISO. An e-mail notification is sent to EPMI when the file is submitted to the document. After submission to the ISO, EPMI performs a high level reasonableness check using scheduled and metered usage by demand zone. In the event that metered usage is determined to be inaccurate prior to trade date plus 45 days, EPMI resubmits customer usage to the ISO. Detailed Testing Procedures: In testing the accuracy of the settlement meter usage reporting process, 6/30/1999 meter usage by applicable load profile was tested on a scope basis. Since EES’s test environment was not functioning properly, EES reprocessed June 30, 1999 meter data through the Cheops production environment to generate SQMD meter usage in a CSV format. After selecting load profiles for testing, raw meter data associated with the load profiles selected was manually recalculated and compared to a Cheops report that detailed summarized, hourly usage by load profile. To ensure the accuracy of the summary by load profile, the report was compared to the hourly SQMD usage by demand zone for accuracy and completeness. The meter data tested included both interval and time-of-use meters read by EES, PG&E, SDG&E, and SCE. Under this testing methodology, if manually calculated meter usage associated with load profiles tested equaled usage on the summarized usage by load profile report, it was assumed that Cheops was properly processing meter usage downloaded into Cheops. Microsoft Excel models were created to replicate Cheops data processing procedures. The following explains the testing process in greater detail: - Interval Meter Usage. In testing the accuracy of interval meter data processed through Cheops, the UDC, Voltage Class and Demand Zone applicable to each meter was determined using customer information contained in Cheops. After determining the applicable UDC, Voltage Class and Demand Zone, Distribution Loss Factors (“DLFs”) were applied to the hourly meter data using DLFs downloaded from the PG&E, SDG&E and SCE websites. For each interval meter, total usage was calculated by adding the DLF usage effect to the raw meter usage. The total calculated usage was subtotaled by hour, load profile, and Demand Zone and compared to the 6/30/1999 Cheops report that details summarized hourly usage by type of meter (TOU and interval meters) and load profile. - Time of Use Meter Data. In testing the accuracy of time of use meter data processed through Cheops, the applicable UDC, Rate Class, Voltage Class, Demand Zone and Load Profile for each meter was determined by means of a Cheops meter query. Based on the Cheops query, usage was manually profiled using the applicable load profiles downloaded from the PG&E, SDG&E, and SCE websites. First, the applicable load profiles were copies into the Excel calculation model. Second, the total load profile was by adding hourly load profiles for all days during the measurement period. Next, the applicable Load Profile Factor for each hour (or half hour) was determined for the measurement period by dividing each hourly load profile by the total load profile amount. Finally, each load profile factor was multiplied by the total meter usage for the measurement period to determine hourly meter usage for each day during the measurement period. After determining profiled meter usage, the hourly meter usage was multiplied by the applicable DLFs downloaded from the PG&E, SDG&E, and SCE websites. Finally, the total meter usage by load profile was determined the by subtotaling meter usage for all time of use sample data by load profile. The subtotaled usage by load profile was compared to the 6/30/1999 Cheops report that detailed summarized hourly usage by type of meter (TOU and interval meters) and load profile. ##### Total SQMD Meter Usage. In testing the accuracy of the Cheops report that details summarized hourly usage by type of meter (TOU and interval meters) and load profile, meter usage by hour and Demand Zone on the report was subtotaled and compared to the SQMD meter usage file generated by processing 6/30/1999 meter data through the Cheops system. ##### MDEF Conversion. In testing the accuracy of the MDEF conversion process, 4 days were selected during the testing period. For each day, a comparison was made between the Cheops generated SQMD usage file in CSV format and the MDEF file submitted to the ISO. Findings Related to Testing Procedures: - When profiling time of use meter data, Cheops uses static load profiles rather than dynamic load profiles. Although utilizing dynamic load profiles is not required by the ISO for reporting purposes, when available, dynamic load profiles should be used to process time of use meter data to increase the accuracy of usage reported to the ISO. - Currently, there are several discrepancies between manually calculated and Cheops calculated meter usage. EES is currently investigating all discrepancies. This finding will be finalized the week of May 1st, 2000. - In the event that Cheops cannot identify the proper PGE demand zone for a particular meter read, the processed usage will default to PGE3 and will appear on an exception report. Discrepancies on the exception report are not investigated on a daily basis. The company should ensure that all discrepancies on the exception report are resolved on a daily basis to ensure accurate ISO reporting. Response to Findings Related to Testing Procedures: - During 1999, Cheops used static load profiles, since the ISO did not require use of dynamic load profiles. However, since January 2000 Cheops has started using dynamic load profiles. - Investigation currently in progress - response to be submitted to auditors within the next week. - When zone data had not been provided for a particular PGE account, Cheops does default the usage to zone PGE3. This is done to insure the usage data is included in the settlement file and enhances the integrity of the data. Going forward, a member of the operational staff will be assigned the task of providing discrepancy reports to business area management and resolving the discrepancy and updating the account data with the correct load zone information. Other Findings: - Cheops does not have an automated validity check to ensure that meter usage posted to the UDC website includes all EES customers that should be included in SQMD reported usage. When downloading meter usage from UDC websites into the Cheops system on a daily basis, Cheops does not generate an exception report detailing meter usage not properly downloaded into the system. Currently, EES manually generates a download report that indicates the number of records downloaded into Cheops and the total number of records available on UDC websites. In the event that selected records are not properly downloaded, EES does not research all exceptions to ensure the completeness of meter usage reporting. If the percentage of records loaded is consistent with the prior day, the company does not research discrepancies. If the percentage of records loaded is drastically different from the prior day, the company contacts the applicable UDC to resolve the problem. - When reporting selected February 2000 meter data to the ISO, SCE load profiles were not properly applied to time of use meter data. The problem was encountered during a day-to-day reasonableness review of meter data. The problem resulted when the UDC changed the format of load profiles posted on its website. EES’s webserver did not recognize the format change and failed to include all SCE TOU usage in the SQMD file submitted to the ISO. - In the event that all load profiles are not properly downloaded from UDC websites into Cheops via EES’s webserver, the corresponding time of use meter data will not be processed or included in the SQMD reporting file. Additionally, there is no control in place to ensure that the UDC load profiles have been read completely and accurately. - Cheops does not have a validity check to ensure that all DLFs are loaded into the system on a daily basis. In the event that DLFs are not loaded into Cheops on a particular day, the system should apply a default DLF for all UDCs to ensure that meter usage is reported in megawatt hours rather than kilowatt hours. - Cheops does not have the capability of generating an exception report detailing DLFs that are not downloaded into the Cheops system. During October 1999, selected DLFs for all UDCs were not loaded into the Cheops system. In calculating SQMD usage, all DLFs were not applied to meter data resulting in SQMD usage reported to the ISO in kilowatt hours rather than megawatt hours. Response to Other Findings: Last year, as part of the review of our meter data settlement processes, EES initiated steps to upgrade the existing meter reading and management system, Cheops, in order to ensure the production of error-free SQMD. Cheops was originally designed to operate under an ideal environment and did not have the capability to monitor bad data, missing data, or exceptions. Our resolution was to replace the Cheops system with the MDMA 2.1 system, which would address all the functionality gaps mentioned above. The timeframe for this transition was established to be the 3rd quarter of 1999. However, because of EES’ decision to outsource billing and metering data management to a third party (CSC), time constraints, loss of resources, system problems and related data problems have slowed implementation from expected date. In the interim, high level processes have been put in place, outside of Cheops, to facilitate validation of SQMD as indicated above. Problems with data validation, data submission and data format etc., were addressed as they arose last year on a reactive basis. Since EES intended to move to the new MDMA system, we did not want to invest heavily in Cheops to make it more responsive to the California market nor to make it our long-term solution. Some of these fixes were as follows: - During October last year, as indicated above, DLF's were not loaded into the CHEOPS system and therefore not applied to meter data, as a result of which SQMD usage was reported to ISO in Kilowatt hours instead of megawatt hours. This happened because the DLF extract and import process failed to execute according to schedule. Examination of schedule failure is attributed to not being re-started after routine system maintenance was performed. The DLF process has since been manually submitted twice monthly to run. Operational staff has been increased and assigned responsibility of running and verifying all DLF data has been loaded into the CHEOPS system. - During February 2000 SCE load profiles wer not properly applied to time of use meter data. The problem resulted when the UDC changed the format of load profiles posted on its website. The Cheops system could not recognize the format change and failed to include all SCE TOU usage in the SQMD file submitted to ISO. To address this problem, the load profile extract program has been changed to read and process records in the supplied SCE file format. Load Profile records used by the CHEOPS system to calculate the SQMD file contents are now being monitored by operational staff on a date and time level for each load profile record stored. Fixes such as those mentioned above have allowed us to stay functional, although the process is still far from being efficient and optimal. Realizing the urgency of the situation, EES has initiated a high priority effort to address the shortcomings of our MDMA. In doing so, the following activities are currently underway: - Development of a system that utilizes our CIS/billing/forecasting systems to estimate settlement obligations to the CAISO. This system produces accurate estimates of metered load by zone and will be used as a measure to evaluate settlement data. The expected completion date is 5/10/00. - EES is working with Tenfold, the creators of Cheops, on an expedited basis to bring the original system designers to EES to operate the system and to troubleshoot all current and potential problems. They will also perform an Enhancement Analysis to arrive at a cost for migrating Cheops to a more robust environment. Negotiations with Tenfold will be finalized on 5/1/00. - The date for completing MDMA 2.1 is expected to be 5/15/00. After that a testing period of approximately one month will occur before MDMA 2.1 will be placed into production.