Exelon Questions and Answers: Lincoln Energy Center

October 24, 2000

DLN Combustor Mods

- Specifically, what DLN combustor modifications are being recommended by GE.  Are mods to be implemented on all units?

In general, they are changing the dilution hole sizes in the liners, changing the effective open area of the primary and secondary nozzles and modifying (reducing) the firing rate curves.  Modification is in progress, and will be completed by the end of this month.

- Who is paying for the mods?  How much?

GE is picking up the entire cost.

- What is guarantee as a result of modifications?

The modification will fall under the same warranty provisions as the original equipment.

- What effect will mods have on the Megawatt operating range, start-up, or ramp rate of a unit?  Will operations be changed or restricted in any way?

The modifications should result in no change to the operational profile.  In fact, if the profile is changed, this would be grounds for a warranty claim.  GE has committed to having no effect on operations, other than lowering Nox, CO, and firing temperature.

- What effect will mods have on unit heat rate?

Should have no material effect.

- How many other GE-7EA units have had similar issues?  Can we have references?

GE did provide a graph during their presentation that illustrated this issue affected the entire fleet of 9 ppm DLN 7EA machines. The graph did not disclose the Owners of the other units, nor did GE provide us a hard copy of presentation material.

- Will the unit be compliant over the entire operating range?

The contract guarantee still applies.

- How does the mod impact spare parts? i.e. stocking levels, cost, etc…

The project does not currently have liner/nozzles in spares, so there should be no effect.

No. 7 Generator Failure

- Strand insulation failure at the end is typically related to age and not ascribed to any reason other than fabrication defect.  If all unit coils came from the same supplier and units were fabricated at the same time, how can we GE claim that the remaining units are unaffected?

GE continues to investigate the Root Cause Analysis (RCA), but has stated that other units are not affected.

- What was the root cause for No. 7’s generator failure?

See DealBench Doc # 04.01.04

- Are other units at risk for similar failures?

See DealBench Doc # 04.01.04

- Who paid for No. 7’s repairs and is there a warranty with the new work?

GE paid for repairs in accordance with initial contract warranty provisions.  New work should fall under the same warranty provisions as original equipment. Also, see DealBench Doc # 04.01.04.

- Are there any recommendations for on-line monitoring of the units to pick-up warning signs that the problem exists in the other units?

No such recommendations received from GE/Brush. GE did request that we perform  visual inspection at convenient opportunities but did not specify actual frequency. All units have been inspected by GE/Brush/OEC as part of the work-scope currently underway.

Long Term Service Contract

- Is there a long term service?  If so, what is included in the scope of work and what are the costs associated with the contract?

There is no LTSA with GE.

No. 6 Compressor Blade Failure

- Please provide copies of all documentation associated with the failure, such as root cause analysis report, inspection reports, repair cost, etc…

On Monday October 16 th, Unit No. 6 was dispatched for operation and was synchronized and subsequently base loaded at 6:00 am. with no difficulties or abnormalities noted during the startup. Around 7:30 am, the unit transferred into an extended lean-lean firing condition and in conjuction received a high vibration alarm. The unit was manually being unloaded to get out of the lean-lean firing mode when the unit tripped on a high exhaust temperature.  The unit coasted down and it was put on rachet for cooldown.

A boroscope inspection was performed on the unit the following morning where it was noted that a rotating blade on the seventeenth stage had broken loose at the root and caused damage to both the sixteenth and seventh stages (rotating and stationary).

GE is currently onsite tearing down the unit to remove the compressor rotor with plans to ship it to the Cincinnati repair shop for an unstacking of the rotor and replacement of the sixteenth and seventeenth rotating stages. Repairs for the stationary components will take place onsite. GE has all necessary parts lined up and expect to return the unit to service by the 30th of November.  GE has recognized and accepted the warranty claim and all cost associated with the repairs.

THE INFORMATION CONTAINED HEREIN IS BEING PROVIDED TO YOU PURSUANT TO AND SHOULD BE GOVERNED BY THAT CERTAIN CONFIDENTIALITY AGREEMENT ENTERED INTO AS OF SEPTEMBER 2000 BY AND BETWEEN ENRON NORTH AMERICA  CORP. AND YOUR COMPANY.