EXHIBIT A-1

LOST CREEK GATHERING COMPANY, L.L.C.

LOST CREEK GATHERING STATION

CONTROL SPECIFICATION FOR

STATION CONTROL SYSTEM AND UNIT CONTROL PANELS

TABLE OF CONTENTS

1.0	GENERAL

2.0	SCOPE OF SUPPLY

3.0	SYSTEM DEFINITION

4.0	       HARDWARE SPECIFICATIONS

5.0      SOFTWARE

6.0	CONTROLLER FUNCTIONS

7.0       CONTROL SYSTEM CALCULATIONS

8.0	COMMUNICATIONS

9.0	MAN/MACHINE INTERFACE

10.0	ALARMS AND SHUTDOWNS

11.0	DOCUMENTATION

12.0	TESTING

13.0	COMMISSIONING

14.0	FINAL ACCEPTANCE

15.0	WARRANTY

16.0	CONTROLS INFORMATION

1.0	GENERAL

1.1	Overview

This specification describes the requirements for the design, manufacture, factory test, and commissioning of a station control system and unit control panels for Company’s Red Dessert Gathering Station.

The control system shall generally consist of the following components:

a.	unit control panel

b.	station control system

c.	software and documentation

1.2	Compressor Station

The compressor station will be designed for unattended operation except for minimal operator interface during daylight hours. The station control system will receive operating data from the compressor units. The operator will be able to monitor system operation and control critical functions. The panel will provide facility status communications to Company’s gas control and allow Company’s gas control to monitor and operate the facility.

The compressor units will be either two or more skid mounted high speed, lean-burn, engine driven high speed separable compressors or, as an alternate, one or more skid mounted variable speed motor driven high speed separable reciprocating compressors. Each unit will have its own control panel which will interface with the station control panel.  Certain requirements apply only to the gas engine drive or only to the motor drive.

The configuration envisioned in this Specification will use independent controllers for the unit control panels and a primary controller for the station control system. The two unit panels and station control system will be linked via a networking system. The station control system will contain a controller that will monitor or control; station alarms, shutdowns, pressure control, and sequencing. It will also issue instructions via peer-to-peer communication to the unit control panels.

The unit panel controller will provide the remote/ auto /manual start-up/alarm/shutdown logic and unit optimization including air/fuel ratio, speed, ignition, and torque. The station control system will get its data and send supervision instructions via peer-to-peer communication with the individual unit control panels.

The requirement for the control panels hardware and software are described in this Specification. Should the Contractor be knowledgeable of additional requirements, he shall so state in an attachment to his quote.

Every effort is being made to provide Contractor with sufficient information to supply the system described by this document.  It is the intent of this specification to obtain a stand alone system capable of the sole control of the station and units described. The primary requirement is that the system be reliable. Formulas, subroutines, and other like functions shall not be divided into incremental pieces and distributed throughout the program. The program shall be as simple and straightforward as possible.

Contractor may propose alternates but his base price shall comply with these requirements. Any alternates shall be separately priced.

The validity of the algorithms provided by Company is the Company's responsibility; however, the implementation of these algorithms and any other implied functions are the Contractor's responsibility. If there is a conflict in this document or insufficient information to complete a task, it is Contractor's responsibility to contact Company to resolve the problem.

The values, tag numbers, and names used in the formulas and displays are examples and are not intended to represent the actual system requirements. However, if others are utilized Contractor must strive to use logical alternates.

Electrical power will be provided by the local utility company. A back-up generator will be provided to generate emergency power.

2.0	SCOPE OF SUPPLY

Contractor's scope of supply is as follows:

2.1	Station Control System

a.	IBM Compatible Personal Computer

b.	Modbus port expander

c.	Report Printer

d.	Alarm Printer

e.	Modem(s)

f.	Interconnecting Wiring and Cables

2.2	Unit Control Panels

2.3	Operating Software (including manuals) - 2 Copies

2.4	Diagnostic Software - 3 Copies (Including reference text and manuals)

2.5	Certified Drawings and Operating Manuals - 3 Copies

3.0	SYSTEM DEFINITION

3.1	Control System

The system shall be designed for fail-safe operation where individual components are de-energized for the safe condition.

The basic concepts of the control system are as follows:

a.	Unit alarms will be duplicated to the central PLC for database/report generation and for access by Company’s Gas Control.

b.	Shutdown of the individual units will be done by the unit panels.

3.2	System Configuration

The system configuration shall be commensurate with the required inputs and outputs that are to be connected to the unit control panels and station control system.

3.3	Station-Control System Functions

The Station Control System shall perform the following functions.

a.	Station throughput via metering supplied by others.

b.	Communication to and from Company’s Gas Control.

c.	Annunciate station alarms & shutdowns.

The Station Control System shall provide access to all the information and controls contained in the Unit Panels as well as provide the necessary Man/Machine Interface for station operations.

Failure of a valve to reach the required position shall result in a "Valve Sequence Failure" alarm as well as graphic indication of the malfunctioning valve.

Operation of Station Side Valves

The Control System shall monitor the corresponding differential pressure switch before issuing or allowing OPEN commands to the station side valves and by-pass valves. An open differential pressure switch indicates a differential pressure higher than 50 psi across the valve, and requires that the equalization valve be opened first for pressure equalization. The Control System will issue or allow opening of these valves only after confirming that the corresponding differential pressure switch has closed, indicating a safe differential.

3.3.1	Gas Flow Metering:

Each meter tube has an inlet block valve, an orifice fitting and an air-operated automatic control valve. Each orifice is equipped with three field-mounted two-wire transmitters which output 4-20 mADC signals corresponding to differential pressure, static pressure, and temperature.

Flow setpoints for the compressor(s) (flow control algorithms) will be operator keyboard entries at the SOC, or entries at the flow computers keypads in the LOCAL Control Mode. In the REMOTE Control Mode, the flow setpoints will come from Company’s Gas Control.

3.4	Unit Control Panel Functions

The Unit Control Panel shall perform the following functions:

a.	Unit operating parameter and safety monitoring.

b.	Unit starting, stopping, and loading sequence.

c.	Torque control

d.	Speed control

Refer to Section 6.0 of this specification for detailed descriptions of the functions of the Unit Control Panel.

3.5	SCADA INTERFACE

Company’s Scada System will be connected into the control system via the Modbus port. The Scada System provides access to all information for all connected controls, alarms, shutdowns, and monitoring devices. The Scada System allows Company’s gas control to initiate a station shutdown or individual unit shutdown, individual unit startup, and flow rate, suction, and discharge set point controls.

3.6	Reference Specifications

This specification covers the general requirements of the unit and station control system. Other requirements of the system are covered in the Project Specifications.

3.7	Codes and Standards

Except as otherwise provided herein, the control system specified under this Specification shall meet all applicable requirements set forth in the following codes, standards, or regulations, which form part of this Specification. Later editions of these codes, standards, or regulations may be used, provided that the Manufacturer and/or Contractor certify that the control system also complies with all requirements of the codes, standards, or regulations listed herein.

a.	National Fire Protection Association, NFPA 70 (1993) - National Electrical Code

b.	American National Standards Institute, ANSI MC8.1 (1975) - Recommended Practice for Hardware Testing of Digital Process Computers

c.	Instrument Society of America, ISA-RP12.1 – Electrical Instruments in Hazardous Atmospheres

d.	Instrument Society of America, ISA-S5.1 - Instrument Symbols and Identification

3.8	Precedence of Documents

In the event of a conflict between this Specification and the Project Specification, or drawings approved by Company, Company shall be informed and Contractor shall obtain a written decision on the conflicting matter from Company.

Any deviation from this Specification desired by Contractor shall be brought to the attention of Company. Contractor shall obtain approval from Company for such deviation. For substitution of any item specified, Contractor shall obtain written approval stating that said substitution is a Company-approved equal.

Any exceptions to this Specification shall be documented in Contractor's quotation.

3.9	Ambient Conditions

The Control System provided under this Specification shall be suitable for installation and operation indoors as follows:

a.	Panel: -20°F to 140°F. 90% R.H.

b.	Station Control System: 68°F to 80°F, 70% R.H.

c.	All equipment, when shut down shall be capable of withstanding a maximum temperature of 122°F and a relative humidity of 100% without electrical damage or degradation.

4.0	HARDWARE SPECIFICATIONS

4.1	General

Company has a strong preference for a control system manufacturer that has substantial market share, has multiple sources of stock parts on the shelf, and a large available pool of programmers. Considerable importance will be given to those manufacturers whose hardware and software have traditionally been upwardly compatible with future generation equipment. The controllers shall be either distributed control systems or programmable logic controllers. Available choices are covered in the Project Specifications in Section 8.2.

Power in the station consists of 120 VAC, 60 Hertz, single-phase, with a dedicated circuit for the Station Control System and 24 VDC for the unit panels. Each power source is supplied by uninterruptible power supplies.

A single processor failure or power supply failure should not cause the entire system to fail nor should it cause the communications link to Comapny to be severed, though some degradation in performance may occur.

The Unit Control Panels shall be able to independently operate the units even if there is a total failure of one of the other unit panels or the Station Control System.

All I/O shall be protected against lightning and surges with optical isolators, avalanche diodes, gas tubes, or metal oxide varistors. If not built into the I/O module, external protection must be provided.

It is the intent to connect the field wiring directly to the I/O terminals; however, no more than 2 wires per terminal shall be permitted. Otherwise, a field wiring terminal block shall be provided. (For example, a module with 4 signal terminals but only 1 common terminal). All inner panel wiring, including power distribution to the I/O shall be completed by Contractor.

An I/O list for the Station Control System and for a typical unit panel are discussed in the Project Specifications. A revised I/O list may be issued after bidding. The I/O shall be powered from internal power supplies. Fuses or other current limiting circuitry should be incorporated into or at the I/O modules to prevent a single short circuit from taking down the entire system and shall have a sufficient inrush and continuous current rating to drive the solenoids directly (5 amps inrush and 2 amps continuous at 24 VDC).

4.2	Unit Panel

Equipment installed at each unit panel must be packaged to meet a Class 1, Group D, Division 2 area classification and a 140°F ambient temperature rating. Unless the equipment is listed by FM or UL for use in Division 2 areas it shall be packaged in a class Z purged enclosure as per NFPA #496.

4.3	Station Control System

The Station Control System shall have a hot standby processor.

The station processor, I/O, and other accessories shall be mounted in one or more free standing 19" rack enclosures. They should be approximately 21”W x 30"D x 72"H. (Rital 4000 series or Company approved equal). All wiring into this enclosure shall be from the bottom. PVC wireways are to be installed to route field wiring through the enclosure to the I/O.

The Man/Machine interface shall be a 64-bit Pentium II compatible PC, 128 Mbyte of RAM (minimum), 11 Gbyte (minimum) hard drive, 3.5” 1.44 Mbyte diskette drive, 32x CD ROM drive, 2 serial and 2 parallel ports, SVGA graphics and 19” multi sync monitor, spill-proof keyboard, mouse, and other hardware and software (Wonderware) necessary to support the software package. This PC system shall be approved by the Company.

An Epson 850FX printer shall be provided as an event logger and an Epson 1050FX shall be provided for the report generator. All connecting cables required to connect the PC, printers, and controller together shall be provided by Contractor.

4.4	Field Devices

All field devices to be monit6rod and/or controlled shall be provided and installed by Company. Field device characteristics shall generally be as follows:

a.	Discrete Input: Switch or relay dry contacts rated for 24VDC or 120 VAC.

b.	Discrete Output: 24VDC solenoid valves at 30W maximum; 24VDC relays at 3W maximum; and 120VAC starter coils, NEMA size 3 starters maximum.

c.	Analog Input: Two-wire, 4-20 mADC into 250 ohms maximum.

d.	Analog Output: 4-20 mADC into 600 ohms minimum.

e.	RTD Input: 3-wire, 100 ohm platinum.

f.	Thermocouple Input: ISA Type J. (Unit Panels only).

All devices shall be powered from Contractor furnished redundant power supplies, unless otherwise noted.

5.0	SOFTWARE

5.1	General

The PLC/DCS shall handle communications, data acquisition, sequencing, shutdowns, startup, analog control, PID control, and those mathematical calculations used as part of a control algorithm (fuel flow, horsepower, etc.).

The code for the PLC/DCS shall be as small and concise as possible with no extraneous code carried over from previous projects. Contractor shall work jointly with Company before starting to write code as to how the system is to be mapped, scheme for tagging, and how and where the required functions are to be implemented.

System download of new set points for alarms, shutdowns, control parameters, etc. shall not fail the unit.  In case of download the system will go into a default fail in place mode.

5.2	Curves

For the purpose of this specification, the "curves" referred to in various formulas mean that for an input, as read on the "X" axis should produce an output, as read on the "Y" axis. Contractor should not assume that the curves will be or remain linear.

Contractor shall provide a technique most appropriate for each curve that will generate an output for a given input that tracks the curve. This could include a "look-up table", linear segments, curve fit, or formula. The true engine curves will change over time and will need to be redefined in the program. A straightforward method of entering new curve data shall be provided.

Contractor shall provide a means of correlating the compressor torque to the variable frequency drive’s speed, voltage, amperage and frequency.

5.3	Time Class

All functions shall be assigned to operate in a designated time class and shall complete their task within the specified time.

< 250 ms	The PID, torque, and speed control algorithms should be executed within this time period.

> 250 ms	The digital inputs and outputs, alarms and shutdowns, thermocouple inputs, pocket loading, setpoints, and miscellaneous mathematical calculations shall operate in this time class.

Analog I/O may be multiplexed provided their functions can be executed within the designated time class; otherwise, do not multiplex those specific functions.

5.4	Implementation

Contractor shall develop the software so that it performs all the functions as required by this Appendix.

5.5	Set Point Tuning

The software supplied shall provide the ability to enter set points for control, alarms, and shutdowns in the unit panels from the Station Control System, as described in Section 9.0, Man/Machine Interface.

6.0	CONTROLLER FUNCTIONS

6.1	General

The various functions that the controller must perform are detailed in this section. Algorithms to perform certain tasks are provided; however, alternate algorithms that perform the same functions but are easier to implement may be substituted with Company approval. Algorithms of a more general nature in most equipment's development package such as PID, AGA 3, curve fit, or matrix functions are not described in detail.

6.2	Station Pressure and Flow Control

Station control is accomplished in the Station Panel by varying the speed of the compressors in order to maintain the desired suction pressure, station flow rate, and discharge pressure. The following rules apply:

a.	The most efficient operation is when the units are operating at their maximum rated speed and maximum rated load. Each unit is assigned a sequence number by the operator through the MMI. The unit with the highest sequence number is the "swing unit" and is the first unit to be controlled by the central PLC. The other units operate at the maximum rated speed and maximum rated load. Contractor shall incorporate the option to swing more than one unit together as a group.

b.	The units are controlled by the central PLC sequentially, starting with the unit assigned the highest sequence number (last in first out).

C.	A unit placed in the "manual" mode is removed from the control sequence and will run at the local/manual setpoint speed entered by the operator for the Unit Panel.

d.	Start up of a unit can be accomplished in three modes; manual, auto, and remote. Under manual mode, unit start up will be handled by the operator at the unit panel by stepping through the sequences by pushbutton. In auto mode the operator will initiate the start up sequence by depressing a start up pushbutton. All subsequent activities are performed by the unit PLC. In the remote mode, unit start up will be handled by the station operator by software command.

e.	As the required throughput of the station declines, the station control system will ramp the speed of the unit with the highest sequence number down slowly to meet the required throughput. If the required throughput is still not met then the speed of the unit with the next highest sequence number will be reduced.

If the setpoint conditions cannot be satisfied by backing all the units to their respective minimum allowable speeds, than a negative bias is added to the torque setpoint of the "swing" unit to force it to unload. This ramp should be slow enough to allow the unloading process to occur. The unloading is stopped when setpoint conditions are satisfied. If the conditions are not satisfied, the other units are unloaded sequentially. Units in "manual" mode are not subject to this unloading criteria.

f.	If both units are running at minimum speed and are totally unloaded, the unit with the highest sequence number will be automatically shutdown after 15 minutes.

g.	If one unit's air manifold pressure drops below 4" Hg for 15 seconds then this unit will be shutdown.

h.	If the station discharge pressure Hi Hi is met, sequentially shut down units until the discharge pressure drops below the Hi Hi set point.

i.	If a unit's % rod load exceeds a specified value, the excessive rod load alarm will be tripped. If the rod load continues to increase the unit will be shut down.

It should be noted that an engine may have a governor whose 4-20 Ma input corresponds to a 50-100% speed whereas the allowable operating range is only 90-100% speed. Selection of the sequence order, local setpoints, and "manual/auto" speed choice for each unit is made through the MMI. The tuning constants shall be introduced through the station PLC and not through the MMI, i.e., not available to the station operator. Remote setpoints are downloaded from the SCADA system. The setpoints and process variables shall be entered and displayed in engineering units.

6.3	Torque Control

Torque control is in the Unit Panel. The premise behind torque control is that an engine operates most efficiently when it is operated at full rated torque. Torque is controlled by the Unit Panel by increasing or decreasing the cylinder clearance (volume) in the compressor cylinders. Increasing the clearance reduces the torque and reducing the clearance increases the torque. Fixed amounts of clearance are added to the compressor cylinders by opening bottles called unloader pockets. Generally, there are multiple pockets of various sizes mounted on each of the compressor cylinders. Solenoids are used to switch instrument air to pneumatic actuators mounted on the pockets which either open (solenoid de-energized) or close (solenoid energized) the valves to the pockets. Closing pockets increases the torque and opening pockets decreases the torque. A predetermined pattern of open and closed pockets forms a load step. A table of these load steps is called a load step matrix. Load steps are numbered from 0 to n, where step “0” indicates a fully loaded (all pockets closed) configuration and step "n" indicates a fully unloaded (all pockets open) configuration.

A switch shall be provided on the front of the unit panel to select manual torque control or automatic torque control In the manual position, the operator may open or close individual pockets by way of individual switches on the front of the panel.

For automatic control, the percent torque is calculated for a compressor unit based on a curve of Specific Fuel Consumption versus Torque, energy into the unit, and unit speed. This curve is based either on empirical values supplied by the manufacturer or on engine analysis. See equation #4 (note that equations #2 and #3 must be solved first). Once the percent torque has been calculated, the proper load step can be selected to match the desired operating percent torque.

The torque controller uses the rules described below to increase or decrease the engine torque in order to match the operator entered setpoint. The torque controller will assume a 50% torque until the engine reaches its minimum allowable speed. At this time, the actual calculated torque is compared to the torque setpoint and load step is increased or decreased if required.

The software package, shall provide a two dimensional matrix with the load steps on one axis and the pocket numbers on the other. The station operating personnel will enter "ones" or “zero’s” in the matrix to indicate which pockets are closed or opened, respectively, for a given load step. The software shall incorporate an index pointer to "read" the matrix to control the clearance pockets.

The matrix shall also provide the ability to exclude a particular pocket (or pockets) from automatic control and leave it (them) in either the open or closed position.

There is a finite clearance associated with each pocket which will be entered into the PLC by the station operator as basic data. The PLC shall calculate the clearance for each load step for use in the unit algorithms.

The load step controller operates using the following rules:

a.	The index pointer always returns to the fully unloaded state which is the "n"th, or highest step whenever the unit is manually stopped or is automatically shut down by the system.

The index pointer always moves from one step to another in sequence (1,2,3 or 7,8,9) with an adjustable time delay (0-5 min) at each load step. It never jumps (1,10 or 8,2). The loading time delay is different from the unloading time delay.

c.	With the index pointer on a given load step, the actual % torque being developed is calculated (equation #4) and is compared to the % torque setpoint. Whenever the actual % torque is less that the % torque setpoint minus a deadband, the load step is increased by one (load). Whenever the actual % torque is more than the % torque setpoint plus a deadband, the load step number is decreased by one (unload). This procedure continues until the % torque is within the deadband.

d.	If % torque (plus a deadband) is equal to or exceeds 105%, the over-torque alarm shall be set and shutdown will be activated within 2-3 minutes. If no action is taken, then the unit will be shutdown. At 110% torque the unit shall be shut down immediately.

e.	The torque setpoint may be negatively biased by other control algorithms in order to achieve a safe operating condition.

7.0	CONTROL SYSTEM CALCULATIONS

7.1	Fuel Gas Flow

(Equation #1)

Fuel flow is required for a number of calculations to be mentioned later. The orifice constant should be determined in accordance with American Gas Association (AGA) Report #3. All other dependent variables should be continuously measured for best results.

Qf	=	C1 x	hw x(Pg+Patm)

SG x Tg

Qf	=	Orifice Meter Flow (MCF/HR)

C1	=	Orifice constant per AGA #3 (dimensionless)

hw	=	orifice meter differential pressure ("H20)

Pg	=	Orifice meter static pressure (PSIG)

SG	=	Fuel gas specify gravity (dimensionless)

Tg	=	Orifice meter gas temperature (°R)

Patm	=	Atmospheric Pressure (PSIA)

7.2	Ambient Rated Horsepower

(Equation #2)

HPar	=	HPsr + Tconst1 (Tconst2 – Tam)

HPar	=	Ambient rated horsepower

HPsr	=	Site rated horsepower

Tam	=	Air manifold temperature, (lowest temperature for vee engines)

Tconst1	=	Ambient rated constant

Tconst2	=	Ambient air temperature (°F)

7.3	Fuel Horsepower

(Equation #3)

HPfuel	=	Qf x SFC-PL x HPar

(1-FL)

HPfuel	=	Fuel Horsepower (HP)

SCF	=	Specific Fuel Consumption (BTU/HP HR), curve lookup

FL	=	Friction Loss (dimensionless), constant

HPar	=	Ambient Rated Horsepower (HR), Equation #3

Qf	=	Fuel flow (SCFH)

7.4	Torque Calculated

(Equation #4)

Torquecalculated	=	HPfuel	x	RPMrated	x 100

HPar		RPMactual

Hpfuel	=	Fuel Horsepower (HP), Equation #4

Hpar	=	Ambient Rated Horsepower (HP), Equation #3

SFC	=	Specific Fuel	Consumption (BTU/HP HR), curve	lookup

FL	=	Friction Loss (dimensionless), constant

RPMrated	=	Design speed (RPM)

RPMactual	=	Measured speed (RPM)

7.5	Unit Torque

Since torque must be indirectly determined an iterative process must be used to determine Actual Torque.

Calculate Fuel Flow Using Equation #1

Set TORQUE assumed to 50%

Lookup SFC from SFC vs. Torque Curve

Determine Fuel Horsepower Using Eq. #3

Determine TORQUE calculated Using Eq. #4

TORQUEcalculated – TORQUEassumed – Delta

T

Is Delta > 0.5%	Decrease TORQUEassumed by 0.5%

F

T

Is Delta < 0.5%	Increase TORQUEassumed by 0.5%

F

TORQUEcalculated – TORQUEassumed – Delta

As illustrated on the previous page, the iteration begins by assuming a Torque, using that value of Torque and a Specific Fuel Consumption (SFC) vs. Torque curve to determine SFC for the assumed Torque value.

The next step is to calculate (Equation #3) Fuel Horsepower using Fuel Flow (Equation #1), the SFC determined in the pervious step, Friction Losses (constant) and Ambient Rated Horsepower (Equation #2).

The next step utilizes the previously determined Fuel Horsepower along with Ambient Rated Horsepower and the ratio of actual and rated speed to determine Calculated Torque (Equation #4).

The process just described is iterated until Assumed Torque approaches Calculated Torque. At that point Assumed Torque equals Actual Torque and that value is used in the torque control strategy.

7.6	Specific Fuel Consumption, Fuel Based

(Equation #5)

SFCfuel	=	Qf x LHV

HPfuel

SFCfuel	=	Fuel Based Specific Fuel Consumption,	(BTU/BHP-HR)

Qf	=	Fuel Flow, (MCF/HR), Equation #1

LHV	=	Lower Heating Value, (BTU/cubic feet) = HV x 0.902

HHV	=	Fuel High Heating Value, (BTU/cubic feet), 	chromatograph

Hpfuel	=	Fuel Horsepower, (HP), Equation #4

7.7	Total Compressor Clearance

(Equation #6)

Ctotal	=	(Cfixed - CPopen x CPvol] x 100

Ctotal	=	Calculated Compressor Clearance, Total, (cubic feet)

Cfixed	=	Compressor Clearance, Fixed, (cubic feet)

CPopen	=	Clearance Pocket, Open (integer)

CPvol	=	Clearance Pockets, Volume, (cubic feet)

7 .8	Percent Rod Load, Tension

(Equation #7a)

RLten	=	[ (Ap - Ar) x (Pd + Patm) - Ap x (Ps + Patm)]	x 100

Allowable Rod Load in Tension

RLten	=	Percent	of Allowable Rod Load in Tension

Ap	=	Area of Piston, (square inches)

Ar	=	Area of Rod, (square inches)

Pd	=	Discharge Pressure, (PSIG)

Ps	=	Suction Pressure, (PSIG)

Patm	=	Atmospheric Pressure at Site, (PSIA)

7.9	Percent Rod Load, Compression

(Equation #7b)

RLcom	=	[ Ap x (Pd + Patm) – (Ap - Ar) x (Ps+Patm)]	x 100

Allowable Rod Load in Compression

RLcom	=	Percent	of Allowable Rod Load in Compression

Ap	=	Area of Piston, (square inches)

Ar	=	Area of Rod, (square inches)

Pd	=	Discharge Pressure, (PSIG)

Ps	=	Suction Pressure, (PSIG)

Patm	=	Atmospheric Pressure at Site, (PSIA)

7.10	Isentropic Discharge Temperature

(Equation #8)

(k-1)

Tdi	=	 (Ts+460) x	Pd+Patm	k	-  459.67

Ps+Patm

Tdi	=	Isentropic Discharge Temperature (°F)

Ts	=	Suction Temperature (°F)

Pd	=	Discharge Pressure (PSIG)

Ps	=	Suction Pressure (PSIG)

Patm	=	Atmospheric Pressure at Site (PSIA)

k	=	Isentropic Exponent

7.11	Compressibility

(Equation #9)

EA	=	Specific Gravity, (dimensionless)

EB	=	CO2, (mol weight)

EC	=	N2, (mol weight)

ED	=	EA - (13.84 x EB) + (5.42 x EC)

EE	=	Pressure at Point of Interest, eg. Ps, Pd, Pb (PSIG)

EF	=	    (ED - 0.6)       x   EE

22.26 - ED

EG	=	EE + EF

EH	=	Temperature at Point of interest, eg. Ts, Tdi, Tb (ºF)

El	=	EH + 460

EJ	=	EA - (0.472 x EB) – (0.793 x EC)

EK	=	 (0.6 - EJ)	x EI

0.468+EJ

EL	=	EH + EK

__1___

EM	=	(EL+460)

EN	=	__1___

(EL+60)

EO	=	 -0.048745388 + 65.370503 x EM – 18175.784

x EM²  – 0.031963078 x EN + 0.4690263 x EN2

EP	=	0.0000018631585 - 0.0079712762 x EM + 4.4346248 x EM²

+ 0.00026428048 x EN + 0.0016438531 x EN²

EQ	=	3. 9846513 x 10-9 + 4.3368839 x 10-6 x EM + 8.456803 x 10-4

x EM² + 1.5071412 x 10-7 x EN - 8.739461 x 10-7 x EN2

ER	=	-1.90975 x 10-14  x  EN

ES	=	EO + (EG x EP) + (EG2 x EQ) + (EG4 x ER) x EG x 2EN + 1

ET	=		1

ES²

7.12	Suction Volumetric Efficiency, Calculated

(Equation #10)

1

EVSC	=	1 – 0.01x	Pd +Patm	- C x	Pd + Patm	k x	Z s	-  1

Ps + Patm	Ps + Patm     	Zdi

EVDC	=	Discharge Volumetric Efficiency, Calculated

EVSC	=	Suction Volumetric Efficiency, Calculated

Pd	=	Discharge Pressure, (PSIG)

Ps	=	Suction Pressure, (PSIG)

C	=	Compressor Clearance, Total, (inches square), Equation #6

k	=	Isentropic Exponent, (dimensionless)

Zs	=	Suction Compressibility,(dimensionless), Equation #9

Zdi	=	Discharge Compressibility, (at Pd) dimensionless), Equation #9

Patm	=	Atmospheric Pressure (PSIA)

7.13	Discharge Volumetric Efficiency, Calculated

(Equation #11)

EVDC	=		EVSC

1

Pd+Patm	k	  Zs

Ps+Patm 	      x    Zdi

EVDC	=	Discharge Volumetric Efficiency, Calculated

EVSC	=	Suction Volumetric Efficiency, Calculated

Pd	=	Discharge Pressure, (PSIG)

Ps	=	Suction Pressure, (PSIG)

C	=	Compressor Clearance, Total, (inches square), Equation #6

k	=	Isentropic Exponent, (dimensionless)

Zs	=	Suction Compressibility, (dimensionless), Equation #9

Zdi	=	Discharge Compressibility, (at Pd), (dimensionless), Equation #9

Patm	=	Atmospheric Pressure (PSIA)

7.14	Calculated Throughput

(Equation #12)

Qc	=	Da x N x EVSCx	Zb 	(Ps+Patm)	x	(Tb+460)	x k2

Zs     	Pb	(Ts+460)

Qc	=	Calculated Throughput (MMSCFD)

Da	=	Total Unit Swept Volume, (cubic feet per revolution)

N	=	Unit Speed, (RPM)

EVSC	=	Compressor Volumetric Efficiency, calculated

Zb	=	Compressibility at Base Conditions, Equation #9

ZS	=	Compressibility at Suction Conditions, Equation #9

Ps	=	Suction Pressure, (PSIG)

Patm	=	Atmospheric Pressure at Site (PSIA)

Tb	=	Base Temperature, (OF)

Ts	=	Suction Temperature

k2	=	Constant = 0.00144

Pb	=	Base Pressure (PSIA)

7.15	Suction Valve Loss

(Equation #13a)

HP/MMCFs	=	Csvl x SG x N2 x [1388 EVSC - 886 x EVSC2  – 33 x EVSC3 ] x

Pb

14.4

Tb x Zb

HP/MMSCFs	=	Suction Valve Loss, (HP/MMSCF)

Csvl	=	Suction Valve Loss Constant, (dimensionless)

SG	=	Specific Gravity, (dimensionless)

N	=	Speed, (RPM)

EVSC	=	Suction Volumetric Efficiency, Calculated Equation #10

Pb	=	Pressure at Base Condition, (PSIG)

Tb	=	Temperature at Base Condition, (°F)

Zb	=	Compressibility at Base Condition, (dimensionless)

7.16	Discharge Valve Loss

(Equation #13b)

HP/MMCFs	=	Csvl x SG x N2 x [1388 x EVDC - 886 x EVDC2  – 33 x EVDC3 ] x

Pb

14.4

Tb x Zb

HP/MMSCFs	=	Suction Valve Loss, (HP/MMSCF)

Csvl	=	Suction Valve Loss Constant, (dimensionless)

SG	=	Specific Gravity, (dimensionless)

N	=	Speed, (RPM)

EVDC	=	Discharge Volumetric Efficiency, Calculated, Equation *11

Pb	=	Pressure at Base Condition, (PSIG)

Tb	=	Temperature at Base Condition, (°F)

Zb	=	Compressibility at Base Condition, (dimensionless)

7.17	Isentropic Horsepower/Million

(Equation #14)

(k-1)

IHP	=	44.64 x	  k		x	(Pd+Patm)	k	-	x	(Zs + Zdi)	x

k-1	(Ps+Patm)	2 · Zb

(Ts+459.67)

(Tb+459.67)

IHP	=	Isentropic Horsepower/million, (IHP/MMSCF)

k	=	Isentropic Exponent

Pd	=	Discharge Pressure, (PSIG)

Ps	=	Suction Pressure, (PSIG)

Patm	=	Atmospheric Pressure at Site

Zs 	=	Compressibility at Suction Condition

Zdi	=	Compressibility at Discharge Condition

Zb	=	Compressibility at Base Condition

Ts	=	Suction Temperature, (ºF)

Tb	=	Temperature at Base Condition, (ºF)

7.18	Horsepower/Million

(Equation #15)

HP/MMSCF	=	IHP + HP/MMSCFs + HP/MMSCFd

HP/MMSCF	=	Horsepower/Million Standard Cubic Feet, (HP/MMSCF)

IHP        	=	Isentropic Horsepower/Million, (HP/MMSCF), Equation #15

HP/MMSCFs	=	Suction Horsepower/Million, (HP/MMSCF), Equation #13a

HP/MMSCFd	=	Discharge Horsepower/Million, (HP/MMSCF), Equation #13b

7.19	Compressor Horsepower

(Equation #16)

HPcomp	= 	HP/MMSCF x Qc

HPcomp	=	Compressor Horsepower

HP/MMSCF	=	Horsepower/Million, (HP/MMSCF), Equation #15

Qc	=	Compressor Throughput, (MMSCF), Equation #12

7.20	Total Compressor Brake Horsepower

(Equation #17)

BHPcomp	=	HPcomp	+ HPpara

EFFmech

BHPcomp	=	Compressor Brake Horsepower, (BHP)

HPcomp	=	Compressor Horsepower, (HP), Equation f16

EFFmech	=	Mechanical Efficiency, (dimensionless)

HPpara	=	Parasitic Horsepower, (HP)

7.21	Compressor Specific Fuel Consumption

(Equation #18)

SFCcomp     	=	Qf x LHV

BHPcomp

SFCcomp	=	Compressor Specific Fuel Consumption, (BTU/HP-HR)

Qf	=	Fuel Flow, (MSCF/HR), Equation #1

LHV	=	Lower Heating Value of Fuel, (BTU/Cubic Foot) = HHV - 0.902

HHV	=	Measured High Heating Value of Fuel, (BTU/Cubic Foot), Chromatograph

BHPcomp	=	Compressor Brake Horsepower, (HP), Equation #17

7.22	Compressor Cylinder Efficiency

(Equation #19)

(k-1)

(Tg+460) x	Pd+Pa+Patm	k	-  (Tg+460)

EFFcy ln             =	 		Ps+Patm____________________	x 100

(Tdln - Tg)

EFFcy ln	=	Compressor Cylinder n, Efficiency, (%)

Tg	=	Flowing Gas Temperature, (ºF)

Pd	=	Discharge Pressure, (PSIG)

Ps	=	Suction Pressure, (PSIG)

Patm	=	Atmospheric Pressure at Site

Tdln	=	Isentropic Discharge Temperature of Cylinder, (ºF)

n	=	Cylinder Number

k	=	Isentropic Exponent

7.23	Compression Adiabatic Efficiency

(Equation #20)

EFFcomp     	=	(Effcyl1+EFFcyl2+...+EFFcy ln)

N

EFFcomp	=	Compressor Adiabatic Efficiency, (%)

EFFcyl1	=	Compressor Efficiency, Cylinder #1, (%), Equation #19

EFFcyl2	=	Compressor Efficiency, Cylinder #2, (%), Equation #19

EFFcy ln 	=	Compressor Efficiency, Cylinder #n, (%), Equation #19

N	=	Total Number of Cylinders

7.24	Engine Compressor Efficiency

(Equation #21)

EFFEC	=	HPfuel

BHPcomp

EFFEC	=	Engine Compressor Efficiency

HPfuel	=	Fuel Horsepower, (HP), Equation #8

BHPcomp	=	Compressor Brake Horsepower, (HP), Equation #17

7.25	Compressor Throughout Brake Horsepower

(Equation #22)

k-1

BHPthput	=	193.94 x	(Pd+Patm)	k	- 1	x	(Zs+Zd) x Zd  x

(Ps+Patm)	2

(Tg+459.67) x		1		x   Qc  x  100

(Tb+459.67)	EFFcomp

BHPthput	=	Compressor Throughout Brake Horsepower, (HP)

Pd	=	Discharge Pressure, (PSIG)

Ps	=	Suction Pressure, (PSIG)

Patm	=	Atmospheric Pressure at Site, (PSIA)

Zs	=	Compressibility at Suction Condition, (dimensionless)

k	=	Isentropic Exponent, (Dimensionless)

Tg	=	Flowing Gas Temperature, (ºF)

Tb	=	Base Temperature, (ºF)

EFFcomp	=	Compressor Adiabatic Eficiency, (%), Equation #20

Qc	=	Compressor Thoughput, (MMSCF), Equation #12

7.26	Throughput Efficiency

(Equation #23)

EFFthput	=	BHPthput   x 100

BHPcomp

EFFthput	=	Throughput Efficiency,

BHPthput	=	Compressor Throughput Brake Horsepower, (HP), Equation #22

BHPcomp	=	Compressor Brake Horsepower, (HP), Equation	#17

7.27	Station Throughput

(Equation #24)

Qs	=	Qc1 + Qc2 + ... +Qcn

Qs	=	Station Throughput, (MMSCF)

Qc1	=	Throughput, Compressor #1

Qc2	=	Throughput, Compressor #2

Qcn	=	Throughput, Compressor #n

8.0	COMMUNICATIONS

The Station Control System shall be required to communicate to Comapny gas control using the MODBUS protocol. If a distributed system is proposed, the data highway may be a proprietary bus but should have the speed to update the database in the main PLC/DCS within five seconds for a four unit station.

9.0	MAN/MACHINE INTERFACE

The software for the man/machine interface (MMI) shall be "Wonderware". The MMI shall provide the graphic displays, alarm annunciation, trending, report generation, and allow the operator to enter commands to the system.

The MMI package shall comply with Company's following requirements.

a.	The MMI shall be configured to control the data flow and display information in a logical, meaningful format. It is much more desirable to have a few well crafted screens than to display a massive amount of data on many screens. The screens should be developed on paper and evaluated in conjunction with each other before screen building begins.

b.	Company will supply typical screens that may be used as a guide as to the type of displays to be created and the type of information to be displayed. Company expects to work with Contractor in configuring the screens to be included in the final package.

c.	Some alarms and shutdowns are imported from the PLC/DCS while other alarms and shutdowns are generated within the MMI from trip settings on the analog values being read into the database or being calculated from the algorithms. Each alarm shall have an alarm priority level which is assigned by the operator at his option. A minimum of two levels shall be provided.

d.	The system shall display alarms and shutdowns, with time and date stamps, in a manner similar to a CRT based annunciator with high priority alarms being in red and going to the top of the list. Lower priority alarms go to the top of the list just under the critical alarms. Both types should blink until acknowledged. As new alarms come in old alarms are pushed down in the buffer until they drop out.

e.	All designated analog values should be trended. it should be possible to specify the sample rate, scale, and number of data points (or days, weeks, etc.) to be stored in the rolling buffer. It should be possible to select and display multiple trends, define and expand portions of the stored trend data, or print stored data.

f.	Several reports shall be developed to be available for printing. These would include a daily, monthly, and year to date reports. These reports are generated automatically and printed to the hard disk. The operator should have the option of retrieving the report desired and printing to the screen, floppy disk, or printer. Only the daily report should be printed on the printer automatically at the end of the pipeline day. All other reports are printed on demand. It is also desirable to print a performance report in which the user can assign the variables to be printed and the time frame.

g.	Screens for menus, station summary, unit summaries, unit displays (1 set per compressor), PID control shall show the various values on a graphic background. Commands to the PLC/DCS shall also be entered through these screens.

Screens shall also be provided for entry of data which is specific to the equipment in the station, such as engine rated speed, maximum torque, allowable rod loads, alarm and shutdown points, etc. This screen shall prompt the operator to aid with the entry of data. Default values shall be established if no entry is made, and the system should alarm that a default value is being used, with indication on the screen which value is defaulted.

h.	Several information-only type formulas such as station horsepower and efficiency shall be solved on a periodic basis and their values trended. Other data like run time and fuel consumption shall be accumulated and the current value displayed and reported.

10.0	ALARMS AND SHUTDOWNS

Alarms and shutdowns for the station control system and for the unit control panels are defined in the Project Specifications.

The Unit Panels shall have an interface which displays at least four alarms at one time with the capability to scan all alarms.

There are three basic shutdown strings which if interrupted will initiate:

a.	Unit Shutdown - where one individual compressor unit is shut down.

b.	Station Shutdown - where all compressor units are shut down but the station valves are not closed and the station is not depressured.

c.	Emergency Blowdown - where all compressor units are shut down, the station block valves are tripped closed, and the station is depressured.

Unit shutdown is performed by the Unit Control Panel when a shutdown device on the unit is tripped. A portion of these shutdowns shall be by-passed while the engine is being started and are activated when the engine reaches minimum speed.

All alarms and shutdowns shall remain active even if the unit is in the manual operating mode, except that the remote unit shutdown signal from the Station Control System shall be deactivated. The unit may not be switched to automatic mode unless these shutdowns are cleared. The Station Shutdown and Emergency Blowdown shall always remain active through a direct connection to the Unit Panels.

11.0	DOCUMENTATION

Contractor shall provide the following as part of the final documentation package:

a.	The Contractor shall provide Company with 2 copies of the development package used to create the program and/or configure the PLC/DCS and the MMI. This development package should run on a laptop PC and have the capabilities of both on-line and off-line programming, with the abilities to display annotated notes and comments. It should be capable of compiling register tables, generating cross references and sending the results to a printer. Include the reference texts and manuals for this package and 3 ½" diskettes.

b.	The Contractor shall provide 3 copies of a diagnostic type program which would run on a laptop PC and allow an operator to monitor the execution of the program on line for trouble shooting. Ideally, it should also be capable of displaying the annotated notes and comments. Include the reference texts and manuals for this package and 3 ½” diskettes.

c.	The Contractor shall provide with each system an annotated source code listing with embedded comments where necessary to explain the function being executed.

- The Contractor shall provide a written 2-3 page description of how the PLC/DCS is mapped, what functions are performed, where and how the program functions are executed (what is done first, next, etc.). Contractor shall provide a copy of a database (Access file) or spreadsheet (Excel) which is capable of being sorted and contains all variables used in the program identified by tag, mnemonic, long description of the function, register number and the program line where it is used. The MMI should have a similar database created unless it can be combined with the PLC/DCS database.

e.	Contractor shall create and provide start-up and operation manuals. These manuals should cover such items as cold start-up, hot start, transfer to manual or automatic, interpreting graphic displays, configuring trends, entering commands, clearing alarms, and shutdowns, troubleshooting, and other functional items.

f.	Contractor shall provide operation and repair manuals on each piece of hardware provided and including spare parts list. This would include, but not be limited to, the main processor, power supplies, I/O cards, communication cards, co-processors, modems, and any end devices provided.

g.	Contractor shall provide the following drawings for approval which show the location of the various I/O modules, their slot assignments, and other information pertinent to the installation, hook up, and operation of the panels:

- Front Layout

- Wiring Schematics

- Logic Diagrams

- Nameplate Details

Final drawings shall be provided on 3 ½" diskettes.

h.	Contractor shall provide an original copy of the software.

i.	Contractor shall provide complete parts list showing those recommended for one year's operation.

j.	Final certified data and manuals shall be bound in hard-back three-post binders. Sufficient binders shall be provided in each set so that the individual thickness is less than one and one-half inch. Binders are to be numbered 1 of 3, 2 of 3, and 3,of 3 etc.

k.	All drawings and documents shall be clearly marked as follows:

Requisition No.

Purchase Order No.

Station Control System and Unit Control Panel

l.	All drawings and documents shall be date stamped and marked "For Approval", "Certified", or "As-Built".

12.0	TESTING

The Station Control System and Unit Panels shall be tested as a complete package in Vendor's shop with all Contractor-provided components connected. Each test will be witnessed and approved by Company before shipment. Each system shall be functionally tested using multiple line analog simulators and switch banks. These tests should include I/O scaling, alarms and shutdowns, annunciation, displays, trends, calculations, interrupts, and restart on power failure for both the main processor, unit panels, and the MMI. A software simulator or forced input may be used to establish a fixed input to verify that a calculation produces a known output.

Contractor shall provide Company a written test procedure to be used in testing these systems at least two weeks before the final witness test. These test procedures shall be approved by Company before being used.

13.0	COMMISSIONING

Contractor shall provide active on-site and home-office support during the commissioning of each system. Contractor shall assign a person knowledgeable of this specific project application to assist in commissioning each system. This person should have the tools and the knowledge to modify the program of the PLC/DCS and the MMI as required to achieve a successful start-up.

14.0	FINAL ACCEPTANCE

Final acceptance of the control system will be after the system has been operating as specified for one week without modification or service. A complete functional test will be performed to prove that the system is operating as specified. Contractor shall be present during the complete functional test.

15.0	WARRANTY

Contractor shall warrant the equipment supplied to be free of defects for a period of 12 months after final acceptance by Company.

16.0	CONTROLS INFORMATION

Contractor will be required to furnish the required information once the Project is awarded:

a.	A written description with drawings, sketches, and literature that describes the equipment, software, configuration, orientation, overall dimensions, and panel fronts of the items being proposed.

b.	A detailed schedule showing preparation of drawings, approval times allowed, software mapping and approval time, hardware purchase and delivery to shop, fabrication testing, and shipment.

c.	A detailed list of each drawing, each piece of software, or any other documentation required to fill this order. Provide dates of submittal for approval.

d.	Allotted times for service personnel required on site for start-up and commissioning.

e.	Spare parts list.