EXHIBIT A  BASIS CONDITIONS	78 1

EXHIBIT A-1 BASIS FUEL	79 2

EXHIBIT A-2 NOT USED	80 3

EXHIBIT A-3 - NOT USED	81 4

EXHIBIT B  SCOPE OF WORK/SPECIFICATION	82 5

EXHIBIT B-1  SPECIFICATION	84 7

EXHIBIT B-2  NOT USED	85 8

EXHIBIT B-3  NOT USED	86 9

EXHIBIT B-4  APPROVED VENDORS	87 10

EXHIBIT B-5  DOCUMENT REVIEW STATUS CRITERIA	94 17

EXHIBIT C-1  SELLER PARENT GUARANTEE	96 19

EXHIBIT C-2  NOT USED	98 21

EXHIBIT E NOT USED	101 24

EXHIBIT F  PERFORMANCE TEST GUIDELINES	102 25

EXHIBIT F-1  SOUND LEVEL TEST GUIDELINES	106 29

EXHIBIT F-2  EMISSIONS TEST GUIDELINES	108 31

EXHIBIT G-1  PERFORMANCE TEST CERTIFICATE	112 35

EXHIBIT G-2  PERFORMANCE TEST COMPLETION CERTIFICATE	113 36

EXHIBIT H-1  TECHNICAL DIRECTION OF INSTALLATION	115 38

EXHIBIT H-2  TRAINING	120 43

EXHIBIT I  CANCELLATION CHARGE	121 44

EXHIBIT J  QUALITY	122 45

EXHIBIT K  PROJECT PLANNING	127 50

EXHIBIT L EQUIPMENT REQUIRING INSURABILITY CERTIFICATE	129 52

EXHIBIT M-1  NOT USED	130 53

EXHIBIT M-2 NOT USED	131 54

EXHIBIT N-1  PURCHASE AMOUNT RECONCILIATION 132 NOT USED	55

EXHIBIT N-2  OPTIONS	133 56

EXHIBIT O  HAZARDOUS MATERIAL NOTIFICATION	135 58

EXHIBIT P  UNIT SERIAL NUMBER	137 60

EXHIBIT Q SAMPLE PACKING LIST	138 61

EXHIBIT R  SCHEDULE OF WITNESS TEST POINTS	140 63

EXHIBIT S  FINAL WAIVER  OF LIENS FORM	141 64

EXHIBIT T  NOT USED	145 68

EXHIBIT U  FACILITY SPECIFIC PERFORMANCE LEVELS	146 69

Draft of 10/03/00 12/06/00

EXHIBIT A  BASIS CONDITIONS

Performance Guarantee basis conditions for the Units shall be as set forth below:

| Fuel | Natural Gas | Units of Measure |
| --- | --- | --- |
| Fuel Composition | See Exhibit A-1 |  |
| Load | Base Load |  |
| Ambient Temperature | 91 | F |
| Inlet Air Chiller Status | ON Chilled to 50 | F |
| Elevation | 0 | Ft. |
| Barometric pressure | 14.7 | psia Psia |
| Ambient Relative Humidity | 45 | % |
| Fuel LHV | 19,000 | BTU/lb |
| Fuel Temperature | 77 | F |
| Exhaust Loss (Static) If not in Scope of Work | 6 | In. H20 |
| Inlet Loss (Static) | 5 | In. H20 |
| Generator Power Factor (Lagging) | 0.90 |  |
| Generator Frequency | 60 | Hertz |
| Water Injection (to 25 ppmNOX) | 22,379 | lbs/hr+/-20% |

EXHIBIT A-1 BASIS FUEL

A.	The Guaranteed Levels and Specific Performance Guarantees are based upon the Unit’s operating on natural gas having the following composition:

| Composition by vol. |  |
| --- | --- |
|  | Percent |
| Methane | 84.50 |
| Ethane | 5.58 |
| Propane | 2.05 |
| Butane | 0.78 |
| Pentane | 0.18 |
| Hexane | 0.17 |
| Carbon dioxide | 0.67 |
| Nitrogen | 5.93 |
| Oxygen | 0.14 |
| Total | 100.00 |

Delivery Pressure 		=	655 psig (minimum)

Delivery Temperature		= 	77 F

The natural gas will contain not more than:

- 0.3 grains of hydrogen sulfide per 100 SCF.

- 20 grains of total sulfur (including the sulfur in any hydrogen sulfide and mercaptan) per 100 SCF.

- 7 pounds of water vapor per million SCF.

- The Facility Specific Performance Guarantees are based upon the Unit’s operating on liquid fuel of the type and having the characteristics identified as follows:

fuel type:

composition:

[To be completed if applicable]

EXHIBIT A-2 NOT USED

EXHIBIT A-3 - NOT USED

EXHIBIT B  SCOPE OF WORK/SPECIFICATION

1.	SCOPE OF SUPPLY

For a detailed description of the basic and optional scope of supply please refer to the accompanying Product Specification manual.

A.	BASIC SCOPE OF SUPPLY

The following equipment and services are included in the basic scope of supply:

1)	LM6000 gas turbine engine equipped with inlet bellmouth and screen.

2)	Gas fuel system, complete and self-contained on the unit, with connection on the baseplate for customer’s filtered, regulated fuel supply at 675 psig ± 20 psig.

3a)	Brush Generator, 13,800 Volt, 60 Hz, 3600 RPM, 71,000 KVA @ 0.85 pf.   Low maintenance  brushless excitation system suitable for Class 1, Group D, Div 2 areas.  Neutral and line cubicles with CTs, surge protectors and lightning arrestors

4)	I-beam baseplates for turbine, generator and unit mounted accessories.  The baseplate will be drilled and doweled for field re-alignment.

5)	Acoustic enclosure for gas turbine and generator.  Redundant ventilation systems, AC internal lighting and DC emergency lighting.

6)	Multi stage air inlet filtration system for both gas turbine and generator, including weather hoods, inlet screen, pre-filter, final barrier filter, intake silencer, and standard ducting to plenum chamber.  Filterhouse ladders and platforms are included.  The inlet silencer shall be designed for noise attenuation to 85 dBA at 3 feet.

7)	Electro-hydraulic start system.

8)	Separate lube oil systems for gas turbine and generator, including duplex filters, duplex fin-fan coolers, stainless steel piping, and stainless steel reservoirs.

9)	Axial-exhaust system with discharge flange for customer connection.

10)	Unit control panel for indoor mounting in a controlled environment, including microprocessor fuel management and sequencing system, generator metering, Bentley Nevada vibration monitoring, CRT annunciation of alarms and shutdowns, and Ethernet connection for data output to customer’s control systems.  Beckwith integrated generator protection system.

11)	I/O cubicle mounted on gas turbine enclosure.

12)	24V DC control system battery with dual battery chargers.

13)	Fire and gas detection and extinguishing system, serving both turbine and generator compartments, complete with 24V DC battery and charger.

14)	“On-line” water wash system and “soak wash” system.

15)	Generator factory testing to IEEE or IEC standards.  Gas turbine performance test by SSEP at SSEP factory (Houston).

16)	Six sets of drawing and data packages, O & M manuals.  Six sets of drawing and data packages and O&M/Installation Manuals.

17)	Training course for up to 10 customer personnel.

18)	Inlet chiller coil

19)	Enchanced Sprint power augmentation system including main GT skid piping/tubing, injection pump and metering system.

20)	Winterization package to - 10oF

21)	Nox water injection skid including main GT skid piping/tubing, injection pump and metering system.

22)	Special tools for installation and removal of the gas turbine.

23)	Technical Site Supervision - 240 man-hours per Unit

24)	Packing and crating for domestic shipment

25)	Special lifting devices for Unit installation (to be returned to Seller).

26)	Option H – Dual fuel system

EXHIBIT B-1  SPECIFICATION

EXHIBIT B-2  NOT USED

EXHIBIT B-3  NOT USED

EXHIBIT B-4  APPROVED VENDORS

AIR FILTERS

Altair

Donaldson

Stewart & Stevenson

Universal

BALL VALVES

Apollo

Kitz

Orbit

Rockwell

Watts

WKM

BATTERY CHARGERS

Lamarche

Sens

BEACON LIGHTS

Whelen

Tomar

CABLE

Alpha

Belden

Consolidated

Okonite

Pirrelli

Tensolite

Thermo-Electric

CHECK VALVES

Check-All

Circle Seal

Durabala

Emco

Gulf Valve

Hoke

Kepner

Kitz

Ladish

Mueller

OIC

TRW Mission

Valtek

Vogt

CENTRIFUGE

Centrico

Alpha Laval

CENTRIFUGAL CHILLERS

Trane

COUPLINGS

Falk

Kopflex

Lovejoy/Centiflex

Lucas Aerospace

Magnalloy

Thomas

Waldron (Garrett)

Zurn

DAMPERS

American Warming

DIFFERENTIAL PRESSURE SWITCHES

Dwyer

Neo-Dyn

Orange Research

DIFFUSER

American Warming

ELECTRIC GENERATORS

Brush Electric

GEC Alsthom

General Electric

Kato

EMERGENCY LIGHTS

Crouse Hinds

EXHAUST STACK

Braden

EXPANSION JOINTS

Expansion-Joint Systems

JM Clipper

Pathway

Power Dynamics

RM Engineered Projects

Hyspan

FANS

Aerovent

FIRE SYSTEMS/COMPONENTS

Alestec

Detronics

Kidde

Rexnord

Wilson

FLAME DETECTORS (UV)

G.E.

Honeywell

FLOW METERS

Cal-O-Flow

EG&G Flow Technology

Foxboro

Yokogawa

FLOW SWITCHES

Delta Controls

Fluid Components

FUEL CONTROL VALVES

EGT

Whittaker

Woodward

RECIPROCATING GAS COMPRESSORS

Ariel

Dresser-Rand

GAS FUEL FILTERS

Texas Systems & Controls

GATE VALVES

Bonney Forge

Kitz

Stockham

Vogt

GEARBOXES

Lufkin Industries

Maag

Koe Milwaukee

GLOBE VALVES

Stockham

HEAT EXCHANGERS

Air Coolers

American Technology

Air-X-Changer

GEA Rainey

Hayden

Oil Coolers

Basco

HEAT TRACE

Thermon

Wyegland

HEATERS

Fuel Oil

Texas Systems & Controls

Compartment

Ruffneck

Lube Oil Tank

Chromalox

CO2 Enclosure

Caloritech

INLET SILENCERS

Donaldson

Farr

IAC

Spitzer & Assoc.

INSTRUMENT VALVES

Dragon

INSULATORS

Victor

JUNCTION BOXES

Hoffman

Stewart & Stevenson

Tanco

LEVEL SWITCHES

IMO

Jobell

Link

Murphy

LIGHTNING ARRESTORS

GE

LUBE OIL FILTERS

Donaldson

Pall

Parker

MIST COLLECTORS/AIR OIL SEPARATORS

Aercology

Altair

Dollinger

Monsanto

Stewart & Stevenson

MOTOR CONTROL CENTERS

Allen Bradly

General Electric

MOTORS

GE

Marathon

ORIFICE

Meriam

LPC

GE

Allen Bradley

Xycom

PRESSURE CONTROL VALVES

Fisher

PRESSURE GAUGES

Ashcroft

Dwyer

Orange Research

PRESSURE SWITCHES

Dwyer

Neo-Dyn

United Electric

PRESSURE TRANSMITTERS

Honeywell

Rosemount

Schlumberger

Statham

PUMPS

Barnes

EGT

Gould

IMO

Rexroth

Roper

Roto-Jet

Sundstrand

Tuthill

Voith-Eckerle

Whitton

Woodward

REGULATORS

Fisher

RELIEF VALVES

Anerson Greenwood

Circle Seal

Crosby

Fisher

Hycon

Kepner

Parker

RTD’S

Brush

Rosemount

Weed Instrument

SEQUENCER

Woodward

SIGHT GLASS/FLOW INDICATORS

Cyclops

Jacoby-Tarbox

OPW

SNUBBERS

Ashcroft

SOLENOID VALVES

Asco

Atkomatic

Denison

Versa (Stig)

SPEED SENSORS

GE

STARTER

Rexroth

Starter Clutch

Hillard

STRAINERS

Hayward

Marvel

Mueller

SURGE CAPACITORS

GE

TANK THERMOMETERS

Ashcroft

TANKS

Brunner Mfg.

Gulf Coast Alloy Welding

Jerryco

Stewart & Stevenson

TEMPERATURE INDICATORS

Ashcroft

TEMPERATURE SENSORS

Rosemount

Weed

Woodward

TEMPERATURE SWITCHES

Neo-Dyn

United Electric

TERMINAL BOARDS

Buchanan

Entrelec

Phoenix

THERMOSTATIC CONTROL VALVES

Amot

THERMOSTATIC SWITCHES

Amot

Neo-Dyn

United Electric

VANEAXIAL FANS

Aerovent

Hartzell

VIBRATION MONITORING

Bentley Nevada Corp.

VIBRATION SYSTEMS

Bentley Nevada Corp.

EXHIBIT B-5  DOCUMENT REVIEW STATUS CRITERIA

DRAWING PROCESSING

A copy of each drawing reviewed will be returned to Seller as stipulated herein.  Copies of drawings returned to Seller will be in the form of a print with Purchaser’s marking.

A.	DEFINITION OF SELLER DOCUMENT REVIEW STATUS

The guidelines listed below are followed in assigning the document status number to Seller prints.  These status numbers serve as hold points for starting or continuing manufacture of the covered commodity.  The document and its transmittal letter indicate the reason for the status.

Status 1: Work may proceed.

The document conforms to Agreement requirements.  The document requires no changes or additions.  Matters remaining to be resolved do not require document change and will be handled by correspondence.  Where it is known that the design information on a supplier document is not complete and resubmittals will be made, such as “hold” areas, the document is assigned another status number.

Status 2: Revise and resubmit.  Work may proceed subject to resolution of indicated comments.

The document is in basic conformance with Agreement requirements.  Minor deviations from Agreement requirements (not including minor changes for Purchaser’s convenience) have been noted or other minor technical or physical changes in the equipment are required.  Such changes may include those affecting dimensions, material, colors, etc.  Administrative type changes such as inclusion or equipment or tag numbers and shipping notes may be combined with technical changes in this status.  Seller shall resolve comments and resubmit documents prior to shipment of commodity.

Status 3:  Not Used.

Status 4: Review not required.  Work may proceed.

Document is not subject to Purchaser review.  Typical uses for this status are in the review of items that are supplier standard products, small internal parts of major equipment, or Seller standardized data.

Permission to proceed does not constitute acceptance or approval of design details, calculation analysis, test methods, or materials developed or selected by the supplier from full compliance with contractual obligations.

FINAL DRAWINGS

Upon receipt from Purchaser of drawings marked Status 1 or Status 4, Seller drawing shall be considered acceptable and no further corrective action shall be required.  After completion of fabrication and release for shipment, all drawings shall be resubmitted showing the “as installed” configuration of the Equipment.

EXHIBIT C-1  SELLER PARENT GUARANTEE

GUARANTEE

THIS GUARANTEE, dated the ______ of ____________________, 200___, is from [Seller's Parent Company], a [           ] corporation ("XXX"), to [                ]. ("RECIPIENT").

WHEREAS, [Seller] is an affiliate of [Seller's Parent Company] ("XXXX"); and

WHEREAS, RECIPIENT and [Seller] entered into the attached Agreement dated [------] (the "Agreement"); and

WHEREAS, Seller desires to assign all or part of its rights and benefits and delegate its duties and obligations under the Agreement to [Assignee] (the “Assignee”); and

WHEREAS, [Seller's Parent Company] has agreed to guarantee the performance of Assignee under the Agreement in order to induce RECIPIENT to consent to Seller’s assignment of the Agreement;

NOW THEREFORE, [Seller's Parent Company] hereby irrevocably and unconditionally guarantees to RECIPIENT the performance by Assignee of all of Seller’s undertakings, covenants, indemnities and obligations under the Agreement to the extent and under the terms and conditions and subject to the limitations set forth in the Agreement.  [Seller's Parent Company] hereby consents that at any time and from time to time without notice to [Seller's Parent Company], the performance or observance by Assignee of any term or covenant of the Agreement may be waived, the time of performance thereof extended, any provisions thereof amended and the rights of RECIPIENT hereunder assigned, without affecting the liability of [Seller's Parent Company] hereunder.  [Seller's Parent Company] may assert any and all defenses and limitations of liability possessed by Assignee, but excluding any defenses based upon invalid execution of the Agreement.

This guarantee shall be governed by, and construed, interpreted and enforced in accordance with the substantive law of the State of Texas, excluding any conflict of laws or principles which would result in a choice of law for this Guarantee other than Texas law.  Further, the parties stipulate that this Guarantee is deemed to have been made and entered into by them in the State of Texas.  With respect to any suit, action or proceedings relating to this Guarantee (the "Proceedings"), each party irrevocably submits to the exclusive jurisdiction of the courts of the State of Texas and the United States District Court located in Harris County, Texas, and irrevocably waives any objection which it may have at any time to the laying of venue of any Proceeding brought in any such court, waives any claim that such Proceedings have been brought in an inconvenient forum and further waives the right to object, with respect to such proceedings, that any court does not have jurisdiction of such party.  Nothing in this Guarantee precludes either party from enforcing in any jurisdiction any judgement, order or award obtained in any such court.

[Seller’s Parent Company] waives any rights to subrogation/security and agrees to be bound by any findings of fact or final award or judgement made in an arbitration against Assignee under the Agreement.

This Guarantee and any liability or obligation created hereunder shall expire upon the expiration of all liability and obligations of [Assignee] under the Agreement.

IN WITNESS WHEREOF, [Seller's Parent Company] has caused this Guarantee to be executed as of the date first written above.

[SELLER'S PARENT COMPANY] By: Printed Name: Title:

EXHIBIT C-2  NOT USED

EXHIBIT D  SAMPLE LETTER OF CREDIT

Applicant:   [-------] (“Seller”)

Beneficiary: [-------] (“Beneficiary”)

Bank: [------- ] (“Bank”)

Expiry Date:

Amount:       US ($--------)

I.	Funds under this irrevocable standby Letter of Credit are available to Beneficiary against presentation to us of Beneficiary’s draft drawn at sight on _____________, marked thereon “Drawn under standby Letter of Credit number ________, and accompanied by the following documents:

1.	Original Beneficiary’s statement purportedly signed by an authorized officers of Beneficiary (as determined at Beneficiary’s sole and absolute judgement) stating:  “Seller is in default of its obligation to perform in accordance with Section(s) [-------] of Agreement No. [------------] (the “Agreement”), dated _________.  This statement is a demand for payment under irrevocable standby Letter of Credit number _______ notwithstanding any objection by Seller or any other person or entity whatsoever.”

2.	A copy of the written Notice to Seller sent pursuant to Article 25 of the Agreement (a copy of the conformation of receipt shall be attached thereto) , dated at least thirty (30) Days prior to presentation of any claim under this irrevocable standby Letter of Credit evidencing that Beneficiary gave the requisite written notification to Seller stating therein that Seller was in breach of a specified obligation under the Agreement and that it is [beneficiary] intent to drawdown [specify amount] in the event Seller fails to cure or commence to cure such default within thirty (30) Days from the date of this Notice.

II.	Special Conditions:

1.	Payment under this irrevocable standby Letter of Credit will be made to an account in Beneficiary’s name at such bank as Beneficiary shall stipulate.  The amount or amounts demanded shall not exceed, in the aggregate, the amount of this Letter of Credit.

2.	Any payment made hereunder shall be made free and clear of and without deduction for, or on account of, any present or future taxes, levies, imposts, duties, charges, fees, commissions, deductions or withholdings of any nature whatsoever and by whomever imposed.

3.	Any reference to Agreement/Bid item is for information purposes only and is not incorporated in nor made a part of this irrevocable standby Letter of Credit.

4.	Bank agrees and consents that this irrevocable standby Letter of Credit may be modified, adjusted, amended, extended, suspended or shortened pursuant to Article VI of the Agreement, and that this irrevocable standby Letter of Credit, subject to agreement of Beneficiary, Seller and Bank, may be modified to comply with any such changed requirements of the Agreement.

5.	Seller’s liability under this irrevocable standby Letter of Credit is limited to ([-------] United States Dollars [$-------]).  This irrevocable standby Letter of Credit shall expire at our counters [-------]     , 20[---].

6.	Demands may be made against this irrevocable standby Letter of Credit in one or more increments; however, the aggregate of such demands shall not exceed the amount set forth in Paragraph 5 of this irrevocable standby Letter of Credit.

We hereby engage with the Beneficiary that draft(s) accompanied by documents drawn in strict compliance with the terms and conditions of this irrevocable standby Letter of Credit shall be duly honored by us if presented to us at our office located at _______________________on or before the expiration date.

This irrevocable standby Letter of Credit is subject to the uniform customs and practice for documentary credits (1993 revision), International Chamber of Commerce, Publication No. 500.  This irrevocable standby Letter of Credit shall be governed by, and construed in accordance with the laws of the State of New York.

EXHIBIT E NOT USED

EXHIBIT F  PERFORMANCE TEST GUIDELINES

A.	TEST PHILOSOPHY

I.	General.

The performance guarantees for the Unit include the Specific Performance guarantees of the Specific Performance Levels and performance guarantees of the Guaranteed Levels.  The performance test procedure will include three (3) one (1) hour input/output test runs for each Unit utilizing a combination of installed station instrumentation and special test instruments to (i) observe and record of the parameters required to demonstrate or calculate performance and (ii) enable correction of the demonstrated or calculated performance to Basis Conditions (individually a “Test Run”).  All instruments used to measure parameters used to calculate the results of the Test shall meet the accuracy and calibration requirements of the Codes and Standards or as specified in this Exhibit F, if station instrumentation does not meet accuracy, Purchaser shall install temporary equipment to meet accuracy.

If the test run results and uncertainty bands calculated from the post-test uncertainty analysis demonstrate “complete overlap”, as described in PTC 19.1-1998 Section 8.5 and Figure 8.3, the Seller may choose two (2) of the three (3) Test Runs for the basis of test acceptance.  The results of the same two test runs shall be used to evaluate all of the performance guarantees.

The Performance Test will be performed by the Purchaser.  Seller will supply gas turbine correction curves and calculations, while Purchaser will prepare a detailed Test Procedure, based on PTC 1-1999, PTC 22-1997, PTC 4.4-1981, PTC 19.1-1998, PTC 46-1996 and appropriate related ASME Performance Test Codes and ASME Standards (the “Codes and Standards”), Purchaser will perform calculations to determine Unit performance relative to Guaranteed Levels and Specific Performance Levels and will prepare test result certificates in the form as set forth in Exhibits G-1 and G-2 for submittal to Seller’s Representative.

Performance Tests should be conducted as soon as possible (within 200 site fired hours) after first fire.

II.	Procedure

The gas turbine generator will be operated at Base Load as defined in the Agreement.  The Test Procedures will include a demonstration of power capability, heat rate, exhaust energy (when applicable) and exhaust temperature (when applicable).  The Unit’s auxiliary equipment power consumption data will be measured to enable determination of net Electrical Output of the Unit.

The Performance Test Procedures will establish the methodology, based on the Codes and Standards, for calculating the Unit performance and for correcting the Unit’s measured Electrical Output (gross), Heat Rate (gross), and Exhaust Gas Temperature and Exhaust Gas Energy, as applicable to plant cycle design, from existing Site conditions to Basis Conditions, and subsequently deducting Unit auxiliary loads for the purpose of comparing the Adjusted Electrical Output, Adjusted Heat Rate, Adjusted Exhaust Gas Temperature and Adjusted Exhaust Gas Energy values against Guaranteed Levels and Specific Performance Levels as applicable.  Unit specific correction curves needed to correct from Site conditions to Basis Conditions will be developed by Seller and included in the Performance Test Procedures.

A Facility specific Facility Agreement Performance Test Guideline will be prepared for each Site.  The specific guideline will include a means of verifying that the Unit is at base load during each performance test run by comparison of operating data with control variables.  It is the Seller’s responsibility to ensure that the Unit is operating on its control curve that defines Base Load at the time of the test.  A test run will not be valid if the Unit control mode changes during that run.  The GE cycle deck will be used to determine the performance corrections for determination of the Test Result, however, the performance guarantee margins and test uncertainty will be taken into account.   Since the Unit has multiple control modes it is necessary to make corrections of the Unit performance for inlet conditions to evaluate the corrected control mode.  The uncertainty analysis shall include control element uncertainty as noted in PTC 22-1997.  Seller will supply all necessary correction curves for the purpose of the calculating the Test Results.

B.	STANDARD FIELD PERFORMANCE TESTING PROCEDURE

I.	Scope

The Test Procedure will follow ASME PTC 22-1997 and ASME PTC 46-1996.  Whenever deviations from ASME PTC 22-1997 and/or ASME PTC 46-1996 are required the performance test procedure will clearly identify the deviations, the reasons for the deviations, and the alternative proposed method to be used during testing for agreement among the parties involved in the testing.  Any deviation from the ASME PTC codes is required to maintain the high accuracy criteria of the codes and of this Exhibit F.

II.	Machine Condition

In accordance with Section 12.4.1 of the Agreement, Seller’s representative shall certify that the Unit is ready to test.

The Unit shall be tested when in new and clean condition subject to Section 10.12.4 of the Agreement.  The Seller’s representative shall determine, in its sole and reasonable discretion, based on the terms of this Agreement and the Test Procedures, whether the subject Equipment is in new and clean condition and ready to be tested.  For testing conducted after new and clean period as defined in Section 10.12.4.2 of the Agreement, Seller’s degradation curves, as set forth in this Agreement, shall be utilized.

If the Seller’s representative, in its sole reasonable discretion, determines that the subject Equipment is not in new and clean condition prior to the conduct of the Performance Test, the Equipment shall be cleaned in accordance with Seller’s recommendations set forth in Exhibit A-2, Attachment 3 (Seller reference).

III.	PTC 22-1997 Modifications and Clarifications

A.	A valid Test Run will consist of a minimum of thirteen (13) sets of instrument reading taken at five (5) minute intervals over a sixty (60) minute time span after steady state conditions have been established as listed in PTC 22.

B.	Speed measurements are required and must be measured by an electronic tachometer or equal, and averaged for the Test Run.  Any corrections for frequency variation shall be applied to the calculation.

C.	Unit Electrical Output is to be measured by polyphase calibrated watthour meters (of revenue meter quality) at the generator terminals.  Revenue quality metering shall be provided by Purchaser.

D.	Gas Turbine exhaust temperature will be measured in control thermocouples mounted in the exhaust plenum (supplied by Purchaser).

E.	It is essential that the temperature indicating system be adjusted and calibrated in place with a known millivolt source prior to the test so that it reports reliable data.

F.	Barometric Pressure at the test site shall be measured with a mercury or aneroid barometer with an accuracy in accordance with PTC 22.  A minimum reading accuracy of 0.01 inches of Hg is required.

G.	Fuel Consumption: Gas fuel is to be measured with a flat plate orifice or venturi installed in accordance with ASME MFC-3M or a turbine meter installed according to ASME MFC-4M standards.  Calculation of gas flow will be done in accordance with either ASME MFC-3M or MFC-4M as appropriate.  The upstream pressure will be measured with a precision test gage, the pressure drop with a manometer, the gas temperature with a thermometer or thermocouple.  The above flow will be verified with the Unit mounted fuel flow meter.

H.	Four (4) gas samples shall be taken from the fuel system during the test for laboratory analysis of composition according to ASTM D1945.

I.	The higher and lower heating values will be determined according to ASTM D 3588.

J.	Ambient air condition will be measured with at least two (2) (preferably 4) RTD’s with an uncertainty meeting PTC 22.

K.	Turbine exhaust static pressure at or near the turbine exhaust flange or other convenient location must be measured using at least two (2) disc type static pressure probes.

L.	All instruments to be used in the performance test shall be calibrated immediately prior to the performance test and checked immediately after the performance test.  The Parties to the Test will witness the calibrations and inspections.

IV.	Evaluation

The Performance Test Procedure will include the tolerance due to measurement uncertainties associated with each particular test result in accordance with Section 10.12.10 (iii) of the Agreement.

The Parties will agree on a method of determining the sufficiency of the inlet chiller coils to provide the desired inlet air cooling.  The results of this determination will be included in the calculation of the Test results and in the Performance Test report.

AUXILIARY POWER LOAD

| GT Package Equipment | Quantity in Operation |
| --- | --- |
| Turbine Vent Fans | 1 |
| Generator Vent Fans | 1 |
| Hydraulic Start Pump | 0 |
| Gen. Aux. L.O. Pump | 0 |
| Gen. Jacking Oil Pump | 0 |
| Turbine L.O. Heater | 0 |
| Gen. L.O. Heater | 0 |
| Turbine Air/Oil Separator | 1 |
| Lighting and Low Voltage Distribution System | 1 |
| Sprint Water Pump | 1 |
| Water Inj. Pump-Gas Fuel | 1 |

EXHIBIT F-1  SOUND LEVEL TEST GUIDELINES

PERFORMANCE TEST GUIDELINES FOR NEAR SOURCE SOUND LEVELS

- Testing methodology shall be based on the latest version of ANSI/ASME PTC 36.  The final result shall be the arithmetic average of the sound power levels (“SPLs”) measured around the equipment after background and other corrections have been applied.  The equipment shall be in compliance if the final result does not exceed the noise limit(s) specified in Section 10.5 of the Agreement.

- Equipment shall be operated in a new and clean condition as intended by the designers when measurements are taken.  All access compartments, doors, panels and other temporary openings shall be fully closed; all silencing hardware shall be fully installed; all systems designed to be airtight shall be sealed.

- Corrections to the measured SPLs shall be made per ANSI/ASME PTC 36 procedures.  Background noise is defined as the noise measured with all Seller supplied equipment off and all other plant equipment on.

- Intermittent noises such as steam safety blow off valves and filter pulse noise are not included in the above guarantee.

- Measurements shall be taken 3.28 feet (1 meter) away from the outermost surfaces of equipment, including piping, conduit, framework, barriers, Equipment enclosures and personnel protection devices if provided.

- Measurements shall not be taken in any location where there is an airflow velocity greater than 4.9 feet per second (1.5 meters per second), including nearby air intakes or exhausts.

- Free field conditions must be prevalent at measurement locations.  Testing and corrections to a free field shall be per ANSI/ASME PTC 36.

- Testing shall be done according to a test plan agreed to by both the Purchaser and Seller.  Such a plan shall be submitted to both the Purchaser and Seller at least 30 Days prior to noise compliance testing.  The test results shall be submitted in the form of a test report that shall be made available to both the Purchaser and Seller.

Measurement responsibility shall be stated in the Agreement.  Seller reserves the right to audit or parallel these measurements.

PERFORMANCE TEST GUIDELINES FOR FAR FIELD SOUND LEVELS

- Testing methodology shall be based on the latest version of ANSI B133.8.  The final result shall be the arithmetic average of the SPL’s at the 8 measurement locations after background and other corrections have been applied.  The equipment shall be in compliance if the final result does not exceed the noise limit(s) specified above.

- Equipment shall be operated in a new and clean condition as intended by the designers when measurements are taken.  All access compartments, doors, panels and other temporary openings shall be fully closed; all silencing hardware shall be fully installed; all systems designed to be airtight shall be sealed.

- Corrections to the measured SPL shall be made per ANSI B133.8 procedures.  Background noise is defined as the noise measured with all Seller supplied equipment off and all other plant equipment on.

- Intermittent noises such as steam safety blow of valves and filter pulse noised are not included in the above guarantee.

- Measurements shall be taken 4.9 feet +/- 2.5 feet (1.5  meters +/- .75 meters) above the ground.  Such measurement locations shall be on a flat elevation no more than 16 feet (5 meters) above or below the plant base elevation.

- Measurements shall not be taken in any location where there is an airflow velocity greater than 5 feet per second (1.5 meters per second), including nearby air intakes or exhausts.

- Measurement locations shall be chosen such that free field conditions exist at those locations.  Measurement locations shall not be closer than 12 feet (3.5 meters) to any nearby reflecting surfaces.

- Testing shall be done according to a test plan agreed to by bother the Purchaser and Seller.  Such a plan shall be submitted to both the Purchaser and Seller at least 30 Days prior to noise compliance testing.  The test results shall be submitted in the form of a test report that shall be made available to both the Purchaser and Seller.

Measurement responsibility shall be Purchaser’s.  Seller reserves the right to audit or parallel these measurements.

EXHIBIT F-2  EMISSIONS TEST GUIDELINES

GE POWER SYSTEMS
U.S. Standard Field Testing Procedure for Emission Compliance

Test Philosophy

Testing to demonstrate emission guarantees and for adjustment of the NOx reduction system (if required) will be performed using procedures which are mutually agreed between Seller and the Purchaser.  Seller engineers and/or technical advisors may be present at the tests for procedural direction.  Test methods chosen are EPA methods which yield data on site immediately, wherever possible.

Emission Testing

A.	General

Emission testing identified herein shall be within Purchaser’s scope of supply using procedures which are mutually agreed.  Sampling for inlet pollutant concentrations may be required, at the sole discretion of GE, in order to demonstrate compliance with emission guarantees.  Seller’s guarantees apply to the net increase of these pollutant emissions.

B.	Nitrogen Oxides Emissions

Before the official compliance testing is begun, the NOx reduction system will be adjusted to verify compliance with  NOx emission limits.  The gas turbine control system contains a pre-programmed schedule for either water or steam injection, this schedule may be adjusted to achieve an appropriate emission level approximately 5% to 10% below emission limits, and minimize the supply requirements.  Once the proper injection schedule has been established, this schedule is maintained throughout the testing, and it is programmed into the control system.

The NOx emission testing and related oxygen testing will be in accordance with U.S. EPA Method 2 presented in the Code of Federal Regulations.  Title 40, Part 60 (40CFR60 Appendix A and 40CFR60 Subpart GG -- Standards of Performance for Stationary Gas Turbines), with the following modifications, limitations and additions:

a.	The NOx instrument will be limited to a chemiluminescent type which meets 40CFR60 Appendix A, Method 7E.

b.	The span of the NOx analyzer will be set for appropriate spread of the expected NOx readings, rather than the specified 300 ppm.

c.	Oxygen will be sampled simultaneously with all NOx readings since Subpart GG of 40CFR60 requires correction to 15% O2.  Method 3A from 40CFR60 Appendix A is used for the oxygen analysis.

d.	Section 60.33(c)  (i)of Subpart GG has been replaced by U.S. EPA Memorandum dated June 2, 1997 for GE gas turbines using either water or steam for NOx reduction.  The EPA memorandum approves the Seller injection control algorithm in lieu of the Subpart GG ISO correction equation.

e.	Section 60.335(c) (i) is not applicable to gas turbines with dry low NOx combustors.

C.	Carbon Monoxide Emissions (If Required)

Sampling is the same as for NOx normally with the same line feeding the different instruments.  Method 10 per 40CFR60 appendix A is used, but only the continuous sample method per Section 5.1 is acceptable to Seller.  A recorder is mandatory, not optional as per 5.3.9, with a span which gives an appropriate spread of the expected readings.

D.	Unburned Hydrocarbon Emissions (If Required)

Sampling and analysis must be on a wet basis to avoid condensing out the higher hydrocarbons.  Moisture determination by Method 4 (or Method 5) is necessary to convert results to dry basis.  Method 25A per 40CFR60 Appendix A is used for unburned hydrocarbons.  Results are presented as methane (CH4).  This method uses a flame ionization detector or analyzer.

E.	Volatile Organic Emissions (If Required)

When volatile organic emissions (non-methane, non-ethane hydrocarbons) are required, Method 18 per Section 7.2 is used.  This requires a gas chromatograph at the site.  Seller requires calibration of the measurement train at the sampling probe.

F.	Sulfur Emissions (If Required)

Sulfur emissions will be determined by use of fuel flow data and fuel analysis for sulfur content.

G.	Particulate Matter Emissions (If Required)

Particulate matter emissions are determined by sampling, analysis and calculation in accordance with U.S. EPA Methods 5 and 5B with traversing per Methods 1 and 2 all from 40CFR60 Appendix A.  The following modifications and limitations on choices within the methods apply:

a.	Sampling probe internal surfaces must be made of chemically inert and non-catalytic material such as quartz.

b.	The filter material shall be quartz.

c.	Nozzle, probe and filter must be heated to 248 to 273oF per Method 5, or at last 10oF higher than the dew point of sulfuric acid in the exhaust duct.  Use of Method 5B requires nozzle, probe and filter to be heated to 320 to 345oF.

d.	Probe wash shall be acetone per Method 5.

e.	Sampling technique shall provide a fairly large exhaust gas sample, with an objective of 100 SCF.

f.	Sulfates are excluded from the Seller guarantees for particulates.

H.	PM10 Emissions (If Required)

PM10 emissions are determined by sampling, analysis and calculation in accordance with U.S. EPA Methods 5 for front half filterable particulate matter and Method 202 for back half condensible particulate matter with traversing per Methods 1 and 2, all from 40CFR60, Appendix A except for Method 202.  Method 202 is from 40CFR51, Appendix M.  The following modifications and limitations within the methods apply:

a.	Sampling probe internal surfaces must be made of chemically inert and non-catalytic material such as quartz.

b.	The filter material shall be quartz.

c.	Nozzle, probe and filter must be heated to 248 to 273oF per Method 5, or at least 10oF higher than the dew point of sulfuric acid in the exhaust duct.

d.	Probe wash shall be acetone per Method 5.

e.	Sampling technique shall provide a fairly large exhaust gas sample, with an objective of 100 SCF.

f.	Impinger solution shall be extracted with ACS grade methylene chloride per Method 202.

I.	Opacity (If Required)

Opacity shall be measured in accordance with EPA Method 9 from 40CFR60, appendix A.

J.	Ammonia Slip (If Required)

Required EPA methods for measuring ammonia slip have not been published.  GE has established in the interim a preference for the determination of ammonia slip.  The ammonia slip emissions will be determined by on-site sampling and analysis plus calculations in accordance with the on-site industry procedure of Indophenol Absorptiometrics.  This procedures requires the use of reactant solutions and a photoelectric spectrophotometer at the plant site.

Sample collection procedures should include Item G(a)-(e) above (Particulate Matter Emissions - Front - Half Filterable Solids Only).

K.	Certification of Calibration Gases

All gases used in certification of instruments or performance of emissions guarantee demonstrations shall be analyzed and certified in a manner and by a laboratory mutually agreeable to GE and Purchaser.  Examples of acceptable certification are:

- U.S. EPA Standard Methods

- U.S. EPA Protocols

- U.S. National Bureau of Standards Certification Procedures

L.	Exhaust Gas Flow Determination (Not required for this Agreement)

Seller has established preferences for the determination of exhaust flow based on accuracy of the determination.  GE prefers the following:

The primary exhaust flow determination shall be by the F - factor method per 40CFR60, appendix A, Method 19 (as specified in Method 20 for gas turbine emissions).  The F - factor constants from Table 19-1 shall be applied in all cases where possible per Paragraph 3.1.

Where available, the compressor inlet air flow signal shall also be used to compute exhaust flow.  Exhaust flow on a dry basis is the turbine inlet air flow minus the water vapor plus the fuel flow minus the water formed from the combustion of hydrogen in the fuel.  Gas turbine inlet air is measured using the compressor inlet air scroll as a flow element.  The inlet scroll is calibrated during the factory tests of the gas turbine.

Flow measurements by Velocity Traverse, per 40CFR60, Appendix A, Methods 1 and 2, can result in errors of 25% or more in this application, and is not acceptable.

M.	Fuel Bound Nitrogen Determination

Prior to emission testing, analysis for fuel bound nitrogen must be determined in accordance with ASTM D4629 which is based on a combustion/chemiluminescence method.

EXHIBIT G-1  PERFORMANCE TEST CERTIFICATE

PERFORMANCE TEST CERTIFICATE

The undersigned duly authorized representative of (Name of Purchaser’s Company), under the provisions of the Agreement between [-------------] and [--------------], dated (_______) the “Agreement” hereby certifies that:

1.	Performance Tests have been conducted pertaining to Electrical Output, Heat Rate, Sound Levels and  Emissions [and in the case of combined cycle operations, Exhaust Gas Energy and Exhaust Gas Temperature] of the combustion turbine generator units referred to in the Agreement (each a “Unit” and collectively the “Units”) as set forth therein.

2.	During the most recent Performance Test, completed [date] the [turbine SNs] Units tested produced [-------] kW as the Adjusted Electrical Output for the [   ] Units when consuming [---] for fuel.

3.	During the most recent Performance Test, completed [date] the [turbine SNs] Units tested produced [-------] BTU/kWh as the Adjusted Heat Rate for the [    ] Units.

4.	During the most recent Sound Level Test, completed [date] the [turbine SNs] Units tested produced a Near Field Sound Level of [----] d(B)A.

5.	During the most recent Performance Test, completed [date] the [turbine SNs] Units tested produced as the Adjusted Emissions for the [    ] Units as set forth in the attached table.

6.	During the most recent Far Field Sound Level Test, completed [date] the [turbine SNs] Units tested produced a Far Field Sound Level of [----] d(B)A.

7.	During the most recent Performance Test, completed [date] the [turbine Sns], combined cycle Units tested produced Exhaust Gas Energy the for the [    ] Units as set forth in the attached table.

8.	During the most recent Performance Test, completed [date] the [turbine Sns], combined cycle Units produced Exhaust Gas Temperature as set forth in the attached table.

19.	Capitalized terms used herein and not defined herein shall have the respective meanings assigned to them in the Agreement.

IN WITNESS WHEREOF, has executed and delivered this Certificate as of the       day of        , 200  .

By:

Title:

From and on Behalf of

[Name of Purchaser’s Company]

EXHIBIT G-2  PERFORMANCE TEST COMPLETION CERTIFICATE

PERFORMANCE TEST COMPLETION CERTIFICATE

The undersigned duly authorized representative of (Name of Purchaser’s Company), under the provisions of the Agreement hereby certifies that:

1.	Performance Tests pertaining to Electrical Output and Heat Rate on the combustion turbine generator units referred to in the Agreement have been conducted (each a “Unit” and collectively the “Units”).

2.	As set forth in the Agreement, Seller guaranteed that (i) the Adjusted Electrical Output of each of the Units will be at least [-----] kW when consuming natural gas for fuel, and that in any event Seller guaranteed that the Units shall produce no less than [------] kW Adjusted Electrical Output when the Electrical Output is measured and adjusted in accordance with the Test Procedures and the Agreement and (ii) if six (6) or more Units are installed at the Facility, the average Adjusted Electrical Output of all such Units will be at least [-----] kW.

The results of the Performance Tests show that the Units produced an average Adjusted Electrical Output of ________, and that each Unit individually produced the Adjusted Electric Output set forth below:

| Unit | Adjusted Electrical Output |
| --- | --- |
| Unit No_____ [turbine SN] | ________ kW |
| Unit No_____ [turbine SN] | ________ kW |
| Unit No_____ [turbine SN] | ________ kW |

[USE A, B, and C BELOW AS APPROPRIATE]

A.	The Adjusted Electrical Output of the Units as set forth above, individually and, if applicable, collectively on average, are greater than or equal to the Electrical Output Guarantee and, if applicable, the Optional Electric Output Guarantee, and therefore, Seller is not liable for Performance Liquidated Damages associated with Electrical Output.

B.	The Adjusted Electrical Output of [turbine SNs] Units set forth above is/are less than the Electrical Output Guarantee of [___________], but greater than the Specific Performance Electrical Output Guarantee of [____________]; therefore, the undersigned has determined that the amount of Unit Output Liquidated Damages to be assessed against the Seller for failure to meet the Electrical Output Guarantee is U.S. $_____________.

C.	The average of the Adjusted Electrical Output of the Units is less than the Optional Electrical Output Guarantee of [             ]; therefore, the undersigned has determined that the amount of Optional Output Liquidated Damages to be assessed against the Seller for failure to meet the Optional Electrical Output Guarantee is US $              .

3.	As set forth in the Agreement, Seller guaranteed that the Adjusted Heat Rate of the [turbine SNs] Units will be at least [-----] BTU/kWh(LHV) when consuming natural gas for fuel, and that in any event Seller guaranteed that the Units shall demonstrate no less than a [------] BTU/kWh(LHV) Adjusted Heat Rate when the Heat Rate is calculated and adjusted in accordance with the Test Procedures and the Agreement.  The results of the Performance Tests show that each of the [turbine SNs] Units produced the Adjusted Heat Rate set forth below:

| Unit | Adjusted Heat Rate |
| --- | --- |
| Unit No_____ [turbine SN] | ________ BTU/kWh (LHV) |
| Unit No_____ [turbine SN] | ________ BTU/kWh (LHV) |
| Unit No_____ [turbine SN] | ________ BTU/kWh (LHV) |

[USE EITHER A OR B BELOW AS APPROPRIATE]

A.	The Adjusted Heat Rate of each of the Units as set forth above is less than or equal to the Heat Rate Guarantee and therefore, Seller is not liable for Performance Liquidated Damages associated with Heat Rate.

B.	The Adjusted Heat Rate of [turbine SNs] Units set forth above is greater than the Heat Rate Guarantee [-------------], but less than the Specific Performance Heat Rate Guarantee of [-------------]; therefore, the undersigned has determined that the amount of Heat Rate Liquidated Damages to be assessed against the Seller for failure to meet the Heat Rate Guarantee is U.S. $[----------------].

EXHIBIT H-1  TECHNICAL DIRECTION OF INSTALLATION

1.0	General.  The parties agree that as part of this Scope of Work Seller shall provide the requisite technical direction of installation (the “Technical Direction of Installation” or “TD of I”) support at the Site required for installation, start-up and correction of problems related to waived shop testing and commissioning of the Equipment.

2.0	Schedule.  Seller and Purchaser’s Representative shall coordinate the start and finish schedules of each of the TD of I personnel.  Seller shall provide a maximum two hundred forty (240) man-hours per Unit installed (straight time 40 hrs/week TD of I advisors as required to support Purchaser’s receipt of Equipment, installation, startup, commissioning and correction of problems related to waived shop testing until certified ready for testing in accordance with the Agreement. Seller shall provide a bar chart for its manpower staffing in support of the construction schedule, which shall be adjusted from time to time by Seller and Purchaser as the work progresses.  Hours worked by Seller’s TD of I personnel in excess of 40 hours straight time hours each week shall be deducted from the 240 manhour count, at the equivalent rate of one and one half straight time hours pursuant to Section 8 below.  Seller’s 40 hour work week is 8 hours per Day, Monday through Friday

3.0	Cost.  Seller shall bear each and every expense for services provided by its TD of I personnel including, but not limited to, international and local transportation, salary, lodging, per diem, taxes, work permits and expenses which costs are included within the Purchase Amount.  Any TD of I activities associated with field testing and correction of the Units which would normally be performed in the factory is included in Seller’s Scope of Work and is not counted against the 240 manhour count.

4.0	Supervision of Craft Labor.  Seller’s TD of I personnel shall not be responsible for the productivity or quality of work performed by Purchaser’s contractors and shall not have direct supervision responsibility over craft labor.

5.0	Seller Technical Direction Office Facilities.  Purchaser shall provide:

(a)	A secure, furnished private jobsite office facility of sufficient size (near the Equipment) that can accommodate 3 to 4 field engineers per Unit, where drawings, special tools, and other Seller proprietary materials and equipment can be kept and referred to or worked upon.

(b)	Purchaser shall coordinate installation of four (4) direct phone lines to Seller’s jobsite office facility and Seller shall be responsible for payment of the monthly local and long distance service and usage charges to the telephone company.

(c)	Seller’s jobsite office facility shall have HVAC and contain furnishing equivalent to that in use by Purchaser and its other subcontractor’s suitable for supporting Seller’s work.  The facility shall have adequate lighting, electrically outlets and sanitary facilities shall be accessible.  Seller shall be required to comply with the Site security and safety requirements at all times including control, use and parking restrictions relevant to Seller’s personnel’s privately owned vehicles.

6.0	Staffing Levels.

Seller shall provide biographical data and other qualifications as requested by Purchaser’s project manager for review and approval of Seller’s lead advisor (such approval not to be unreasonably withheld).

Staffing shall include:

(a)	Site manager not part of contract except in the case of large sites with 6 turbines, a site manager may be requested by the Purchaser.

(b)	Turbine Generator Installation team comprised of technical advisors skilled in mechanical erection of gas turbines and related equipment, electrical equipment installation and testing, Control System checkout, calibration and unit startup, and shall be capable of providing guidance and counsel for the following:

-	The inspection and unloading of the major components at the installation site and their placement on the foundations.

-	The setting of necessary shims between sole plates and the turbines.

-	The removal of shipping supports on the turbine and generator packages.

-	The installation of the turbine units to the proper center line and elevation.

-	The alignment of the accessory equipment and generators to the turbines.

-	The installation and checkout of conduit, piping, control wiring and instrumentation between the turbines and Seller supplied auxiliary equipment and generators.

-	Checkout and initial operation of the turbine starting equipment.

-	The sequencing and checkout of the turbine Milennium Control Panels.

-	The installation and checkout of the generator excitation/electric systems.

-	The startup of the turbine units with the Purchaser’s operating personnel.

-	Mark up two (2) sets of drawings to reflect the “as-built” condition of the equipment.  One (1) set for site records and one (1) set to be returned to GE Customer Service.

-	Installation and check out of all auxiliary and ancillary equipment provided under this Agreement.

-	Electrical checkout and powering of the control consoles.

7.0	Additional Services

In addition to providing the expertise outlined above, Seller’s personnel shall be relied upon to answer questions and provide or obtain interpretation of manufacturer supplied instructions and drawings during the execution of work (construction, erection, commissioning, etc.).  Included in this category of support are:

(a)	Confirmation that specifications and instructions to be applied during construction, erection and commissioning by the different Vendors are met and that the specified results of tests and examinations are obtained;

(b)	Corrections of construction/erection/commissioning software, if necessary, as far as design and engineering tasks are not concerned;

(c)	Confirmation that the necessary standard of quality has been sustained in all areas which could affect facts and information provided by Seller to Purchaser;

(d)	Immediate written objections to Purchaser’s representative if the standard of quality is jeopardized, and advise Purchaser’s representative in a timely manner on the implications where any work procedure may impair the Equipment warranty;

(e)	Troubleshooting, technical guidance and expertise during instrumentation and control systems loop and function checks;

(f)	Technical expertise for energization and synchronization activities performed during commissioning; and

(g)	Provide impromptu training to Facility operators during start up and commissioning.

8.0	Expected Work Week.  Purchaser anticipates that the normal work week on Site will consist of working six (6) Days per week (Monday through Saturday) for ten (10) hours per shift each work Day; however, such work hours and Days shall be adjusted to accommodate Purchaser’s general Site work schedule.  It is the intent of the parties that Purchaser shall have the flexibility to require Seller’s personnel to work more or less hours per Day than the standard work Day in support of certain construction activities.  All time worked, except for those hours worked in support of the waived shop tests, shall be subtracted from the total of Seller’s obligation set forth in Section 1.0 above.  Total TD of I hours worked in excess of the 240 manhours, subject to Sections 2 and 3 above, shall be reimbursed to Seller pursuant to a Change Order, at the following rates:

| Straight time (8hrs/Day) | = $135.00/hour (US & Canada) |
| --- | --- |
|  | $165.00/hour (International) |
| Overtime (excess of 8 hrs/Day Sundays and Holidays) = |  |
|  | $165.00/hour (US & Canada) |
|  | $248.00/hour (International) |

Additional manhours and other service rate classifications purchased will be subject to:

-	GE Aeroderivative and Package Services published rate sheet for technical assistance.

-	Required travel will be reimbursed at cost or in accordance with IRS mileage rates;

-	Travel time will be invoiced at the applicable straight time or overtime rate; and

-	Per diem will be applicable at the rate of $196.00 during all Days commencing on departure from point of origin through return or its equivalent.

9.0	Replacement of Unsatisfactory Personnel.  If any of Seller’s personnel provided under this Agreement fail, in Purchaser’s reasonable judgement, to fulfill his duties as assigned by Seller, Seller shall cause such personnel to properly perform such duties, or at the request of Purchaser replace the personnel. In the event of a replacement:

-	The replacement must be of equivalent qualifications to the person being replaced;

-	Seller shall provide Purchaser a resume of the recommended replacement;

-	The replacement must be approved by Purchaser, prior to the replacement’s   commencement of work, such approval, not to be unreasonably withheld; and

-	Seller shall bear all additional travel, living or other costs associated with removing the unsatisfactory individual and furnishing the replacement.

10.0	Supplemental Seller Personnel.  Seller’s personnel shall be direct employees of Seller, or Seller may elect to hire supplemental third party Sellers screened and trained by Seller.  In addition to any such screening and training, such personnel must have verifiable and demonstrable prior hands-on experience in installation or training as applicable to the work to be performed by such person. Seller shall provide Purchaser’s Representative resumes of all individuals selected by Seller as supplemental personnel pursuant to this Paragraph 9, and obtain Purchaser’s Representative’s prior approval of each individual’s assignment, such approval not to be unreasonably withheld.

11.0	Change of Seller’s Personnel.  Seller and Purchaser recognize that changing of personnel during the performance of the Scope of Work can be disruptive and adversely affect the timely and proper performance of the Scope of Work; however, both Seller and Purchaser realize that under certain circumstances, Seller may, on an exception basis, need to substitute personnel in the course of performance of the Scope of Work.  Seller may, on an exception basis, substitute personnel; provided that the following shall apply:

-	The replacement must be of equivalent capabilities to the person being replaced;

-	Seller shall provide Purchaser a resume of the recommended replacement;

-	Such change is for a compelling personal reason, or by mutual agreement the existing individual does not have the required skill;

-	The replacement must be approved by Purchaser prior to the replacement’s   commencement of work, such approval not to be unreasonably withheld, and,

-	Seller shall bear all additional travel, living or other costs associated with such change.

12.0	Debugging.  Seller shall provide with respect to TD of I, normal debugging of problems encountered during installation, start-up and commissioning of the equipment.  In the event debugging reveals a factory defect, Seller shall provide Purchaser written observations regarding such defect.

13.0	Release of Seller’s Personnel.  If Technical Direction of Installation Representative is/are released from site by Purchaser while the installation is in progress, the same Technical Direction of Installation Representative may not be available to return but will be replaced with a qualified Technical Direction of Installation Representative within two weeks after Company’s receipt of written request from the Purchaser for Technical Direction of Installation Representative.

14.0	Purchaser’s Responsibilities.  Purchaser will take all necessary precautions, at all times, for the safety of Company personnel at site.  This includes, but is not limited to, indoctrination of Purchaser’s safety practices, energization/de-energization of all power systems (electrical, mechanical and hydraulic) using a lock-out tag procedure, and conducting periodic safety meetings during construction and start-up.

EXHIBIT H-2  TRAINING

EXHIBIT I  CANCELLATION CHARGE

In the event Purchaser cancels this Agreement with respect to a Unit, Purchaser’s liability for cancellation charges shall not exceed the values set forth below for each Unit canceled:

| Receipt of Cancellation Notice Days After September 23, 1999 | Cancellation Charge/Fee (expressed as % of the Purchase Amount for the cancelled Unit) |
| --- | --- |
| 0-26 | 0 |
| 27-60 | 5 |
| 61-90 | 12 |
| 91-120 | 15 |
| 121-150 | 20 |
| 151-180 | 25 |
| 181-210 | 30 |
| 211-240 | 40 |
| 241-270 | 50 |
| 271-300 | 60 |
| 301-330 | 70 |
| 331-360 | 75 |
| 361-390 | 80 |
| 391-420 | 85 |
| 421-450 | 90 |
| 451-480 | 95 |
| After Day 481 | 100 |

Notes:

- Seller shall maintain title to the Unit when cancellation occurs prior to shipment.

- Cancellation exposure is 100% of the pro rata value of each Unit after shipment.

- The pro rata value of each Unit shall increase or decrease as applicable as a result of increases or decreases to the Purchase Amount due to executed Change Orders.

- The Purchase Amount with respect to a Unit will be calculated in accordance with Exhibits N-1 and N-2.

EXHIBIT J  QUALITY

1.0	QUALITY ASSURANCE AND CONTROL

1.1	Quality Assurance Arrangements

Seller, and its nominated Vendors shall work to defined quality assurance arrangements compliant with ISO 9001.  Seller shall indicate the results of any recent audits.

In addition to requirements detailed in ISO 9001, Seller shall:

- Ensure that all quality related activities are planned and that adequate resources are made available for these activities.

- Establish means by which all materials and components are identified through each stage of performance of the Scope of Work.  These measures will facilitate the traceability of materials as identified in the agreed quality plans.

- Arrange for the protection of the quality of the product to include delivery to the specified destination.

1.2	Vendors

Seller shall specify all quality assurance requirements to its Vendor and shall ensure that all Vendors comply with these requirements.

Seller shall undertake in respect of its nominated Vendors, where no such acceptable information is available or where the Vendor has not been subject to a quality audit within the previous 12 months, to carry out an audit of that Vendor in order to ensure that completion of works will be compliant with contract requirements.

Seller and its nominated Vendors maybe subject to a quality audit by Purchaser.

1.3	Quality Plans

Quality plans shall be prepared by Seller for all areas of activity.  These quality plans shall be submitted to Purchaser for review.

The format of the quality plans shall be agreed with Purchaser.  Seller shall ensure that all activity is carried out in accordance with the quality plans and will notify Purchaser of any deviations as they occur.

1.4	Review of Documents

Seller shall submit for review all quality plans and design documentation as may reasonably be required by Purchaser.  A schedule of drawings and documentation shall be maintained by Seller to show the current status and revision of each document.

1.5	Records

Seller shall maintain records as required by the quality plans.  All records including audit reports shall be made available for inspection by Purchaser, as required.

Seller shall generate records in a manner coincidental with the activities to which they refer, such that the quality status of each item can be readily verified.

All records shall be concisely compiled and coded.  They shall, in addition be clearly cross referenced to the parts or assemblies to which they refer.

Records shall in general, be available at the time of equipment delivery.  Such records shall include relevant certifications and build documentation together with any information which would facilitate the general traceability of component items or materials.

All records generated during the course of performance of the Scope of Work shall be retained by Seller for a minimum period of ten years from the date of Acceptance or supplied to Purchaser for its retention.

1.6	Seller’s Responsibility

Review and comment by Purchaser of the quality assurance procedures, quality plans, inspection and test arrangements operated by either Seller or his Vendors, will not relieve Seller of its obligation to provide Equipment which complies with the requirements of the Agreement.

2.0	QUALITY SURVEILLANCE

2.1	Quality Surveillance Requirements

Seller shall define the items which it proposes to Vendor together with all items for which quality plans (inspection and test plans) will be submitted.  Seller shall provide Purchaser’s Quality Assurance Manager the name of his representative authorized as having responsibility for resolving or obtaining resolution, of any problems arising in respect of the acceptability of raw materials, components, and assemblies.

Seller shall establish and maintain a documented inspection system capable of producing objective evidence that all material manufactured parts and assemblies comply with the quality requirements of the Agreement.

General information on the type of system in use by Seller shall be provided.

Seller’s inspection system shall include procedures used for controlling the following functions:

- Availability at inspection points of applicable drawings, instructions, etc and prompt removal of obsolete documents.

- Maintenance and calibration of suitable inspection and test equipment, which should comply with requirements set out in ISO 9001

- Inclusion (or referencing) on purchase orders of the necessary technical inspection and test details to meet the specified requirements and of Purchaser’s possible involvement at the Vendor’s facilities.

- Incoming, in process and final inspection and inspection of packing and marking.

- Means of identifying inspection status throughout manufacture.

- Provisions of complete inspection and test records.

Seller shall submit for review within 30 days after the execution of this Agreement, a quality plan, excluding testing and inspection on work already completed as of such submission date, in which case test records will be provided, (inspection and test plan) defining the program of quality control and inspection activities which it or its Vendors will perform in order to ensure that the manufacture and completion of the plant complies with the specified requirements.  The quality plan may be of any form to suit Seller’s system, but it shall as a minimum:

- Indicate each inspection and test point and its relative location in the production cycle including incoming, packing and site inspections.

- Indicate mandatory Seller Factory hold points for an item or process before the work can proceed.

Seller shall include in all its orders to Vendors, a note advising that all materials and equipment are subject to inspection by Purchaser.

In order to verify compliance with engineering, procurement, manufacturing requirements and program, Purchaser shall have access at all times as arranged by Seller, to all places where materials or equipment are being prepared or manufactured, including the works of Vendor’s raw materials.

Inspection of the Equipment may be by Purchaser and may include the following activities:

- Evaluation of Seller’s system and quality plans.

- Periodic monitoring to confirm the effectiveness of and Seller’s compliance with the established system procedures, quality plan and inspection and test instructions.

- Witnessing of inspections and test and/or verification of inspection records including:

a.	Compliance of raw material with specified requirements.

b.	Compliance of manufactured parts, assemblies and final items with specifications, drawings, standards and good engineering practice.

c.	Periodic inspection of Seller’s design manufacturing, installation work and the production of progress reports.

d.	Witnessing of inspections and tests.

e.	Packing for shipment including check for completeness of shipment, handling requirements, and identification.

Seller’s compliance with equipment documentation, drawing, delivery and commissioning schedules shall be monitored by Purchaser.

Raw materials, components, shop assemblies and the installation thereof, shall be subject to inspection and test by Purchaser as required by the specification and the extent practicable at all times and places during the period of manufacture.

Seller shall keep Purchaser informed, in advance, of the time of starting and of the progress of the Scope of Work in its various stages so that arrangements can be made for inspection and for test.  He shall also provide without additional charge, all reasonable facilities and assistance for the safety and convenience of Purchaser in the performance of his duties.  All of the required tests shall be made to Seller’s expense, including the cost of all samples used.

In the event of the unreasonable postponement, by Seller, of tests previously scheduled, or of the necessity tests due to unsatisfactory results of the original tests, or other reasons attributable to Seller, Seller will bear the costs incurred by Purchaser of his nominated representative in re-inspecting the non-conforming item or its replacement.

Seller’s and nominated Vendor’s quality assurance program shall identify and shall isolate items not conforming to the technical specification.  All such items shall be reported to Purchaser via a non-conformance report which shall identify:

- The identification of the item.

- The relevant specification, drawing etc including revision number.

- A sketch of the non-conformance.

- The method by which the non-conformance was identified.

- The cause of the non-conformance.

- The proposal for resolution the con-conformance.

- A concession application including the technical justification and the appropriate supporting documents if applicable.

- The proposed action to prevent re-occurrence.

Seller shall not offer, unless otherwise agreed, any item of equipment for inspection to Purchaser until all planned inspections and tests to date have been completed to the satisfaction of Seller.

Any non-conformance identified by Purchaser may be notified by issue of Purchaser’s non-conformance report to Seller.  Notification of re-inspection shall not be made until the completed non-conformance report together with any applicable concession application have been submitted to Purchaser.

The inspection and tests by Purchaser of any components or lots thereof does not relieve Seller of any responsibility whatever regarding defects or other failures which maybe found before the end of the Primary Warranty Period.

Seller shall provide a quality release certificate confirming compliance with the contract requirements and a data book containing relevant manufacturing and quality records.

Seller shall furnish Purchaser with 4 copies of the data book.

The parties agree that, in light of the fast-track nature of the project for which these Units are being supplied, and the advanced stage of manufacturing, Purchaser and Seller shall review the requirements, obligations and responsibilities set forth in this Exhibit J during two pre-inspection/quality meetings (one for the gas turbine, one for the generator). Seller shall coordinate and schedule a mutually agreed date for both meetings at Seller’s factory, with the goal of having them within two months after the Order Definition Meeting.  Seller shall document all mutually agreed adjustments to Exhibit J, issue the notes in letter form for review and agreement, and issue a final conformed letter  for subsequent endorsement by the parties and use as quality assurance guidelines.

EXHIBIT K  PROJECT PLANNING

1.	PURPOSE AND OBJECTIVES

1.1	Seller shall provide information and data required for development of a Project Schedule for the Work in accordance with the requirements of this Exhibit.  Seller’s information and data shall be provided electronically in a software which can be readily used in “Primavera Project Planner” software which will be used by Purchaser to develop the Project Schedule.  The purpose of the Project Schedule shall be to:

(1)	assure adequate planning, scheduling and reporting during the prosecution and progress of the Scope of Work by Seller in order to complete the Scope of Work in accordance with any and all milestones;

(2)	assure coordination of the efforts of Seller, his various Vendors and Purchaser furnished equipment and materials, if any;

(3)	assist Seller, and Purchaser, in monitoring the progress of the Scope of Work and in evaluating proposed changes to the Agreement and the Project Schedule.

2.	PROGRESS UPDATES

2.1	The Project Schedule shall be updated on a monthly basis and on a periodic basis throughout the duration of the Scope of Work, and until Agreement Completion.  Seller shall meet with Purchaser at the completion of each agreed upon period to review actual progress made through the date of the Project Schedule update, including dates for activities actually started and/or completed, and to review the overall percentage of the Scope of Work actually completed.  The data date of each Project Schedule update shall be the last Day of the month, or some other Day previously designated by Purchaser.  In case of disagreements at the Project Schedule update meeting concerning actual progress to date, Purchaser’s determination shall govern.

2.2	In addition to the Project Schedule updates, Seller shall submit a Monthly Contractor’s Progress Report containing the following minimum information as follows:

MONTHLY CONTRACTOR’S PROGRESS REPORT

Timing:	Submitted 4 copies (4th of each Calendar month)

Contractor Name:

Reporting Month:

(1)	Management Summary (One Page)

Overall Project Situation

-  Major Activity

-  Significant Problems

(2)	Progress Review

Milestone Report

-  Updated Bar Chart Schedule (Current vs. Target)

-  Problems Affecting Progress

-  Decisions and Actions

-  Actions and Orientations required from Purchaser

(3)	Commercial Situation

Payment Status

-  Change Order Register

-  Notice of Claims

3.	RECOVERY SCHEDULE

3.1	Should the updated Project Schedule show at any time during Seller’s performance, in the sole opinion of Purchaser, that Seller is fourteen (14) or more days behind schedule for any [Specific Date, ] Seller shall prepare a [Recovery Schedule ] at no additional cost to Purchaser (unless Purchaser is solely responsible for the event or occurrence which has caused the schedule slippage) explaining and displaying how Seller intends to reschedule his work in order to regain compliance with the Project Schedule.

Note: Undefined Terms

4.0 PROJECT SCHEDULE REVISIONS

4.1	If, as a result of the monthly and periodic Project Schedule update, it appears the Project Schedule no longer represents the actual prosecution and progress of the Scope of Work, Purchaser will request, and Seller shall submit, a revision to the Project Schedule.

4.2	Seller may also request revisions to the Project Schedule in the event Seller’s planning for the work is revised.  If Seller desires to make changes in the Project Schedule to reflect revisions in its method of operation and scheduling of the Scope of Work, Seller shall notify Purchaser in writing, stating the reason for the proposed revision.  In no case will Notice to Purchaser of a request for schedule revision relieve Seller of any of his obligations under this Agreement.  All Project Schedule revisions and updates shall conform to all provisions of the Agreement documents contained herein.

EXHIBIT L EQUIPMENT REQUIRING INSURABILITY CERTIFICATE

Seller shall provide assistance as necessary in order to ensure that the following Equipment is inspected by Purchaser’s Insurance Representative in attainment of an insurability certificate:

(a)	Generator

(b)	Generator Module

(c)	Gas Turbine Module

(d)	Control Room Module

(e)	Lube Oil Module

(f)	Auxiliary Module

(g)	Fin-Fan Cooler Module

EXHIBIT M-1  NOT USED

EXHIBIT M-2 NOT USED

EXHIBIT N-1  NOT USED PURCHASE AMOUNT RECONCILIATION

Items Included in Initial Purchase Amount U.S. Dollars Subtotal Unit Price For Units -  $/Unit  Sets of Sprint Power Boost Enhanced System Hardware (Option L) $450,000/Unit  Option D - Fin Fan Oil Coolers - ___ Units @ $63,000/Unit $63,000/Unit  Option E - Alternate side location for piping connections and turbine removal Included  Option I & Option J - Water Injection Metering System w/upgrade to duplex NOx water pressurization pump skid $57,000/Unit  Option O - Turbine Inlet Air Chilling/Anti-Ice Coil Included -0- Option Q - Winterization Package Included -0- Option Y - 3 Extra CT’s Terminated in MGTB for Redundant Relay Protection $23,000/Unit  Purchase Amount Reconciliation

EXHIBIT N-2  OPTIONS

| Item | Notification Required to Secure Option | Quantity | Price in U.S. Dollars |
| --- | --- | --- | --- |
| Transportation Option A | 6 months | Per Unit | 5% + Seller’s Cost |
| Transportation Option B | > 3 or < 6 months | Per Unit | 7% + Seller’s Cost |
| Transportation Option C | < 3 months | Per Unit | 10% + Seller’s Cost |
| Option H - Dual Fuel System | 10 months | Per Unit | $280,000 |
| Option J - Upgrade to Dual Water Injection Skids w/Enclosures | 7 months | Per Unit | $57,000 |
| Option P1 - Exhaust Assembly (45 ft. 85 dBA) (Standard Base) | 7 months | Per Unit | $198,000 |
| Option P2 - Exhaust Assembly (60 ft. 85 dBA) (Standard Base) | 7 months | Per Unit | $236,000 |
| Option P3 - Exhaust Assembly (45 ft. 85 dBA) (Heavy Base) | 7 months | Per Unit | $233,000 |
| Option R - LM6000 Engine Level 1 Maintenance and Borescope Training | 6 months | Per Class | $28,000 |
| Option S - Modular Control Room (for up to 2 units) | 7 months | 1 | $125,000 |
| Option T - Switchgear, Generator Circuit Breaker in NEMA 3R enclosure (as described in Seller’s Published Product Specification Manual) | 7 months | Per Unit | $130,000 |
| Option U - Unit Motor Control Center | 7 months | Per Unit | $45,000 |
| Option V - Chiller Module (2200 Tons) | 7 months | Per Unit | $950,000 |
| Option W - Cooling Tower for Chiller Module | 7 months | Per Unit | $150,000 |
| Option X - O&M Manuals on CD-ROM w/Browser and Bookmarks | 6 months | Per Config. | $25,000 |
| Option Y - 3 Extra CT’s Terminated in MGTB for Redundant Relay Protection | 6 months | 1 Lot Per Unit | $23,000 |
| Storage Cost - Per Unit | Putting into storage |  | $10,800 per move |
|  | Taking out of storage |  | $8,300 per move |
|  | No charge for first 90 days |  |  |
|  | For months 4, 5 & 6 |  | $3,800 per month |
|  | Per month after month 7 |  | $4,800 per month |

NOTE: This Agreement may be amended by Change Order to add other balance of plant equipment modules to Seller’s Scope of Work.

EXHIBIT O  HAZARDOUS MATERIAL NOTIFICATION

HAZARDOUS AND TOXIC SUBSTANCES
DISCLOSURE REQUIREMENTS
AGREEMENT NUMBER

Show the order identification 
on all correspondence

Seller:

Attention:

Address:                                      ZIP:

Phone Number: (     )

HAZARDOUS AND TOXIC SUBSTANCES DISCLOSURE REQUIREMENTS

The Occupational and Health Act (OSHA) of 1970, and OSHA regulation 29CFR 1910 contain hazardous and toxic substances reporting requirements.

Seller shall be required to provide the following documents, as applicable to Purchaser at the time of Agreement, if possible, but not later than ten (10) days thereafter. A copy of the Material Safety Data Sheet, (Form OSHA-20), or equivalent, must accompany each shipment of hazardous or toxic substances to Purchaser.  The following documents may be required for more than one item within the Agreement.

MATERIAL SAFETY DATA SHEET

The Material Safety Data Sheet (Form OSHA-20), or equivalent is required for each material containing a chemical substance which: (i) is regulated by any Federal law or rule, (ii) is listed in the latest edition of the National Institute for Occupational Safety and Health Registry of Toxic Effects of Chemical Substances. (iii) testing has yielded positive evidence of an acute or chronic health hazard, or (iv) has a Material Safety Data Sheet available to Seller indicating that the material may pose a hazard to human health.

-AND/OR-

SELLER DISCLAIMER STATEMENT

Seller may alternatively submit a disclaimer statement set forth below:

HAZARDOUS AND TOXIC SUBSTANCES DISCLAIMER

Seller hereby swears or affirms that the material furnished on this Purchase Order does not, to its best knowledge, contain any toxic substances or harmful physical agents as defined under 29CFR 1910.  In the event Seller discovers that such hazardous and toxic substances or agents are to be supplied, an appropriate Material Safety Data Sheet (Form OSHA-20), or equivalent shall be immediately supplied to Purchaser.

| ________________________ Signature of Company Officer | Date: _______________________________ |
| --- | --- |
| ________________________ Title |  |

NONCOMPLIANCE

Seller assumes all responsibility for its failure to supply Purchaser a completed Material Safety Data Sheet (Form OSHA-20), or equivalent or a Seller Disclaimer Statement as applicable.

EXHIBIT P  UNIT SERIAL NUMBER

UNIT SERIAL NUMBERS:

| Unit 17 : | 309604 |
| --- | --- |
| Unit 18 : | 309719 |
| Unit : |  |
| Unit : |  |
| Unit : |  |
| Unit : |  |

EXHIBIT Q SAMPLE PACKING LIST

| PKG. # | DESCRIPTION | GROSS WT. | L | W | H | CFT. |
| --- | --- | --- | --- | --- | --- | --- |
| PC 1 | LM6000 Generator Base | 68000 | 337 | 172 | 178 | 5971 |
| PC 2 | Turbine Base | 120000 | 371 | 172 | 178 | 6573 |
| PC 3 | Brush Generator | 176000 | 301 | 150 | 130 | 3397 |
| PC 4 | Roof Skid | 44000 | 470 | 172 | 149 | 6971 |
| Box 5 | V.B.V. Silencer | 17500 | 174 | 75 | 148 | 1118 |
| Box 6 | V.B.V. Duct | 15600 | 158 | 150 | 106 | 1454 |
| Box 7 | V.B.V. Hood | 3480 | 140 | 103 | 60 | 501 |
| PC 8 | L.H. Coil Module “A” | 42000 | 400 | 129 | 149 | 4449 |
| PC 9 | R.H. Coil Module “B” | 42000 | 400 | 129 | 149 | 4449 |
| PC 10 | Plenum | 24400 | 394 | 146 | 149 | 4960 |
| Box 11 | Raincap | 1320 | 82 | 82 | 54 | 210 |
| Box 12 | Raincap | 1320 | 82 | 82 | 54 | 210 |
| Box 13 | Roof Skid silencer | 2290 | 80 | 80 | 76 | 281 |
| Box 14 | Roof Skid Silencer | 2290 | 80 | 80 | 76 | 281 |
| Box 15 | Electrical Shiploose | 1105 | 96 | 48 | 38 | 101 |
| Box 16 | Generator Exhaust Hood | 9070 | 174 | 160 | 87 | 1314 |
| Box 17 | Neutral Cubicle | 4400 | 96 | 68 | 120 | 453 |
| Box 18 | Lineside Cubicle | 2800 | 68 | 68 | 124 | 332 |
| Box 19 | Mechanical shiploose | 2785 | 170 | 48 | 43 | 203 |
| Box 20 | Exhaust Flashing | 725 | 62 | 62 | 17 | 38 |
| Box 21 | Zurn Coupling | 1225 | 120 | 31 | 33 | 71 |
| Box 22 | Demister | 720 | 36 | 36 | 74 | 56 |
| Box 23 | Roof Skid Transition | 1710 | 148 | 78 | 34 | 227 |
| Box 24 | Nuts & Bolts Shiploose | 1245 | 48 | 48 | 36 | 48 |
| Box 25 | Paint (1-5 Gal.) | 130 | 24 | 18 | 23 | 6 |
| Box 26 | Generator Transition Throat | 1800 | 125 | 125 | 39 | 353 |
| Skid 27 | CO2 Bracket | 600 | 91 | 24 | 35 | 44 |
| Box 28 | Run Down Tanks (4) | 1455 | 106 | 46 | 30 | 85 |
| Box 29 | Water Injection Skid | 7620 | 195 | 62 | 64 | 448 |
| Box 30 | Shear Lugs (8) | 1020 | 45 | 25 | 17 | 11 |
| Box 31 | Pressure Balance Pipe | 500 | 54 | 48 | 24 | 36 |
| Box 32 | Walkways & Handrails | 3640 | 152 | 60 | 44 | 232 |
| Box 33 | Coil Module Parts | 1225 | 44 | 44 | 38 | 43 |
| Skid 34 | Support Structure & Ladder | 5620 | 312 | 81 | 62 | 907 |
| Box 35 | H-Frame | 2085 | 174 | 35 | 39 | 137 |
| Box 36 | Auxiliary Skid | 17000 | 180 | 140 | 100 | 1458 |
| Box 37 | CO2 Enclosure | 2535 | 106 | 34 | 106 | 280 |
| Box 38 | Sprint Skid | 2560 | 84 | 73 | 67 | 238 |
| Box 39 | Batteries & Racks | 1210 | 65 | 37 | 37 | 51 |
| Box 40 | Battery Chargers (2) | 610 | 44 | 33 | 49 | 41 |
| Box 41 | Generator Fan Expansion Joints | 450 | 51 | 51 | 24 | 36 |
| Box 42 | Ruffneck Heaters (2) | 615 | 66 | 35 | 38 | 51 |
| Box 43 | Cold Weather Enclosure/Gauge Panel | 1180 | 118 | 111 | 17 | 129 |
| Box 44 | CO2 Bottles (8) | 2700 | 37 | 37 | 72 | 57 |
| Box 45 | Flex Hoses | 260 | 64 | 19 | 14 | 10 |
| Box 46 | Misc. Shiploose | 145 | 34 | 26 | 17 | 9 |
| Box 47 | Acid (45 GALS.) | 640 | 48 | 19 | 36 | 19 |
| Box 48 | Control Panel | 4125 | 128 | 44 | 102 | 332 |
| Box 49 | Engine Lift Fixture | 1440 | 128 | 76 | 17 | 96 |
| Box 50 | Alignment Tool | 505 | 104 | 29 | 31 | 54 |
| Box 51 | Discharge Heads | 125 | 27 | 27 | 14 | 6 |
| Box 52 | Hood for Aux. Skid | 1290 | 77 | 52 | 83 | 192 |
| Box 53 | Pre-Filter Doors (16) | 2090 | 128 | 58 | 52 | 223 |
| Box 54 | Pre-Filter Doors (16) | 2015 | 128 | 58 | 52 | 223 |
| Box 55 | TCP Shiploose | 80 | 27 | 27 | 14 | 6 |
| Box 56 | CO2 Bottles (4) | 1405 | 26 | 26 | 72 | 28 |
| Box 57 | LG. Lift Pins (4) SM. Lift Pins (4) | 7260 | 114 | 86 | 30 | 170 |
| PC 58 | Donaldson Spreader Bar | 4650 | 440 | 33 | 12 | 101 |
| PC 59 | Main Unit Spreader Bar | 1800 | 211 | 26 | 12 | 116 |
| PC 60 | Generator Spreader Bar | 1400 | 133 | 126 | 12 | 116 |
| Box 61 | Slings & Shackles | 10000 | 136 | 96 | 42 | 317 |
| PC 62 | Vertical Stack Duct | 13110 | 180 | 131 | 132 | 1801 |
| PC 63 | Vertical Stack Duct | 23350 | 361 | 131 | 132 | 3613 |
| PC 64 | Vertical Duct | 33250 | 361 | 150 | 150 | 4701 |
| PC 65 | Breech Duct | 37750 | 181 | 197 | 151 | 3116 |
| Lot 66 | Ladder & Platforms | 10000 | 480 | 110 | 60 | 2933 |

EXHIBIT R  SCHEDULE OF WITNESS TEST POINTS

EXHIBIT S  FINAL WAIVER  OF LIENS FORM

AFFIDAVIT AND RELEASE OF LIEN

THE STATE OF ________	§

COUNTY OF ___________	§

[Seller Name] hereby acknowledges the receipt and sufficiency of the sum of $                , (                                                           ), and other good and valuable consideration, in full payment for all design, labor, materials, equipment, supplies and services, for the supply of GTG packages for the [            project name                  ], (“the Project”) pursuant to the Purchase Agreement No. [           ] dated [--------] , between [Seller Name] (the “Seller”) and [--------] (the “Purchaser”).

[Seller Name] hereby acknowledges and certifies that [--------] paid                      , all sums owing and that it has no further claims against [-------], or any subsidiary, affiliate or parent of [-------] except for the outstanding unresolved Change Order listed in Appendix A to this Affidavit.  [if none, delete all of paragraph after “except for...”]

[Seller Name] further covenants and warrants that the Project is free from all liens and claims for payment by any subcontractor, materialman or employee.

In consideration for such full payment, [Seller Name], on behalf of itself and its predecessors, employees, agents, officers, directors, shareholders, representatives, attorneys, successors, insurers and assigns, subcontractors and on behalf of any other persons claiming by, through or under [Seller Name], does hereby waive, release, and relinquish its rights to and discharge, release and acquit [-------], its subsidiaries, affiliates and parent and its employees, agents, officers, directors, shareholders, representatives, attorneys, successors, insurers, assigns and subcontractors, from any and all causes of action, claims, demands, debts, liabilities, expenses or costs of any kind and every character and nature whatsoever, including but not limited to any lien claims or rights, whether known or unknown, contingent or fixed, either in or arising out of the law of contracts, torts or property rights, whether arising under statutory law or common law, at law or in equity, with respect to the above-referenced property.  Furthermore, [Seller Name] agrees to Indemnify and hold harmless [Purchaser Name], its subsidiaries, affiliates and parent and all other persons or entities released by [Seller Name] above against the full amount of any liability, loss, claim, damage, or expense (including attorneys’ fees and any judgment required to be paid) in connection with any of the matters it has released in the event any person should assert against such released person or entity a claim under assignment or title derivative from [Seller Name] and in connection with any claims made in connection with or relating to [Seller Name] provision of design, labor, materials, equipment, supplies and/or services on the above-referenced property.

EXECUTED this _________ day of ______________________, 200__.

[Seller Name] ___________________

By:____________________________

Name:__________________________

Print or Type

Title:___________________________

SWORN TO AN SUBSCRIBED BEFORE ME, under my official hand and seal of office on this ____ day of ___________________, 200__.

______________________________

Notary Public in and for

the State of ___________

My Commission Expires:
_____________________

(SEAL)

AFFIDAVIT

THE STATE OF ________	§

COUNTY OF ___________	§

BEFORE ME, the undersigned Notary Public, on this day personally came and appeared                       known to me to be the individual whose name is subscribed to the foregoing RELEASE OF LIEN and being duly sworn, did state and acknowledge on his oath that he is the                     of                           , is authorized to execute and deliver the foregoing on behalf of                          as an act and deed of that entity for the purposes and consideration therein expressed.

GIVEN UNDER MY HAND AND SEAL OF OFFICE this           day of                 , 200    .

______________________________

Notary Public in and for

the State of ___________.

(SEAL)

My Commission Expires:

_____________________

CERTIFICATION

This is to certify that all work covered by Invoice No. [__________]  is complete and that the invoice is correct, authentic and the only one issued for the work described therein.

[      NAME OF OFFICER      ]

A C K N O W L E D G E M E N T

(COUNTRY) [                       ]

(CITY)    [                       ]

Before me, a Notary Public for and in the City of [     CITY     ], [     COUNTRY     ], this [     DATE      ] personally appeared [     NAME OF OFFICER    ], exhibiting to me his Residence Certificate No. [               ] issued at [                    ], [     NAME OF OFFICER    ] on [             ] to be the same person who executed the foregoing Certification acknowledged to me that the same is a free and voluntary act and deed and to me known as the same person who acknowledged this certification.

In witness hereof, I have hereunto set my hand and affixed my notarial seal this [      ] of [          ], 200[---] in

[   NAME OF CITY   ] [     COUNTRY     ].

[       NAME OF NOTARY       ]

Notary Public, State of ______.

My Commission Expires __________

Doc. No. ____________

Page No. ____________

Book No. ____________

Series of 200

W  I  T  N  E  S  S  :

[         NAME          ]								[          NAME          ]

EXHIBIT T  NOT USED

EXHIBIT U  FACILITY SPECIFIC PERFORMANCE LEVELS

- Includes:  Heat Rate, Output and Emissions for liquid fuel. See §10.8.4.

------------------ COMPARISON OF HEADERS ------------------

-HEADER 1-

------------------ COMPARISON OF FOOTERS ------------------

-FOOTER 1-

HOU:554886.3 WAS:83333.1

554886-3 xi ii

-FOOTER 2-

554886-3 WAS:83333.1

E

-FOOTER 3-

HOU:554886.3 WAS:83333.1

554886-3 146 69

D

This redlined draft, generated by CompareRite (TM) - The Instant Redliner, shows the differences between -

original document   : C:\DOCUME~1\LINDJ~1.AKL\LOCALS~1\TEMP\HOU_554886_3

and revised document: C:\DOCUME~1\LINDJ~1.AKL\LOCALS~1\TEMP\WAS_83333_1

CompareRite found   43 change(s) in the text

CompareRite found    5 change(s) in the notes

Deletions appear as Overstrike text

Additions appear as Double Underline text