# EXHIBIT A  BASIS CONDITIONS

Performance Guarantee conditions for the Units shall be as set forth below:

| Fuel | Natural Gas | Units of Measure |
| --- | --- | --- |
| Fuel Composition | See Exhibit A-1 |  |
| Load | Base Load |  |
| Ambient Temperature (dry bulb) | 55 | °F |
| Barometric Pressure | 14.55 | PSIA |
| Ambient Relative Humidity | 55 | % |
| Fuel LHV @ 80 deg F | 20,659 | BTU/lb |
| Fuel Temperature | 365 | °F |
| Inlet Loss (Static) | 3 | In. H20 |
| Exhaust Loss (Static) | 16 | In. H20 |
| Generator Power Factor (Lagging/Leading) | 0.85 |  |
| Generator Frequency | 60 | Hertz |

[Note:  This will need to be revised on a case-by-case basis]

# EXHIBIT A-1 BASIS FUEL

Component				Mol Percent

Methane C1				95.173

Ethane C2				2.898

Propane C3				0.074

Iso-Butane C4				0.010

n-Butane C5				0.011

Iso-Pentane C5			0.003

n-Pentane C5				0.001

Hexane and above C6+		0.001

Nitrogen N2				1.146

Carbon Dioxide CO2			0.682

Total					100.00

[Note:  This will need to be revised on a case-by-case basis]

# EXHIBIT A-2 SELLER FUEL SPECIFICATION

The Unit shall be capable of operating with natural gas fuels meeting the requirements in GEI 41040F dated January 1999, (Attachment 1).

Purchaser shall be required to comply with Seller’s specification for Gas Turbine Compressor Washing Liquid Washing Recommendations for Gas Turbines with Pulsed Water Wash Systems,

Reference GEK-107122A (Attachment 2).

[Note:  Each attachment must be provided prior to execution]

# EXHIBIT B  SCOPE OF WORK/SPECIFICATION

Attached is Purchaser’s Specification Revision 3, dated May 9, 2000.

[Note:  I assume this will change on a case-by-case basis]

# EXHIBIT B-1  SPECIFICATION

Attached is Seller’s specification for the Scope of Work, Reference 90782AG revision 0, dated April, 2000.

[Note:  I assume this will change on a case-by-case basis]

# EXHIBIT B-2 GUARANTEED DELIVERY DATE

Item:					Guaranteed Delivery Dates:

Gas Turbine					[		]

Generator					[		]

[Note:  This will need to be revised on a case-by-case basis]

# EXHIBIT B-3 PERFORMANCE GUARANTEES AND SPECIFIC PERFORMANCE GUARANTEES

B.3.1	Specific Performance Exhaust Gas Temperature and Energy Guarantees.

B-3.1.1	Exhaust Gas Temperature Guarantee.  Seller guarantees that the Adjusted Exhaust Gas Temperature of the Unit as measured during the most recent Performance Test shall not be less than 1110 degrees Fahrenheit (°F) (the "Exhaust Gas Temperature Guarantee").

B-3.1.2	Specific Performance Exhaust Gas Temperature Guarantee.  As a Specific Performance Obligation, Seller guarantees that the Adjusted Exhaust Gas Temperature of the Unit as measured during the most recent Performance Test shall not be less than 1092 degrees Fahrenheit (°F) and shall not be greater than 1130 °F (the "Specific Performance Exhaust Gas Temperature Guarantee").  Subject to the provisions of Section 10.12.8, if the Adjusted Exhaust Gas Temperature of the Unit is within the preceding specified range, Seller will be considered to have satisfactorily caused the Unit to meet the Specific Performance requirement associated with the Specific Performance Exhaust Gas Temperature Guarantee.

B-3.1.3	Exhaust Gas Energy Guarantee.  As a Specific Performance obligation, Seller guarantees that the Adjusted Exhaust Gas Energy of the Unit as measured or calculated during the most recent Performance Test of the Unit shall be greater than or equal to 952.0 x 106 BTU/hr (LHV) (the "Exhaust Energy Guarantee").

B-3.1.4	Specific Performance Exhaust Gas Energy Guarantee.  As a Specific Performance obligation, Seller guarantees that the Adjusted Exhaust Gas Energy of the Unit as measured or calculated during the most recent Performance Test of the Unit shall be greater than or equal to 926.9 x 106 BTU/hr (LHV) (the "Specific Performance Exhaust Energy Guarantee").  Subject to the provisions of Section 10.12.8, if the Adjusted Exhaust Energy of the Unit is greater than or equal to the Specific Performance Exhaust Energy Guarantee, Seller will be considered to have satisfactorily caused the Unit to have met the Specific Performance requirement associated with Specific Performance Exhaust Energy Guarantee.

B.3.2	 Specific Performance Sound Level Guarantees.

B.3.2.1   Near Source Sound Level Guarantee.  As a Specific Performance obligation, Seller guarantees that the near field average A-weighted sound pressure levels of each Unit shall not exceed 85dB(A) (referenced to 20 micropascals) (the "Near Source Sound Level Guarantee") when measured during a Performance Test or Sound Level Test in accordance with the Sound Level Test Procedures at one and half (1.5) meters above any working elevation and one (1) meter from the surface.

The Near Source Sound Level Guarantee is limited to normal continuous sound sources within the Scope of Work.

B.3.2.2   Far Field Sound Level Guarantee.  As a Specific Performance obligation, Seller guarantees that the far field average A-weighted sound pressure level of the Unit (referenced to 20 micropascals) as installed and erected shall not exceed 67 dB(A) at 400 feet (the values at the stated distances from the nearest edge of the Unit) (the “Far Field Sound Level Guarantee”) when measured during a Performance Test or Sound Level Test while operating at steady state loads from 50 to 100 percent in accordance with the Sound Level Test Procedure.

B.3.3	Specific Performance Exhaust Emissions Guarantee.

B.3.3.1  Emissions Guarantee.  As a Specific Performance obligation, Seller guarantees that the Adjusted Emissions of the Unit when the Unit is operated between 20 °F and 90 °F, from 50% load through Base Load, between 0% and 100% humidity and at all other Basis Conditions (the "Emissions Guarantee") will not be greater than the following values:

Category		Value				Units of Measure

NOx			9				ppmvd @ 15% O2

CO			9				ppmvd

PM 10			18				lb/hr

VOC’s			1.4				ppmvw

Subject to the provisions of Section 10.12.8, if the Adjusted Emissions of the Unit are less than or equal to the  Emissions Guarantee, Seller will be considered to have satisfactorily caused the Unit to have met the Specific Performance requirement associated with the Emissions Guarantee.

B.3.4  Electrical Output Guarantees.

B.3.4.1  Electrical Output Guarantee.  Seller guarantees that the Adjusted Electrical Output, as demonstrated during the most recent Performance Test, shall be equal to or greater than 169,450 kW (after deducting the Unit's auxiliary Loads) (the "Electrical Output Guarantee").

B.3.4.2  Specific Performance Electrical Output Guarantee.  As a Specific Performance obligation, Seller guarantees that the Adjusted Electrical Output of the Unit, as demonstrated during the most recent Performance Test, shall be equal to or  greater than 164,964 kW (after deducting the Unit's  auxiliary loads) (the "Specific Performance Electrical Output Guarantee").

B.3.5  Heat Rate Guarantees.

B.3.5.1  Heat Rate Guarantee.  Seller guarantees that the Adjusted net Heat Rate of the Unit, as demonstrated during the most recent Performance Test, shall not exceed 9380 BTU/kWh (LHV) (the "Heat Rate Guarantee").  The Heat Rate Guarantee is net of the Unit's auxiliary loads.

B.3.5.2  Specific Performance Heat Rate Guarantee.  As a Specific Performance obligation, Seller guarantees that the net Adjusted Heat Rate of the Unit, as demonstrated during the most recent Performance Test, shall not be more than 9656 BTU/kWh (LHV) (the "Specific Performance Heat Rate Guarantee").  The Heat Rate Guarantee is net of the Unit's auxiliary loads.

[Note:  The guarantees will need to be revised on a case-by-case basis.]

# EXHIBIT B-4  APPROVED VENDORS

APPROVED VENDORS

Inlet Filter House

Braden Steel			Tulsa, OK

Donaldson			Baldwin, WI

Pneumafil Corp.		Charlotte, NC

J & G Steel			Sapupla, OK

Gas Valve Module

Mitten Fluid			Syracuse, NY

Becon				So. Windsor, CT

Hebeler			Tonawanda, NY

Gilkes

Control Center

MEPCO

Inlet Duct

Braden Steel			Tulsa, OK

C&W Fabricators		Gardner,MA

Donaldson			Baldwin, WI

J&G Steel			Sapupla, OK

CO2 Tank

Ansul Preferred

Chemetron			Swansboro, GA

PEECC (including Mark VI and EX2000),GLAC and GNAC

GE Breaker			Philadelphia, PA

Atkinson Industries

Koonst Wagner

Central Electric

PEMCO

Delta Unibus

GE Canada

PACS Industries		Mt. Vernon, OH

Calvert

Hatch

Brush

Electric Power Sys

Generator

GE

Elin

Hitachi

Toshiba

Brush

Water Wash Skid

Hebeler			Tonawanda, NY

MEF

Enpro

Manufacturas

Mitten				Syracuse, NY

Ogden

Midland

Jord

Hilliard			Elmira, NY

Braden

Accessory Base

GE

Avondale Shipyard

Gilkes

Kvaerner Processes

Oakwell Compressor

Harder Mechanic

Mittener

Hebeler			Tonawanda, NY

# EXHIBIT B-5 NOT USED

[Note:  Will this be needed, or can it be deleted?]

# EXHIBIT B-6 LIQUIDATED DAMAGES

B.6.1	Document Delivery Liquidated Damages (per Section 10.1):

1 through 30 days late - $500.00

31 through 90 days late - $1,000.00

91 + days late - $5,000.00

B.6.2	Delivery Liquidated Damages (per Section 10.3.1):

# Day Late			$/Day

1-7				$0

8 +				$22,500

B.6.3	Takeover Liquidated Damages (per Section 10.3.2):

Rate per Day

1 through 30: $60,000/day

31 +               $75,000/day

B.6.4	Output Liquidated Damages (per Section 10.9.1):

Rate per kW

Eight Hundred U.S. Dollars ($800)/kW

B.6.5	Heat Rate Liquidated Damages (per Section 10.9.2):

Rate per BTU/kWh (LHV)

Nineteen Thousand Five hundred U.S. Dollars ($19,500/BTU/kWh(LHV)

B.6.6  Exhaust Temperature Liquidated Damages (per Section 10.9.4):

Rate per oF per Unit

One Hundred Ninety Six Thousand Three Hundred Seventeen U.S. Dollars 			($196,317)

B.6.7 Exhaust Energy Liquidated Damages (per Section 10.9.5):

Rate per MMBtu/hr

One Hundred Forty Two Thousand Nine Hundred Eighty One U.S. Dollars 			($142,981)

# EXHIBIT C-1  SELLER PARENT GUARANTEE

# GUARANTEE

THIS GUARANTEE, dated the ______ of _________________, 200_, is from [Seller's Parent Company], a [           ] corporation ("XXX"), to Enron North America Corp. ("RECIPIENT").

WHEREAS, [Seller] is an affiliate of [Seller's Parent Company] ("XXXX"); and

WHEREAS, RECIPIENT and [Seller] are entering into the attached [----] Contract dated [------] herewith (the "Agreement"); and

WHEREAS, [Seller's Parent Company] has agreed to guarantee the performance of Seller under the Agreement in order to induce RECIPIENT to enter into the Agreement;

NOW THEREFORE, [Seller's Parent Company] hereby irrevocably and unconditionally guarantees to RECIPIENT the performance by [Seller] of all of its undertaking, covenants, indemnities and obligations under the Agreement to the extent and under the terms and conditions and subject to the limitations set forth in the Agreement.  [Seller's Parent Company] hereby consents that at any time and from time to time without notice to [Seller's Parent Company], the performance or observance by [Seller] of any term or covenant of the Agreement may be waived, the time of performance thereof extended, any provisions thereof amended and the rights of RECIPIENT hereunder assigned, without affecting the liability of [Seller's Parent Company] hereunder.  [Seller's Parent Company] may assert any and all defenses and limitations of liability possessed by [Seller], but excluding any defenses based upon invalid execution of the Agreement.

This guarantee shall be governed by, and construed, interpreted and enforced in accordance with the substantive law of the State of New York, excluding any conflict of laws or principles which would result in a choice of law for this Guarantee other than New York law.  Further, the parties stipulate that this Guarantee is deemed to have been made and entered into by them in the State of New York.

Guarantor shall waive any rights to subrogation/security and agrees to be bound by any findings of fact or final award or judgement made in an arbitration against Seller under the Agreement.

This Guarantee and any liability or obligation created hereunder shall expire upon the expiration of all liability and obligations of [Seller] under the Agreement.

IN WITNESS WHEREOF, [Seller's Parent Company] has caused this Guarantee to be executed as of the date first written above.

[SELLER'S PARENT COMPANY]

By:

Printed Name:

Title:

# EXHIBIT C-2 PURCHASER’S GUARANTEE

THIS GUARANTEE, dated the ____ of ____________, 200___, is from __________________, a ______________ corporation (“__________”), to a corporation under the laws of [---------] (“RECIPIENT”).

WHEREAS,__________________ is an affiliate of ________________________.; and

WHEREAS, RECIPIENT and __________________ entering into the attached Purchase Contract of even date herewith (the “Agreement”); and

WHEREAS,________ has agreed to guarantee the performance of ________________ under the Agreement in order to induce RECIPIENT to enter into the Agreement;

NOW THEREFORE, _______ hereby irrevocably and unconditionally guarantees to RECIPIENT the performance by _________________ of all of its undertaking, covenants, indemnities and obligations under the Agreement to the extent and under the terms and conditions and subject to the limitations set forth in the Agreement, provided that all of the obligations or RECIPIENT under the Agreement are met on a current basis. ______ hereby consents that at any time and from time to time term or covenant of the Agreement may be waived, the time of performance thereof extended, any provisions thereof amended and the rights of RECIPIENT hereunder assigned, without affecting the liability of _____ hereunder. _____  may assert any and all defenses and limitations of liability possessed by _______________, but excluding any defenses based upon invalid execution of the Agreement.

This guarantee shall be governed by, and construed, interpreted and enforced in accordance with the substantive law of the State of New York, excluding any conflict of laws or principles which would result in a choice of law for this Guarantee other than New York law.

This Guarantee and any liability or obligation created hereunder shall expire upon the expiration of all liability and obligations of_____________________  under the Agreement.

IN WITNESS WHEREOF, ______ has caused this Guarantee to be executed as of the date first written above.

___________________________________

By: ________________________________

Printed Name: ______________________

Title: ______________________________

# EXHIBIT D  SAMPLE LETTER OF CREDIT

Applicant:	[-------] (“Seller”)

Beneficiary:	Enron North America Corp. (“Beneficiary”)

Bank:		[------- ] (“Bank”)

Expiry Date:

Amount:	US ($--------)

I.	Funds under this irrevocable standby Letter of Credit are available to Beneficiary against presentation to us of Beneficiary's draft drawn at sight on _____________, marked thereon "Drawn under standby Letter of Credit number________, and accompanied by the following documents:

1.	Original Beneficiary's statement purportedly signed by an authorized officers of Beneficiary (as determined at Beneficiary's sole and absolute judgement) stating:  "Seller is in default of its obligation to perform in accordance with Section(s) [-------] of Contract No. [------------] (the “Agreement”), dated _________.  This statement is a demand for payment under irrevocable standby Letter of Credit number _______ notwithstanding any objection by Seller or any other person or entity whatsoever."

2.	A copy of the written notice to Seller sent pursuant to Article XXV of the Agreement (a copy of the conformation of receipt shall be attached thereto) , dated at least thirty (30) days prior to presentation of any claim under this irrevocable standby Letter of Credit evidencing that Beneficiary gave the requisite written notification to Seller stating therein that Seller was in breach of a specified obligation under the Agreement and that it is [beneficiary] intent to drawdown [specify amount] in the event General Electric Company fails to cure or commence to cure such default within thirty (30) days from the date of this notice.

II.	Special Conditions:

1.	Payment under this irrevocable standby Letter of Credit will be made to an account in beneficiary's name at such bank as beneficiary shall stipulate.  The amount or amounts demanded shall not exceed, in the aggregate, the amount of this Letter of Credit.

2.	Any payment made hereunder shall be made free and clear of and without deduction for, or on account of, any present or future taxes, levies, imposts, duties, charges, fees, commissions, deductions or withholdings of any nature whatsoever and by whomever imposed.

3.	Any reference to Contract/Bid item is for information purposes only and is not incorporated in nor made a part of this irrevocable standby Letter of Credit.

4.	Bank agrees and consents that this Contract may be modified, adjusted, amended, extended, suspended or shortened pursuant to Article XI of this Contract, and that  that this irrevocable standby Letter of Credit, subject to agreement of Beneficiary, Seller and Bank may be modified to comply with any such changed requirements of this Contract.

5.	Seller’s liability under this irrevocable standby Letter of Credit is limited to ([-------] United States Dollars [$-------]).  This irrevocable standby Letter of Credit shall expire at our counters [-------]     , 200[–].

6.	Demands may be made against this irrevocable standby Letter of Credit in one or more increments; however, the aggregate of such demands shall not exceed the amount set forth in Paragraph 5 of this irrevocable standby Letter of Credit.

We hereby engage with the beneficiary that draft(s) accompanied by documents drawn in strict compliance with the terms and conditions of this irrevocable standby Letter of Credit shall be duly honored by us if presented to us at our office located at _______________________on or before the expiration date.

This irrevocable standby Letter of Credit is subject to the uniform customs and practice for documentary credits (1993 revision), International Chamber of Commerce, Publication No. 500.  This irrevocable standby Letter of Credit shall be governed by, and construed in accordance with the laws of the State of New York.

# EXHIBIT E  COMMUNICATIONS

E.1	Commercial - Legal Notice Addresses:

If to Seller:

GE Power Systems
1 River Road Bldg. 36 - 3 East
Schenectady, New York 12345

Attn:

Phone:

Fax:

cc:

Phone:

Fax:

If to Purchaser:

Attention:

Phone:

Fax:

[Note: This will need to be revised on a case-by-case basis.  It might be helpful to incorporate this into the body of the Agreement.]

E.2	Technical Communications Notice Addresses.

If to Seller:

GE Power Systems

300 Garlington Road

Room 268

Greenville, South Carolina 29602

Attn:

Phone:

Fax:

cc:

Phone:

Fax:

If to Purchaser:

Attention:

Telephone:

Fax:

cc:

Phone:

Fax:

Attn:

[Note: This will need to be revised on a case-by-case basis.  It might be helpful to incorporate this into the body of the Agreement.]

# EXHIBIT F  PERFORMANCE TEST GUIDELINES

A.	TEST PHILOSOPHY

I.	General

The performance guarantees for the Unit include the Specific Performance Guarantees and/or Performance Guarantees of Electric Output, Heat Rate, Exhaust Gas Temperature, and Exhaust Gas Energy, in accordance with the Agreement.  The performance test procedure will include three one (1) hour input/output test runs for each Unit utilizing a combination of installed station instrumentation and special test instruments to (i) observe and record of the parameters required to demonstrate or calculate performance and (ii) enable correction of the demonstrated or calculated performance to Basis Conditions (a "Test Run").  All instruments used to measure parameters used to calculate the results of the Test shall meet the accuracy and calibration requirements of the Codes and Standards or as specified in this Exhibit F.

The Performance Test will be performed by the Purchaser.  The Seller will prepare a detailed Test Procedure, based on PTC 1-1999, PTC 22-1997, PTC 4.4-1981, PTC 19.1-1998 and appropriate related ASME Performance Test Codes and ASME Standards (the “Codes and Standards”), which will be submitted to Purchaser in accordance with Section 10.12.7.  Purchaser will perform calculations to determine Unit performance relative to Guaranteed Levels and Specific Performance Levels and will prepare test result certificates in the form as set forth in Exhibits G-1 and G-2 for submittal to Seller’s Representative.  Purchaser shall submit the details of the test calculations for Seller's review and verification.

Performance Tests should be conducted as soon as possible after commissioning of the Unit.

II.	Procedure

The gas turbine generator will be operated at Base Load as defined in the Agreement.  The Test Procedures will include a demonstration of power capability, heat rate, exhaust energy, and exhaust temperature.  The Unit's auxiliary equipment power consumption data will be measured to enable determination of net Electrical Output of the Unit.

The Performance Test Procedures will establish the methodology, based on the Codes and Standards, for calculating the Unit performance and for correcting the Unit's measured Electrical Output (net), Heat Rate (net), Exhaust Gas Energy and Exhaust Gas Temperature from existing Site conditions to Basis Conditions for the purpose of comparing the Adjusted Electrical Output, Adjusted Heat Rate, Adjusted Exhaust Gas Energy and Adjusted Exhaust Gas Temperature values against Guaranteed Levels and Specific Performance Levels, as applicable.  Unit specific correction curves needed to correct from Site conditions to Basis Conditions will be developed and included in the Performance Test Procedures.

It is the Seller’s responsibility to ensure that the Unit is operating on its control curve that defines Base Load at the time of the test.  There shall be no correction of Unit performance for deviations from the control curve.

In addition to the correction curves required for calculating the Test results, the following correction curves will be supplied by Seller along with the Test Procedure for information only; however, Purchaser shall rely on the final control curve listed in item 8 below for confirmation that the Unit is operating at Base Load during a Performance Test:

1.	Correction to ISO Conditions (59°F, 60% RH and at 14.7 psia):

Compressor Inlet Temperature vs. Power;

Compressor Inlet Temperature vs. Heat Rate;

Compressor Inlet Temperature vs. Fuel Flow;

Compressor Inlet Temperature vs. Exhaust Flow; and

Compressor Inlet Temperature vs. Exhaust Temperature.

2.	Ambient Pressure vs. Power.

3.	Performance Correction for Excess Inlet Loss for:

Power vs. Excess Inlet Loss; and

Heat Rate vs. Excess Inlet Loss.

4.	Performance Correction for Excess Exhaust losses for:

Power vs. Excess Exhaust Loss; and

Heat Rate vs. Excess Exhaust Loss.

5.	Performance Correction for Exhaust Temperature at Part Load with IGVs

consistent with dry low NOx operation at various inlet temperatures.

6.	Performance Correction for Fuel Flow at Part Load with IGVs consistent with dry 	low NOx operation at various inlet temperatures.

7.	Performance Correction for Fuel Analysis:

For gas fuel, fuel analysis corrections will be made to the corrected performance using the customer version of General Electric Cycle Deck. No correction curves will be provided.  The following correction factors will be calculated:

Exhaust Energy;

Electrical Output; and

Heat Rate.

8.	Gas Turbine Control Curve:

Exhaust Temperature vs. Compressor Pressure Ratio; and

Exhaust Temperature vs. Compressor Discharge Pressure.

9.	Performance Correction for Speed (Hz) for:

Power; and

Heat Rate.

10.	Generator Loss Curve.

11.	Generator Losses vs. MW or MVAR.

B.	STANDARD FIELD PERFORMANCE TESTING PROCEDURE

I.	Scope.

The Test Procedure may follow Seller’s standard guidelines, GEK-28106A, “Standard Field Performance Testing Procedure”, to the extent that it meets the requirements of this Exhibit F.

II.	Machine Condition

In accordance with Section 12.4.1 [Note:  Section does not exist] of the Agreement, Seller’s representative shall certify that the Unit is ready to test.

The Unit shall be tested when in new and clean condition subject to Section 10.12.4 of the Agreement.  The Seller’s representative shall determine, in its sole and reasonable discretion, based on the terms of this Agreement and the Test Procedures, whether the subject Equipment is in new and clean condition and ready to be tested.  For testing conducted after new and clean period as defined in Section 10.12.4.2 of the Agreement, Seller's degradation curves, as set forth in this Agreement, shall be utilized.  GE standard degradation curves for power, heat rate and exhaust energy will be shifted to cross the x axis at the number of operating hours specified in Section 10.12.4.2.

If the Seller’s representative, in its sole reasonable discretion, determines that the subject Equipment is not in new and clean condition prior to the conduct of the Performance Test, the Equipment shall be cleaned in accordance with Seller's recommendations set forth in Exhibit A-2, Attachment 2 (Seller reference GEK-107122A).

III.	PTC-22 Modifications and Clarifications

1.	A valid Test Run will consist of thirteen (13) sets of instrument readings taken at five (5) minute intervals over a sixty (60) minute time span after steady state conditions have been established as listed in PTC-22.

2.	Speed measurements are required and must be measured by an electronic tachometer or equal at the SPEEDTRONIC panel, and averaged for the Test Run.  Any corrections for frequency variation shall be applied to the calculation.

3.	Unit Electrical Output is to be measured by polyphase watthour meters (of revenue meter quality) at the generator terminals.  Revenue quality metering shall be provided by Purchaser.

4.	Gas Turbine exhaust temperature will be measured by control thermocouples mounted in the exhaust plenum with a maximum uncertainty of 5 °F.

5.	It is essential that the temperature indicating system be adjusted and calibrated in place with a known millivolt source prior to the test so that it reports reliable data.

6.	Barometric Pressure at the test site shall be measured with a mercury or aneroid barometer with an accuracy in accordance with PTC-22.  A minimum reading accuracy of 0.01 inches of Hg is required.

7.	Fuel Consumption:  Gas fuel is to be measured with a flat plate orifice or venturi installed in accordance with ASME MFC-3M or a turbine meter installed according to ASME MFC-4M standards.  Calculation of gas flow will be done in accordance with either ASME MFC-3M or MFC-4M as appropriate.  The upstream pressure will be measured with a precision test gage, the pressure drop with a gauge or transmitter, the gas temperature with a thermometer or thermocouple.

8.	Four (4) gas samples shall be taken from the fuel system during the test for laboratory analysis of composition according to ASTM D1945.

9.	The higher and lower heating values will be determined according to ASTM D 3588.

10.	Inlet air condition will be measured with at least four (4) RTD’s with an uncertainty meeting PTC 22.

11.	Turbine exhaust static pressure at or near the turbine exhaust flange or other convenient location must be measured using at least two (2) disc type static pressure probes.

12.	All instruments to be used in the performance test shall be calibrated immediately prior to the performance test and checked immediately after the performance test.  The Parties to the Test will witness the calibrations and inspections.

IV.	Evaluation

The Performance Test Procedure will include the tolerance due to measurement uncertainties associated with each particular test result in accordance with Section 10.12.10(c) of the Agreement.

The Parties will agree on a method of determining the sufficiency of the inlet chiller coils to provide the desired inlet air cooling if applicable.  The results of this determination will be included in the calculation of the Test results and in the Performance Test report.

# EXHIBIT F-1  SOUND LEVEL TEST GUIDELINES

PERFORMANCE TEST GUIDELINES FOR NEAR SOURCE SOUND LEVELS

∙	Testing methodology shall be based on the latest version of ANSI/ASME PTC 36.  The final result shall be the arithmetic average of the SPL’s measured around the equipment after background and other corrections have been applied.  The equipment shall be in compliance if the final result does not exceed the noise limit(s) specified above.

∙	Equipment shall be operated in a new and clean condition as intended by the designers when measurements are taken.  All access compartments, doors, panels and other temporary openings shall be fully closed; all silencing hardware shall be fully installed; all systems designed to be airtight shall be sealed.

∙	If the above guaranteed SPC exceeds the measured background noise by 10dB(a), no correction shall be necessary.  Otherwise, corrections to the measured SPL shall be made per ANSI/ASME PTC 36 procedures.  Background noise is defined as the noise measured with all Seller supplied equipment off and all other plant equipment on.

∙	Intermittent noises such as steam safety blow off valves and filter pulse noise are not included in the above guarantee.

∙	Measurements shall be taken 3 feet (1 meter) away from the outermost surfaces of equipment, including piping, conduit, framework, barriers, Equipment enclosures and personnel protection devices if provided.

∙	Measurements shall not be taken in any location where there is an airflow velocity greater than 5 feet per second (1.5 meters per second), including nearby air intakes or exhausts.

∙	Free field conditions must be prevalent at measurement locations.  Testing and corrections to a free field shall be per ANSI/ASME PTC 36.

∙	Testing shall be done according to a test plan agreed to by both the Purchaser and Seller.  Such a plan shall be submitted to both the Purchaser and Seller at least thirty (30) days prior to noise compliance testing.  The test results shall be submitted in the form of a test report that shall be made available to both the Purchaser and Seller.

Measurement responsibility shall be stated in the Contract.  Seller reserves the right to audit or parallel these measurements.

PERFORMANCE TEST GUIDELINES FOR FAR FIELD SOUND LEVELS (If Required)

∙	Testing methodology shall be based on the latest version of ANSI B133.8.  The final result shall be the arithmetic average of the SPL’s at the 8 measurement locations after background and other corrections have been applied.  The equipment shall be in compliance if the final result does not exceed the noise limit(s) specified above.

∙	Equipment shall be operated in a new and clean condition as intended by the designers when measurements are taken.  All access compartments, doors, panels and other temporary openings shall be fully closed; all silencing hardware shall be fully installed; all systems designed to be airtight shall be sealed.

∙	If the above guaranteed SPL exceeds the measured background noise by 10dB(A), no correction shall be necessary.  Otherwise, corrections to the measured SPL shall be made per ANSI B133.8 procedures.  Background noise is defined as the noise measured with all Seller supplied equipment off and all other plant equipment on.

∙	Intermittent noises such as steam safety blow of valves and filter pulse noised are not included in the above guarantee.

∙	Measurements shall be taken 5 feet +/- 2.5 feet (1.5  meters +/- .75 meters) above the ground.  Such measurement locations shall be on a flat elevation no more than 16 feet (5 meters) above or below the plant base elevation.

∙	Measurements shall not be taken in any location where there is an airflow velocity greater than 5 feet per second (1.5 meters per second), including nearby air intakes or exhausts.

∙	Measurement locations shall be chosen such that free field conditions exist at those locations.  Measurement locations shall not be closer than 12 feet (3.5 meters) to any nearby reflecting surfaces.

∙	Testing shall be done according to a test plan agreed to by both the Purchaser and Seller.  Such a plan shall be submitted to both the Purchaser and Seller at least thirty (30) days prior to noise compliance testing.  The test results shall be submitted in the form of a test report that shall be made available to both the Purchaser and Seller.

Measurement responsibility shall be Purchaser's.  Seller reserves the right to audit or parallel these measurements.

# EXHIBIT F-2 EMISSIONS TEST GUIDELINES

GE POWER SYSTEMS

U.S. Standard Field Testing Procedure for Emission Compliance (Reference GEK-28172E)

Test Philosophy

Testing to demonstrate emission guarantees and for adjustment of the NOx reduction system (if required) will be performed using procedures which are mutually agreed between Seller and the Purchaser.  Seller engineers and/or technical advisors may be present at the tests for procedural direction.  Test methods chosen are EPA methods which yield data on site immediately, wherever possible.

Emission Testing

A.	General

Emission testing identified herein shall be within Purchaser’s Scope of Supply using procedures which are mutually agreed.  Sampling for inlet pollutant concentrations may be required, at the sole discretion of Seller, in order to demonstrate compliance with emission guarantees.  Seller’s guarantees apply to the net increase of these pollutant emissions.

B.	Nitrogen Oxides Emissions

Before the official compliance testing is begun, the NOx reduction system will be adjusted to verify compliance with  NOx emission limits.  The gas turbine control system contains a pre-programmed schedule for either water or steam injection, this schedule may be adjusted to achieve an appropriate emission level approximately 5% to 10% below emission limits, and minimize the supply requirements.  Once the proper injection schedule has been established, this schedule is maintained throughout the testing, and it is programmed into the control system.

The NOx emission testing and related oxygen testing will be in accordance with U.S. EPA Method 20 presented in the Code of Federal Regulations.  Title 40, Part 60 (40CFR60 Appendix A and 40CFR60 Subpart GG -- Standards of Performance for Stationary Gas Turbines), with the following modifications, limitations and additions:

a.	The NOx instrument will be limited to a chemiluminescent type which meets 40CFR60 Appendix A, Method 7E.

b.	The span of the NOx analyzer will be set for appropriate spread of the expected 	 NOx readings, rather than the specified 300 ppm.

c.	Oxygen will be sampled simultaneously with all NOx readings since Subpart GG of 40CFR60 requires correction to 15% O2.  Method 3A from 40CFR60 Appendix A is used for the oxygen analysis.

d.	Section 60.33(c) (i) of Subpart GG has been replaced by U.S. EPA Memorandum dated June 2, 1997 for GE gas turbines using either water or steam for NOx reduction.  The EPA memorandum approves the GE injection control algorithm in lieu of the Subpart GG ISO correction equation.

e.	Section 60.335(c) (i) is not applicable to gas turbines with dry low NOx combustors.

C.	Carbon Monoxide Emissions (If Required)

Sampling is the same as for NOx normally with the same line feeding the different instruments.  Method 10 per 40CFR60 appendix A is used, but only the continuous sample method per Section 5.1 is acceptable to Seller.  A recorder is mandatory, not optional as per 5.3.9, with a span which gives an appropriate spread of the expected readings.

D.	Unburned Hydrocarbon Emissions (If Required)

Sampling and analysis must be on a wet basis to avoid condensing out the higher hydrocarbons.  Moisture determination by Method 4 (or Method 5) is necessary to convert results to dry basis.  Method 25A per 40CFR60 Appendix A is used for unburned hydrocarbons.  Results are presented as methane (CH4).  This method uses a flame ionization detector or analyzer.

E.	Particulate Matter Emissions (If Required)

Particulate matter emissions are determined by sampling, analysis and calculation in accordance with U.S. EPA Methods 5 and 5B with traversing per Methods 1 and 2 all from 40CFR60 Appendix A.  The following modifications and limitations on choices within the methods apply:

a.	Sampling probe internal surfaces must be made of chemically inert and non-catalytic material such as quartz.

b.	The filter material shall be quartz.

c.	Nozzle, probe and filter must be heated to 248 to 273 °F per Method 5, or at least 10 °F higher than the dew point of sulfuric acid in the exhaust duct.  Use of Method 5B requires nozzle, probe and filter to be heated to 320 to 345 °F.

d.	Probe wash shall be acetone per Method 5.

e.	Sampling technique shall provide a fairly large exhaust gas sample, with an objective of 100 SC.

F.	Volatile Organic Emissions

When volatile organic emissions (non-methane, non-ethane hydrocarbons) are required, Method 18 per Section 7.2 is used.  This requires a gas chromatograph at the Site.  Seller requires calibration of the measurement train at the sampling probe.

G.	PM10 Emissions (If Required)

PM10 emissions are determined by sampling, analysis and calculation in accordance with U.S. EPA methods 5 for front half filterable particulate matter and Method 202 for back half condensible particulate mater with traversing per methods 1 and 2, all from 40CFR60, Appendix A except for Method 202.  Method 202 is from 40CFR51, Appendix

M.  The following modifications and limitations within the methods apply:

1.	Sampling probe internal surfaces must be made of chemically inert and non-catalytic material such as quartz;

2.	The filter material shall be quartz;

3.	Nozzle, probe and filter must be heated to 248 °F to  273 °F per Method 5, or at least 10  °F higher than the dew point of sulfuric acid in the exhaust duct;

4.	Probe wash shall be acetone per Method 5;

5.	Sampling technique shall provide a fairly large exhaust gas sample, with an objective of 100 SCF;

6.	Impinger solution shall be extracted with ACS grade methylene chloride per method 202.  [Note:  Can we mark this Section H rather than M and delete the succeeding Section?]

H.	Not Used

I.	Not Used

J.	Not Used

K.	Certification of Calibration Gases

All gases used in certification of instruments or performance of emissions guarantee demonstrations shall be analyzed and certified in a manner and by a laboratory mutually agreeable to GE and Purchaser.  Examples of acceptable certification are:

1.	U.S. EPA Standard Methods

2.	U.S. EPA Protocols

3.	U.S. National Bureau of Standards Certification Procedures

L.	Exhaust Gas Flow Determination

Seller has established preferences for the determination of exhaust flow based on accuracy of the determination.  Seller prefers the following:

The primary exhaust flow determination shall be by the F - factor method per 40CFR60, appendix A, Method 19 (as specified in Method 20 for gas turbine emissions).  The F - factor constants from Table 19-1 shall be applied in all cases where possible per Paragraph 3.1.

Where available, the compressor inlet air flow signal shall also be used to compute exhaust flow.  Exhaust flow on a dry basis is the turbine inlet air flow minus the water vapor plus the fuel flow minus the water formed from the combustion of hydrogen in the fuel.  Gas turbine inlet air is measured using the compressor inlet air scroll as a flow element.  The inlet scroll is calibrated during the factory tests of the gas turbine.

Flow measurements by Velocity Traverse, per 40CFR60, Appendix A, Methods 1 and 2, can result in errors of 25% or more in this application, and is not acceptable.

M.	Not Used

# EXHIBIT G-1  PERFORMANCE TEST CERTIFICATE

PERFORMANCE TEST CERTIFICATE

The undersigned duly authorized representative of (Name of Purchaser's Company), under the provisions of the Purchase Contract between Enron North America Corp. and [--------------], dated (_______) the "Agreement" hereby certifies that:

1.	Performance Tests have been conducted pertaining to Electrical Output, Heat Rate, Sound Levels and Emissions of the gas turbine generator unit referred to in the Agreement (the "Unit").

2.	As set forth in the Agreement, Seller guaranteed that the Adjusted Electrical Output of the [turbine SNs] Unit will be at least [-----] kW when consuming natural gas for fuel, and that in any event Seller guaranteed that the Unit shall produce no less than [------] kW Adjusted Electrical Output when the Electrical Output is measured and adjusted in accordance with the Test Procedures and the Agreement.

The results of the Performance Tests show that the [turbine SNs] Unit produced an Adjusted Electrical Output of

.

[USE EITHER A OR B BELOW AS APPROPRIATE]

A.  The Adjusted Electrical Output above is greater than or equal to the Electrical Output Guarantee and therefore, Seller is not liable for Performance Liquidated Damages associated with Electrical Output.

B.  The Adjusted Electrical Output above is less than the Electrical Output Guarantee [               ], but greater than the aggregate Specific Performance Electrical Output Guarantee of [            ]; therefore, the undersigned has determined that the amount of Electrical Output Liquidated Damages to be assessed against the Seller for failure to meet Electrical Output Guarantee is U.S. $                         .

3.  As set forth in the Agreement, Seller guaranteed that the Adjusted Heat Rate of the [turbine SNs] Unit will be at least [-----] BTU/kWh(LHV) when consuming natural gas for fuel, and that in any event Seller guaranteed that the Unit shall demonstrate no less than [------] BTU/kWh(LHV) Adjusted Heat Rate when the Heat Rate is calculated and adjusted in accordance with the Test Procedures and the Agreement.  The results of the Performance Tests show that the [turbine SNs] Unit produced an Adjusted Heat Rate of        .

[USE EITHER A OR B BELOW AS APPROPRIATE]

A.  The Adjusted Heat Rate above is less than or equal to the Heat Rate Guarantee and therefore, Seller is not liable for Performance Liquidated Damages associated with Heat Rate.

B.  The Adjusted Heat Rate above is greater than the Heat Rate Guarantee [               ], but less than the Specific Performance Heat Rate Guarantee of [            ]; therefore, the undersigned has determined that the amount of Heat Rate Liquidated Damages to be assessed against the Seller for failure to meet the Heat Rate Guarantee is U.S. $                         .

EXHIBIT G-2  PERFORMANCE TEST COMPLETION CERTIFICATE

# PERFORMANCE TEST COMPLETION CERTIFICATE

The undersigned duly authorized representative of (Name of Purchaser’s Company), under the provisions of the Agreement hereby certifies that:

1.	Performance Tests pertaining to Electrical Output and Heat Rate on the combustion turbine generator units referred to in the Agreement have been conducted (each a “Unit” and collectively the “Units”).

2.	As set forth in the Agreement, Seller guaranteed that (i) the Adjusted Electrical Output of each of the Units will be at least [-----] kW when consuming natural gas for fuel, and that in any event Seller guaranteed that the Units shall produce no less than [------] kW Adjusted Electrical Output when the Electrical Output is measured and adjusted in accordance with the Test Procedures and the Agreement and (ii) if six (6) or more Units are installed at the Facility, the average Adjusted Electrical Output of all such Units will be at least [-----] kW.

The results of the Performance Tests show that the Units produced an average Adjusted Electrical Output of ________, and that each Unit individually produced the Adjusted Electric Output set forth below:

| Unit | Adjusted Electrical Output |
| --- | --- |
| Unit No_____ [turbine SN] | ________ kW |
| Unit No_____ [turbine SN] | ________ kW |
| Unit No_____ [turbine SN] | ________ kW |

# [USE A, B, and C BELOW AS APPROPRIATE]

A.	The Adjusted Electrical Output of the Units as set forth above, individually and, if applicable, collectively on average, are greater than or equal to the Electrical Output Guarantee and, if applicable, the Optional Electric Output Guarantee, and therefore, Seller is not liable for Performance Liquidated Damages associated with Electrical Output.

B.	The Adjusted Electrical Output of [turbine SNs] Units set forth above is/are less than the Electrical Output Guarantee of [___________], but greater than the Specific Performance Electrical Output Guarantee of [____________]; therefore, the undersigned has determined that the amount of Unit Output Liquidated Damages to be assessed against the Seller for failure to meet the Electrical Output Guarantee is U.S. $_____________.

C.	The average of the Adjusted Electrical Output of the Units is less than the Optional Electrical Output Guarantee of [             ]; therefore, the undersigned has determined that the amount of Optional Output Liquidated Damages to be assessed against the Seller for failure to meet the Optional Electrical Output Guarantee is US $              .

3.	As set forth in the Agreement, Seller guaranteed that the Adjusted Heat Rate of the [turbine SNs] Units will be at least [-----] BTU/kWh(LHV) when consuming natural gas for fuel, and that in any event Seller guaranteed that the Units shall demonstrate no less than a [------] BTU/kWh(LHV) Adjusted Heat Rate when the Heat Rate is calculated and adjusted in accordance with the Test Procedures and the Agreement.  The results of the Performance Tests show that each of the [turbine SNs] Units produced the Adjusted Heat Rate set forth below:

| Unit | Adjusted Heat Rate |
| --- | --- |
| Unit No_____ [turbine SN] | ________ BTU/kWh (LHV) |
| Unit No_____ [turbine SN] | ________ BTU/kWh (LHV) |
| Unit No_____ [turbine SN] | ________ BTU/kWh (LHV) |

# [USE EITHER A OR B BELOW AS APPROPRIATE]

A.	The Adjusted Heat Rate of each of the Units as set forth above is less than or equal to the Heat Rate Guarantee and therefore, Seller is not liable for Performance Liquidated Damages associated with Heat Rate.

B.	The Adjusted Heat Rate of [turbine SNs] Units set forth above is greater than the Heat Rate Guarantee [-------------], but less than the Specific Performance Heat Rate Guarantee of [-------------]; therefore, the undersigned has determined that the amount of Heat Rate Liquidated Damages to be assessed against the Seller for failure to meet the Heat Rate Guarantee is U.S. $[----------------].

# EXHIBIT H-1  TECHNICAL DIRECTION OF INSTALLATION

1.0	General.  The parties agree that as part of this Scope of Work Seller shall provide the requisite TDI support at the Site required for installation, start-up and correction of problems related to waived shop testing and commissioning of the Equipment.

2.0	Schedule.  Seller and Purchaser's Representative shall coordinate the start and finish schedules of each of the TDI personnel.  Seller shall provide a maximum of 162 manweeks (straight time 40 hrs/week TDI advisors as required to support Purchaser’s receipt of Equipment, installation, startup, commissioning and correction of problems related to waived shop testing until certified ready for testing in accordance with the Agreement. Seller shall provide a bar chart for its manpower staffing in support of the construction schedule, which shall be adjusted from time to time by Seller and Purchaser as the work progresses.  Hours worked by Seller’s TDI personnel in excess of forty (40) hours straight time hours each week shall be deducted from the 162 manweek count, at the equivalent rate of one and one half straight time hours pursuant to Section 8 below.  Seller’s forty (40) hour work week is 8 hours per day, Monday through Friday

3.0	Cost.  Seller shall bear each and every expense for services provided by its TDI personnel including, but not limited to, international and local transportation, salary, lodging, per diem, taxes, work permits and expenses which costs are included within the Purchase Amount.  Any TDI activities associated with field testing and correction of the Unit which would normally be performed in the factory is included in Seller’s Scope of Work and is not counted against the 162 manweek count.

4.0	Supervision of Craft Labor.  Seller's TDI personnel shall not be responsible for the productivity or quality of work performed by Purchaser’s contractors and shall not have direct supervision responsibility over craft labor.

5.0	Seller Technical Direction Office Facilities.  Purchaser shall provide:

(a)	A secure, furnished private jobsite office facility of sufficient size (near the Equipment) that can accommodate 3 to 4 field engineers per unit, where drawings, special tools, and other Seller proprietary materials and equipment can be kept and referred to or worked upon.

(b)	Purchaser shall coordinate installation of four (4) direct phone lines to Seller’s jobsite office facility and Seller shall be responsible for payment of the monthly local and long distance service and usage charges to the telephone company.

(c)	Seller’s jobsite office facility shall have HVAC and contain furnishing equivalent to that in use by Purchaser and its other subcontractor’s suitable for supporting Seller’s work.  The facility shall have adequate lighting, electrically outlets and sanitary facilities shall be accessible.  Seller shall be required to comply with the Site security and safety requirements at all times including control, use and parking restrictions relevant to Seller’s personnel’s privately owned vehicles.

6.0	Staffing Levels.

Seller shall provide Biographical data and other qualifications as requested by Purchaser's project manager for review and approval of Seller's lead advisor (such approval not to be unreasonably withheld).

Staffing shall include:

(a)	A lead technical advisor commencing no later than delivery of the Unit to the Delivery Point, and such person shall be an experienced GE turbine generator installation engineer who shall be capable of providing guidance and counsel for the following:

-	The effective guidance and counseling of the other Seller technical advisors to provide for broader utilization of their skills.

-	The integration of the assigned service work with the Purchaser representatives to assist in meeting scheduled startup, completion and operation dates.

-	The reporting of pertinent facts on failure of equipment warranted by Seller and its Vendors to the proper personnel to permit prompt and equitable settlement of warranty claims.

-	The submittal of timely reports on job progress and resolution of problems.

-	The planning, organization and direction of the other Seller personnel for the installation, startup, testing and warranty implementation of the supplied equipment.

-	The maintenance of installation records and job log book.

(b)	Turbine Generator Installation team comprised of technical advisors skilled in mechanical erection of gas turbines and related equipment, electrical equipment installation and testing, SPEEDTRONIC Control System checkout, calibration and unit startup, and shall be capable of providing guidance and counsel for the following:

-	The inspection and unloading of the major components at the installation site and their placement on the foundations.

-	The setting of necessary shims between sole plates and the turbines.

-	The removal of shipping supports on the turbine and generator packages.

-	The installation of the turbine unit to the proper center line and elevation.

-	The alignment of the accessory equipment and generators to the turbines.

-	The installation and checkout of conduit, piping, control wiring and instrumentation between the turbines and Seller supplied auxiliary equipment and generators.

-	Checkout and initial operation of the turbine starting equipment.

-	The sequencing and checkout of the turbine SPEEDTRONIC Control Panels.

-	The installation and checkout of the generator excitation/electric systems.

-	The startup of the turbine unit with the Purchaser’s operating personnel.

-	Mark up two (2) sets of drawings to reflect the “as-built” condition of the equipment.  One (1) set for site records and one (1) set to be returned to GE Customer Service.

-	Installation and check out of all auxiliary and ancillary equipment provided under this Agreement.

-	Electrical checkout and powering of the control consoles and process unit.

-	Review main communication links between all control systems to assure proper system integrity.  Insure data highway links to all systems are operating properly.

-	Review of control system logic and main central control system graphics to assure proper integrity between all systems.  Make any modifications needed for proper plant control.

7.0	Additional Services

In addition to providing the expertise outlined above, Seller's personnel shall be relied upon to answer questions and provide or obtain interpretation of manufacturer supplied instructions and drawings during the execution of work (construction, erection, commissioning, etc.).  Included in this category of support are:

(a)	Confirmation that specifications and instructions to be applied during construction, erection and commissioning by the different Vendors are met and that the specified results of tests and examinations are obtained;

(b)	Corrections of construction/erection/commissioning software, if necessary, as far as design and engineering tasks are not concerned;

(c)	Confirmation that the necessary standard of quality has been sustained in all areas which could affect facts and information provided by Seller to Purchaser;

(d)	Immediate written objections to Purchaser's representative if the standard of quality is jeopardized, and advise Purchaser's representative in a timely manner on the implications where any work procedure may impair the Equipment warranty;

(e)	Troubleshooting, technical guidance and expertise during instrumentation and control systems loop and function checks;

(f)	Technical expertise for energization and synchronization activities performed during commissioning; and

(g)	Provide impromptu training to Facility operators during start up and commissioning.

8.0	Expected Work Week.  Purchaser anticipates that the normal work week on Site will consist of working six (6) days per week (Monday through Saturday) for ten (10) hours per shift each work day;  however, such work hours and days shall be adjusted to accommodate Purchaser's general Site Seller's work schedule.  It is the intent of the parties that Purchaser shall have the flexibility to require Seller's personnel to work more or less hours per day than the standard work day in support of certain construction activities.  All time worked, except for those hours worked in support of the waived shop tests, shall be subtracted from the total of Seller’s obligation set forth in Section 1.0 above.  Total TDI hours worked in excess of the 162 manweeks, subject to Sections 2 and 3 above, shall be reimbursed to Seller pursuant to a Change Order, at the following rates:

Straight time (8hrs/day) = $230.00/hour

Overtime (excess of 8 hrs/day Sundays and Holidays) = $345.00/hour

Additional mandays purchased will be subject to:

-	Required travel will be reimbursed at cost or in accordance with IRS mileage rates;

-	Travel time will be invoiced at the applicable straight time or overtime rate; and

-	Per diem will be applicable at the rate of $196.00 during all days commencing on departure from point of origin through return or its equivalent.

9.0	Replacement of Unsatisfactory Personnel.  If any of Seller's personnel provided under this Agreement fail, in Purchaser's reasonable judgement, to fulfill his duties as assigned by Seller, Seller shall cause such personnel to properly perform such duties, or at the request of Purchaser replace the personnel. In the event of a replacement:

-	The replacement must be of equivalent qualifications to the person being replaced;

-	Seller shall provide Purchaser a resume of the recommended replacement;

-	The replacement must be approved by Purchaser, prior to the replacement's commencement of work, such approval, not to be unreasonably withheld; and

-	Seller shall bear all additional travel, living or other costs associated with removing the unsatisfactory individual and furnishing the replacement.

10.0	Supplemental Seller Personnel.  Seller's personnel shall be direct employees of Seller, or Seller may elect to hire supplemental third party Sellers screened and trained by Seller.  In addition to any such screening and training, such personnel must have verifiable and demonstrable prior hands-on experience in installation or training as applicable to the work to be performed by such person. Seller shall provide Purchaser's Representative resumes of all individuals selected by Seller as supplemental personnel pursuant to this Paragraph 9, and obtain Purchaser's Representative's prior approval of each individual's assignment, such approval not to be unreasonably withheld.

11.0	Change of Seller's Personnel.  Seller and Purchaser recognize that changing of personnel during the performance of the Scope of Work can be disruptive and adversely affect the timely and proper performance of the Scope of Work; however, both Seller and Purchaser realize that under certain circumstances, Seller may, on an exception basis, need to substitute personnel in the course of performance of the Scope of Work.  Seller may, on an exception basis, substitute personnel; provided that the following shall apply:

-	The replacement must be of equivalent capabilities to the person being replaced;

-	Seller shall provide Purchaser a resume of the recommended replacement;

-	Such change is for a compelling personal reason, or by mutual agreement the existing individual does not have the required skill;

-	The replacement must be approved by Purchaser prior to the replacement's commencement of work, such approval not to be unreasonably withheld, and,

-	Seller shall bear all additional travel, living or other costs associated with such change.

12.0	Debugging.  Seller shall provide with respect to TDI, normal debugging of problems encountered during installation, start-up and commissioning of the equipment.  In the event debugging reveals a factory defect, Seller shall provide Purchaser written observations regarding such defect.

13.0	Release of Seller’s Personnel.  If Technical Direction of Installation Representative is/are released from site by Purchaser while the installation is in progress, the same Technical Direction of Installation Representative may not be available to return but will be replaced with a qualified Technical Direction of Installation Representative within two weeks after Company’s receipt of written request from the Purchaser for Technical Direction of Installation Representative.

14.0	Purchaser’s Responsibilities.  Purchaser will take all necessary precautions, at all times, for the safety of Company personnel at site.  This includes, but is not limited to, indoctrination of Purchaser’s safety practices, energization/de-energization of all power systems (electrical, mechanical and hydraulic) using a lock-out tag procedure, and conducting periodic safety meetings during construction and start-up.

# EXHIBIT H-2  TRAINING

1.	Basic Familiarization Training.  Included in the Scope of Work, Seller will perform on the job training of Purchaser's operator personnel utilizing its technical advisor staff throughout the performance of TD of I and separate from TD of I, Seller shall provide formal classroom familiarization training (5 days)  “Gas Turbine Familiarization Course”with a course content is as follows:

Objective

To familiarize operators and supervisory personnel to safely and properly operate a gas turbine-generator unit.

Emphasis is placed on the operator’s responsibilities with regard to the auxiliary systems, operational data taking, and data evaluation.  Operators are also instructed in how to interpret fault annunciation and how to determine if the annunciated fault can be remedied by operator action or by the assistance of instrumentation and/or maintenance personnel.

The course focuses on starting, loading, and specific operator checks of the various turbine support and auxiliary systems to ensure safe and reliable operation of the turbine unit, including the operation of the Gas Turbine SPEEDTRONIC TM Mark V Controls and the EX2000 Excitation.  In that Owner's staff is familiar with the operating of comparable turbines but not with the Gas Turbine SPEEDTRONIC TM Mark V Controls and the EX2000 Excitation system, the familiarization course will provide greater focus on such systems and less on the basic operating procedures.

Content

The typical Gas Turbine Familiarization course covers the following areas:

∙	Unit Arrangement

--	Gas Turbine, Generator

∙	General Description

--	Gas Turbine and Generator Major Components

∙	Support Systems

--	Lube Oil

--	Hydraulic and Control

--	Cooling Water

--	Cooling and Sealing Air

--	Fuel(s)

--	Starting

--	Heating and Ventilation

--	Fire Protection

--	Generator Systems

∙	Control System

--	Control Panel Arrangement

--	Basic Control Functions and Operating Sequences

Students will be provided limited handout material extracted from Seller’s Instruction Manual.

2.	 Additional Optional Training Courses.  The optional training listed in Exhibit N-2, which is designed to be performed by Seller at the Site consists of the following:

a.	GTG operation (2 weeks duration)

b.	GTG maintenance (1 week duration)

c.	GTG Mark V (2 weeks duration)

d.	EX2000 Excitation (1 week duration)

3.	Lesson Outlines of Optional Training.  The lesson outlines of the above listed training are as follows:

Summary

A comprehensive training program is conducted for a selected number of Purchaser’s engineers, operations and maintenance personnel.  The training will be conducted at Purchaser’s job site.

The Purchaser’s personnel assigned for training must have prior general knowledge of power plant systems operation.

A Seller training coordinator is designated for the project who is familiar with overall plant design and system operations.  This person schedules and coordinates job site training, as well as integrates individual systems training into the overall plant operation.

The training programs will cover the areas specified below and detailed in this Exhibit H-2:

Training Material and Related Conditions (On-Site Training)

∙	Classes run daily (five days/week) and are limited to six (6) hours.  The actual class time, a.m. and p.m. hours, is dictated by the availability of the equipment and the students per the normal work schedule.  Each class time period should be agreed to by Purchaser’s management and Seller’s instructor(s) at the beginning of the program.  The six (6) hour class limitation will allow ample time for the instructor(s) to prepare the next session’s work plan.

∙	A maximum of twelve (12) students per class can be accommodated.

∙	English-speaking instructor(s) will be furnished for the course duration.

∙	Each student will be furnished a suitable bound course instruction and reference handbook in English; shipment costs have been included in the firm price quotes herein.  Any materials furnished are exclusively for the use of the Purchaser’s personnel.  This material is not for resale or to be distributed to third parties, nor is it to be copied or reproduced without Seller’s prior written permission.

∙	Any audio or video recording of Seller’s lecture material is prohibited unless Seller grants permission in writing in advance of the training program.

∙	The instructor(s) will retain all visual aids such as 35mm slides and transparencies used to conduct the course.

∙	The power plant equipment should preferably be operable and available to support this course of study.

∙	Seller shall be responsible for the instructors’ travel and living expenses.

∙	Purchaser will provide class room, audio visual equipment and computers as requested in advance.

Training Schedule

After engineering design has been finalized, training is conducted during a mutually-agreeable time.

Typical Course contents for the Major Plant Components

a.	Gas Turbine-Generator Operations

The objective of this course is to train operators and supervisory personnel to safely and properly operate gas turbine-generator unit.  This course develops a background in gas turbine-generator operation which enables participants to properly analyze operating problems and take the necessary corrective action.

Emphasis is placed on the operator’s responsibilities with regard to auxiliary systems, operations data acquisition and data evaluation.  Operators are also instructed to interpret fault annunciation and determine if the annunciated fault can be remedied by operator action or by the assistance of instrumentation and/or maintenance personnel.

The course focuses on starting, loading and specific operator checks of the various turbine-generator support and auxiliary systems to ensure safe and reliable operation of the turbine-generator unit.

The typical Gas Turbine-Generator operations course covers the following areas:

∙	Gas Turbine-Generator Fundamentals

--	Basic theory of operation

--	Base and machine arrangement

∙	Support Systems Operation

--	Lube oil

--	Hydraulic and control oil

--	Cooling water

--	Fuel system(s)

--	Starting means

--	Heating and ventilation

--	Fire protection

--	Generator systems

∙	Control System

--	Arrangements

--	Control functions and operating sequences

--	Protection functions

∙	Operator Responsibilities

--	Data acquisition and evaluation

--	Operating limits

--	Required operator action on various annunciator indications

∙	Unit Operation

-- 	Startup

--	Normal operation

--	Shutdown

--	Emergency procedures

b.	Gas Turbine-Generator Systems Maintenance

This site specific course is designed to introduce operations and maintenance personnel to the routine preventative maintenance procedure of the turbine-generator support systems required to attain high levels of availability and reliability from the gas turbine-generator.  This course does not cover the turbine-generator disassembly inspections required for major mechanical maintenance.  Operating and maintenance personnel should attend this course together to develop a working relationship regarding the routine maintenance requirements of the unit.

The training will include detailed descriptions of the turbine-generator support systems.  This will include a functional description of the system as well as the routine maintenance requirements of the system.  If the course is held at the customer’s location it will include site visits to familiarize personnel with the location of the various system components and to allow personnel to correlate the system piping schematics to the system hardware.  The training will not incorporate any “hands-on” training or component disassembly.

The typical Gas Turbine-Generator Systems Maintenance course covers the following topics:

∙	Gas Turbine Introduction

--	Explanation of how a gas turbine works

--	Introduction to the customer-specific unit

∙	Gas Turbine-Generator Arrangements

--	Site turbine and accessory base arrangements and enclosures

--	Site generator arrangements and enclosures

∙	Support Systems Operator and Routine Maintenance

--	Inlet and Exhaust Systems including Generator Cooling Air and Inlet Bleed Heat

--	Lube Oil System

--	Hydraulic Oil System

--	Trip Oil System

--	Inlet Guide Vanes

--	Cooling Water System

--	Cooling and Sealing Air System

--	Fuel System

--	Starting System, including slow-roll/cooldown function

--	Heating and Ventilation Systems

--	Fire Protection System

--	Generator Auxiliary Systems (Brush Rigging, Coolers, High Voltage Bushings)

--	Water Wash System as a maintenance tool

c.	Gas Turbine SPEEDTRONIC™ Mark V Technicians Training

This site specific course is designed to enable engineers and competent instruments and control technicians to confidently calibrate the controls and diagnose problems in General Electric Gas Turbine SPEEDTRONIC™ control.

The typical Gas Turbine SPEEDTRONIC™ Mark V Controls course covers the following areas:

∙	Gas Turbine Control Fundamentals

--	Gas turbine principles of operation

--	Governing system requirements

∙	Gas Turbine Systems

--	Piping schematics

--	Electrical wiring diagrams

∙	Gas Turbine Control

--	Startup/speed/temperature/other controls

--	Protection

∙	Control Displays

--	User’s manual

∙	Control System Software

--	IDOS

--	File descriptions

∙	Micro Processor Initialization

--	Troubleshooting

∙	Valve Calibration (LVDT)

--	Input/output configuration screens

∙	Software Tools

--	Modifying and downloading control configuration

--	Data acquisition on Mark V interface

--	Software backup

∙	Troubleshooting

--	Gas turbine process alarms

--	Mark V panel diagnostic alarms

Course Duration:   2 weeks

The course duration will vary depending upon the student’s background and their familiarity with gas turbine controls and computer based control systems.

d.	Excitation for AC Generators

The objective of this course is to improve the ability of personnel to operate, maintain and test rotating and/or static excitation systems for medium and large AC generators.

The course focuses on the testing, maintenance, adjustment and operation of the excitation system in use.  Operational safety precautions are details for both personnel and equipment during troubleshooting and maintenance activities.

The typical Excitation for AC Generators course covers the following areas:

∙	Generator Fundamentals

--	AC generator theory

--	Exciter theory

--	AC generator operation curves

∙	System Components

--	Exciters

--	Regulators

∙	System Operation

--	Regulator

--	Off-line

--	On-lin

--	Parallel

--	Protection systems

∙	Maintenance and Troubleshooting

--	Test instruments

--	Print reading

# EXHIBIT I  CANCELLATION CHARGE

In the event Purchaser cancels this Agreement, Purchaser's liability for cancellation charges shall not exceed the values set forth below for cancellation of the Unit:

| Cancellation Month | % of Purchase Amount |
| --- | --- |
| ________ 200_ | 14% |
| ________ 200_ | 15% |
| ________ 200_ | 20% |
| ________ 200_ | 25% |
| ________ 200_ | 30% |
| ________ 200_ | 34% |
| ________ 200_ | 34% |
| ________ 200_ | 34% |
| ________ 200_ | 34% |
| ________ 200_ | 34% |
| ________ 200_ | 34% |
| ________ 200_ | 98.5% |
| ________ 200_ | 100% |

Notes:

1.	Seller shall maintain title to the Unit when cancellation occurs prior to shipment.
2.	Cancellation exposure is 100% of the value of the Unit after title has transferred.

3.	The value of the Unit shall increase or decrease as applicable as a result of increases or 	decreases to the Purchase Amount due to executed Change Orders.

[Note:  The table will need to be revised on a case-by-case basis]

# EXHIBIT I-1 MILESTONE PAYMENT SCHEDULE

| Milestone Month (Not earlier than) | Milestone Event (Not earlier than) | Monthly % of Purchase Amount | Cumulative % of Purchase Amount |
| --- | --- | --- | --- |

[Note:  To be provided on a case-by-case basis]

# EXHIBIT J  QUALITY

1.0   QUALITY ASSURANCE AND CONTROL

1.1	Quality Assurance Arrangements

Seller, and its nominated Vendors shall work to defined quality assurance arrangements compliant with ISO 9001.  Seller shall indicate the results of any recent audits.

In addition to requirements detailed in ISO 9001, Seller shall:

■	Ensure that all quality related activities are planned and that adequate resources are made available for these activities.

■	Establish means by which all materials and components are identified through each stage of performance of the Scope of Work.  These measures will facilitate the traceability of materials as identified in the agreed Quality plans.

■	Arrange for the protection of the quality of the product to include delivery to the specified destination.

1.2	Vendors

Seller shall specify all Quality Assurance requirements to its Vendor and shall ensure that all Vendors comply with these requirements.

Seller shall undertake in respect of its nominated Vendors, where no such acceptable information is available or where the Vendor has not been subject to a quality audit within the previous 12 months, to carry out an audit of that Vendor in order to ensure that completion of works will be compliant with contract requirements.

Seller and its nominated Vendors maybe subject to a quality audit by Purchaser.

1.3	Quality Plans

Quality Plans shall be prepared by Seller for all areas of activity.  These quality plans shall be submitted to Purchaser for review.

The format of the Quality Plans shall be agreed with Purchaser.  Seller shall ensure that all activity is carried out in accordance with the Quality Plans and will notify Purchaser of any deviations as they occur.

1.4	Review of Documents

Seller shall submit for review all Quality Plans and Design Documentation as may reasonably be required by Purchaser.  A schedule of drawings and documentation shall be maintained by Seller to show the current status and revision of each document.

1.5	Records

Seller shall maintain records as required by the quality plans.  All records including audit reports shall be made available for inspection by Purchaser, as required.

Seller shall generate records in a manner coincidental with the activities to which they refer, such that the quality status of each item can be readily verified.

All records shall be concisely compiled and coded.  They shall, in addition be clearly cross referenced to the parts or assemblies to which they refer.

Records shall in general, be available at the time of equipment delivery.  Such records shall include relevant certifications and build documentation together with any information which would facilitate the general traceability of component items or materials.

All records generated during the course of performance of the Scope of Work shall be retained by Seller for a minimum period of ten years from the date of Acceptance or supplied to Purchaser for its retention.

1.6	Seller's Responsibility

Review and comment by Purchaser of the quality assurance procedures, quality plans, inspection and test arrangements operated by either Seller or his Vendors, will not relieve Seller of its obligation to provide Equipment which complies with the requirements of the Agreement.

2.0	QUALITY SURVEILLANCE

2.1	Quality Surveillance Requirements

Seller shall define the items which it proposes to Vendor together with all items for which quality plans (inspection and test plans) will be submitted.  Seller shall provide Purchaser's Quality Assurance Manager the name of his representative authorized as having responsibility for resolving or obtaining resolution, of any problems arising in respect of the acceptability of raw materials, components, and assemblies.

Seller shall establish and maintain a documented inspection system capable of producing objective evidence that all material manufactured parts and assemblies comply with the quality requirements of the Contract.

General information on the type of system in use by Seller shall be provided.

Seller's inspection system shall include procedures used for controlling the following functions:

■	Availability at inspection points of applicable drawings, instructions, etc and prompt removal of obsolete documents.

■	Maintenance and calibration of suitable inspection and test equipment, which should comply with requirements set out in ISO 9001

■	Inclusion (or referencing) on purchase orders of the necessary technical inspection and test details to meet the specified requirements and of Purchaser's possible involvement at the Vendor's facilities.

■	Incoming, in process and final inspection and inspection of packing and marking.

■	Means of identifying inspection status throughout manufacture.

■	Provisions of complete inspection and test records.

Seller shall submit for review within 30 days after the execution of this Agreement, a quality plan, excluding testing and inspection on work already completed as of such submission date, in which case test records will be provided, (inspection and test plan) defining the program of quality control and inspection activities which it or its Vendors will perform in order to ensure that the manufacture and completion of the plant complies with the specified requirements.  The quality plan may be of any form to suit Seller's system, but it shall as a minimum:

■	Indicate each inspection and test point and its relative location in the production cycle including incoming, packing and site inspections.

■	Indicate mandatory Seller Factory hold points for an item or process before the work can proceed.

Seller shall include in all its orders to Vendors, a note advising that all materials and equipment are subject to inspection by Purchaser.

In order to verify compliance with engineering, procurement, manufacturing requirements and program, Purchaser shall have access at all times as arranged by Seller, to all places where materials or equipment are being prepared or manufactured, including the works of Vendor's raw materials.

Inspection of the Equipment may be by Purchaser and may include the following activities:

■	Evaluation of Seller's system and Quality Plans.

■	Periodic monitoring to confirm the effectiveness of and Seller's compliance with the established system procedures, quality plan and inspection and test instructions.

■	Witnessing of inspections and test and/or verification of inspection records including:

a.	Compliance of raw material with specified requirements.

b.	Compliance of manufactured parts, assemblies and final items with specifications, drawings, standards and good engineering practice.

c.	Periodic inspection of Seller's design manufacturing, installation work and the production of progress reports.

d.	Witnessing of inspections and tests.

e.	Packing for shipment including check for completeness of shipment, handling requirements, and identification.

Seller's compliance with equipment documentation, drawing, delivery and commissioning schedules shall be monitored by Purchaser.

Raw materials, components, shop assemblies and the installation thereof, shall be subject to inspection and test by Purchaser as required by the specification and the extent practicable at all times and places during the period of manufacture.

Seller shall keep Purchaser informed, in advance, of the time of starting and of the progress of the Scope of Work in its various stages so that arrangements can be made for inspection and for test.  He shall also provide without additional charge, all reasonable facilities and assistance for the safety and convenience of Purchaser in the performance of his duties.  All of the required tests shall be made to Seller's expense, including the cost of all samples used.

In the event of the unreasonable postponement, by Seller, of tests previously scheduled, or of the necessity tests due to unsatisfactory results of the original tests, or other reasons attributable to Seller, Seller will bear the costs incurred by Purchaser of his nominated representative in re-inspecting the non-conforming item or its replacement.

Seller's and nominated Vendor's quality assurance program shall identify and shall isolate items not conforming to the technical specification.  All such items shall be reported to Purchaser via a non-conformance report which shall identify:

■	The identification of the item.

■	The relevant specification, drawing etc including revision number.

■	A sketch of the non-conformance.

■	The method by which the non-conformance was identified.

■	The cause of the non-conformance.

■	The proposal for resolution the con-conformance.

■	A concession application including the technical justification and the appropriate supporting documents if applicable.

■	The proposed action to prevent re-occurrence.

Seller shall not offer, unless otherwise agreed, any item of equipment for inspection to Purchaser until all planned inspections and tests to date have been completed to the satisfaction of Seller.

Any non-conformances identified by Purchaser may be notified by issue of Purchasers Non-conformance Report to Seller.  Notification of re-inspection shall not be made until the completed non-conformance report together with any applicable concession application have been submitted to Purchaser.

The inspection and tests by Purchaser of any components or lots thereof does not relieve Seller of any responsibility whatever regarding defects or other failures which maybe found before the end of the Primary Warranty Period.

Seller shall provide a quality release certificate confirming compliance with the contract requirements and a data book containing relevant manufacturing and quality records.

Seller shall furnish Purchaser with 4 copies of the data book.

The parties agree that, in light of the fast-track nature of the project for which this Unit is being supplied, and the advanced stage of manufacturing, Purchaser and Seller shall review the requirements, obligations and responsibilities set forth in this Exhibit J during two pre-inspection/quality meetings (one for the gas turbine, one for the generator). Seller shall coordinate and schedule a mutually agreed date for both meetings at Seller’s factory, with the goal of having them within two months after the design finalization meeting.  Seller shall document all mutually agreed adjustments to Exhibit J, issue the notes in letter form for review and agreement, and issue a final conformed letter  for subsequent endorsement by the parties and use as quality assurance guidelines.

# EXHIBIT K  PROJECT PLANNING

1  PURPOSE AND OBJECTIVES

1.1	Seller shall provide information and data required for development of a Project Schedule for the Work in accordance with the requirements of this Exhibit.  Seller’s information and data shall be provided electronically in a software which can be readily used in Purchaser’s “Primavera Project Planner” software which will be used by Purchaser to develop the Project Schedule.  The purpose of the Project Schedule shall be to:

(1)	assure adequate planning, scheduling and reporting during the prosecution and progress of the work by Seller in order to complete the work in accordance with any and all milestones;

(2)	assure coordination of the efforts of Seller, his various Vendors and Purchaser furnished equipment and materials, if any;

(3)	assist Seller, and Purchaser, in monitoring the progress of the work and in evaluating proposed changes to the Contract and the Project Schedule.

2  PROGRESS UPDATES

2.1	 The Project Schedule shall be updated on a monthly basis and on a periodic basis throughout the duration of the work, and until Contract Completion.  Seller shall meet with Purchaser at the completion of each agreed upon period to review actual progress made through the date of the Schedule Update, including dates for activities actually started and/or completed, and to review the overall percentage of work actually completed.  The data date of each Schedule Update shall be the last Day of the month, or some other Day previously designated by Purchaser.  In case of disagreements at the Schedule Update meeting concerning actual progress to date, Purchaser's determination shall govern.

2.2	 In addition to the Project Schedule updates, Seller shall submit a Monthly Contractor's Progress Report containing the following minimum information as follows:

Monthly Contractor's Progress Report

Timing:    Submitted 4 copies (4th of each Calendar month)

Contractor Name:

Reporting Month:

(1)  Management Summary (One Page)

-  Overall Project Situation

-  Major Activity

-  Significant Problems

(2)  Progress Review

-  Milestone Report

-  Updated Bar Chart Schedule (Current vs. Target)

-  Problems Affecting Progress

-  Decisions and Actions

-  Actions and Orientations required from Purchaser

(3)  Commercial Situation

-  Payment Status

-  Change Order Register

-  Notice of Claims

3  RECOVERY SCHEDULE

3.1	Should the updated Project Schedule show at any time during Seller's performance, in the sole opinion of Purchaser, that Seller is fourteen (14) or more days behind schedule for any Specific Date, Seller shall prepare a Recovery Schedule at no additional cost to Purchaser (unless Purchaser is solely responsible for the event or occurrence which has caused the schedule slippage) explaining and displaying how Seller intends to reschedule his work in order to regain compliance with the Project Schedule.

4  PROJECT SCHEDULE REVISIONS

4.1	If, as a result of the monthly and periodic Project Schedule Update, it appears the Project Schedule no longer represents the actual prosecution and progress of the Work, Purchaser will request, and Seller shall submit, a revision to the Project Schedule.

4.2  Seller may also request revisions to the Project Schedule in the event Seller's planning for the Work is revised.  If Seller desires to make changes in the Project Schedule to reflect revisions in its method of operation and scheduling of the Work, Seller shall notify Purchaser in writing, stating the reason for the proposed revision.  In no case will notice to Purchaser of a request for schedule revision relieve Seller of any of his obligations under this Contract.  All Project Schedule revisions and updates shall conform to all provisions of the Contract documents contained herein.

# EXHIBIT L  EQUIPMENT REQUIRING INSURABILITY CERTIFICATE

Gas Turbines

Generators

EXHIBIT M-1  SPARE PARTS

SELLER’S OPERATING SPARES (ROUTINE) AND PRICES ARE ATTACHED HEREUNDER:

The prices as detailed under Exhibit M-1 are firm for those components ordered prior to the date stated in the footer, and will be updated by Seller for purchases after that date.

[Note:  Must be attached prior to execution]

# EXHIBIT M-2 COMMISSIONING SPARES AND SPECIAL TOOLS

1.	Sellers Start-up Commissioning Spares as required for the Scope of Work are:

∙	One (1) set of filters (except inlet filters); and

∙	One (1) set of gaskets.

2.	The following special tools are provided pursuant to Section 3.14.1:

Turbine maintenance tools (one (1) set per site):

∙	Guide pins (for removal or replacement of bearing caps, compressor casing and
	exhaust frame);

∙	Bearing and coupling disassembly fixture.

Generator maintenance tools (one (1) set per site):

∙	Rotor lifting slings;

∙	Rotor removal equipment including shoes, pans and pulling devices; and

∙	Rotor Jacking bolts.

Installation Equipment:

∙	Trunnion for generator (on loan basis only):

∙	Foundation/installation washer and shim packs; and

∙	Jacking bolts for generator.

# EXHIBIT N-1  PURCHASE AMOUNT RECONCILIATION

| Item | U.S. Dollars |
| --- | --- |
| Base Price for the Unit | 36,000,000 |
| TDI - (162 manweeks) | Included |
| O & M Manuals (10) | Included |
| Maintenance Tools | Included |
| Second Battery Charger | Included |
| In/out Warranty obligation | Included |
| Delete Historian | (130,000) |
| Add Noise attenuation to 85 dB(A) Near Source | Included |
| Inlet System protative coating for high humidity | Included |
| Power Systems Stabilizer | Included |
| -20oF Protection for CO2 tank | 19,000 |
| Combustion System designed to accept 365oF fuel | Included |
| TOTAL (the “Purchase Amount”) | 35,889,000 |

[Note To be revised on a case-by-case basis]

# EXHIBIT N-2  OPTIONS

| Item | Quantity | Price in (U.S. Dollars) |
| --- | --- | --- |
| 1. Training as described in Exhibit H-2 A. GTG Maintenance B. GTG Mark V Technician C. EX2000 Excitation Prices for these classes shall be escalated by 6% per year commencing January 1, 2002 and on the first day of January for each subsequent year thereafter that the option is exercised. | 1 Class (1 week) 1 Class (2 weeks) 1 Class (1 week) | $43,200 $72,000 $40,900 |

# EXHIBIT O  HAZARDOUS MATERIAL NOTIFICATION

HAZARDOUS AND TOXIC SUBSTANCES

DISCLOSURE REQUIREMENTS

CONTRACT NUMBER

Show the order identification

on all correspondence

Seller:

Attention:

Address:                                      ZIP:

Phone Number: (     )

HAZARDOUS AND TOXIC SUBSTANCES DISCLOSURE REQUIREMENTS

The Occupational and Health Act (OSHA) of 1970, and OSHA regulation 29CFR 1910.20 contain hazardous and toxic substances reporting requirements.

Seller shall be required to provide the following documents, as applicable to Purchaser at the time of Contract, if possible, but not later than ten (10) days thereafter. A copy of the Material Safety Data Sheet, (Form OSHA-20), or equivalent, must accompany each shipment of hazardous or toxic substances to Purchaser.  The following documents may be required for more than one item within the Contract.

MATERIAL SAFETY DATA SHEET

The Material Safety Data Sheet (Form OSHA-20), or equivalent is required for each material containing a chemical substance which: (i) is regulated by any Federal law or rule, (ii) is listed in the latest edition of the National Institute for Occupational Safety and Health Registry of Toxic Effects of Chemical Substances. (iii) testing has yielded positive evidence of an acute or chronic health hazard, or (iv) has a Material Safety Data Sheet available to Seller indicating that the material may pose a hazard to human health.

-AND/OR-

SELLER DISCLAIMER STATEMENT

Seller may alternatively submit a disclaimer statement set forth below:

HAZARDOUS AND TOXIC SUBSTANCES DISCLAIMER

Seller hereby swears or affirms that the material furnished on this Purchase Order does not, to its best knowledge, contain any toxic substances or harmful physical agents as defined under 29CFR 1910.20.  In the event Seller discovers that such hazardous and toxic substances or agents are to be supplied, an appropriate Material Safety Data Sheet (Form OSHA-20), or equivalent shall be immediately supplied to Purchaser.

Signature of Company Officer         Date:  _______________________________

____________________________ 
Title

NONCOMPLIANCE

Seller assumes all responsibility for its failure to supply Purchaser a completed Material Safety Data Sheet (Form OSHA-20), or equivalent or a Seller Disclaimer Statement as applicable.

# EXHIBIT P  UNIT SERIAL NUMBER

UNIT’S SERIAL NUMBERS:

Gas Turbine		[---------]

Generator		[---------]

Seller shall provide the above serial numbers prior to the ODM.

# EXHIBIT Q RESERVED

# EXHIBIT R  OBSERVATION POINTS

Seller’s major observation points are as follows:

Gas Turbine

Full Speed No Load Test

Compressor Rotor Balance

Turbine Rotor Balance

Certify for Shipment

Generator

Stator Hi-Pot

Rotor Hi-Pot

Rotor Balance

Control System

Final Test

# EXHIBIT S  FINAL WAIVER  OF LIENS FORM

AFFIDAVIT AND RELEASE OF LIEN

THE STATE OF ________	§

COUNTY OF ___________	§

[Seller Name] hereby acknowledges the receipt and sufficiency of the sum of $                , (                                                           ), and other good and valuable consideration, in full payment for all design, labor, materials, equipment, supplies and services, for the supply of diesel GTG package for the [            project name                  ], ("the Project") pursuant to the Purchase Contract No. [           ] dated [--------] , between [Seller Name] (the "Seller") and [--------] (the "Purchaser").

[Seller Name] hereby acknowledges and certifies that [--------] paid                                            , all sums owing and that it has no further claims against [-------], or any subsidiary, affiliate or parent of [-------] except for the outstanding unresolved Change Order listed in Appendix A to this Affidavit.  [if none, delete all of paragraph after "except for..."]

[Seller Name] further covenants and warrants that the Project is free from all liens and claims for payment by any subcontractor, materialman or employee.

In consideration for such full payment, [Seller Name], on behalf of itself and its predecessors, employees, agents, officers, directors, shareholders, representatives, attorneys, successors, insurers and assigns, subcontractors and on behalf of any other persons claiming by, through or under [Seller Name], does hereby waive, release, and relinquish its rights to and discharge, release and acquit [-------], its subsidiaries, affiliates and parent and its employees, agents, officers, directors, shareholders, representatives, attorneys, successors, insurers, assigns and subcontractors, from any and all causes of action, claims, demands, debts, liabilities, expenses or costs of any kind and every character and nature whatsoever, including but not limited to any lien claims or rights, whether known or unknown, contingent or fixed, either in or arising out of the law of contracts, torts or property rights, whether arising under statutory law or common law, at law or in equity, with respect to the above-referenced property.  Furthermore, [Seller Name] agrees to Indemnify and hold harmless [Purchaser Name], its subsidiaries, affiliates and parent and all other persons or entities released by [Seller Name] above against the full amount of any liability, loss, claim, damage, or expense (including attorneys' fees and any judgment required to be paid) in connection with any of the matters it has released in the event any person should assert against such released person or entity a claim under assignment or title derivative from [Seller Name] and in connection with any claims made in connection with or relating to [Seller Name] provision of design, labor, materials, equipment, supplies and/or services on the above-referenced property.

EXECUTED this _________ day of ______________________, 200[–].

[Seller Name]

By:

Name:

Print or Type:

Title:

SWORN TO AN SUBSCRIBED BEFORE ME, under my official hand and seal of office on this ____ day of ___________________, 200[–].

Notary Public in and for

the State of

My Commission Expires:

(SEAL)

AFFIDAVIT

THE STATE OF ________	§

COUNTY OF ___________	§

BEFORE ME, the undersigned Notary Public, on this day personally came and appeared                                     known to me to be the individual whose name is subscribed to the foregoing RELEASE OF LIEN and being duly sworn, did state and acknowledge on his oath that he is the                           of                                            , is authorized to execute and deliver the foregoing on behalf of                                              as an act and deed of that entity for the purposes and consideration therein expressed.

GIVEN UNDER MY HAND AND SEAL OF OFFICE this _______ day of ________________, 200__.

Notary Public in and for

the State of

My Commission Expires:

(SEAL)

CERTIFICATION

This is to certify that all work covered by Invoice No. [__________]  is complete and that the invoice is correct, authentic and the only one issued for the work described therein.

[      NAME OF OFFICER      ]

A C K N O W L E D G E M E N T

(COUNTRY) [                       ]

(CITY)   	[                       ]

Before me, a Notary Public for and in the City of [     CITY     ], [     COUNTRY     ], this [     DATE      ] personally appeared    [     NAME OF OFFICER    ], exhibiting to me his Residence Certificate No. [               ] issued at [                    ], [     NAME OF OFFICER    ] on [               ] to be the same person who executed the foregoing Certification acknowledged to me that the same is a free and voluntary act and deed and to me known as the same person who acknowledged this certification.

In witness hereof, I have hereunto set my hand and affixed my notarial seal this [     ] of [               ], 200[---] in

[   NAME OF CITY   ] [     COUNTRY     ].

[	NAME OF NOTARY		]

Notary Public, State of

My Commission Expires:

Doc. No. ____________

Page No. ____________

Book No. ____________

Series of 200

W  I  T  N  E  S  S  :

[         NAME          ]								 [          NAME          ]

# EXHIBIT T  DOCUMENT DELIVERY SCHEDULE
AND DOCUMENT DELIVERY STATUS

| MPL or MLI | Title | Document Delivery Date (Weeks after ODM) |
| --- | --- | --- |
| 0040 | MS/SCHEMATICS | 10 |
| 0301* | OUTLINE, GT PACKAGE CONN-ELEC | 14 |
| 0302* | OUTLINE, PURCH MOUNTED DEVICES | 14 |
| 0306* | OUTLINE, MECH-GT & LOAD | 12 |
| 0313* | OUTLINE, GT PACKAGE CONN-PIPING | 14 |
| 0314 | NOTES, GT PACKAGE CONN OUTLINE-PP | 14 |
| 0323* | PL, FOUNDATION INTERFACE OUTLINE | 14 |
| 0330* | OUTLINE, FOUNDATION INTERFACE, OFF-BASE, ELECTRICAL | 14 |
| 0326* | OUTLINE, FOUNDATION INTERFACE, OFF-BASE, MECHANICAL | 20 |
| 0408 | WT & CG, GAS TURBINE PACKAGE | 14 |
| 0414 | DEVICE SUMMARY | 11 |
| 0438 | DOCUMENT LIST, GTD TO CUSTOMER | 6 |
| 0444* | DIAGRAM, ONE LINE | 11 |
| 0463 | DIAGRAM, BLOCK, CABLE | 12 |
| 1603* | FOUNDATION BOLTING ARRANGEMENT | 14 |
| 0403 | ELEMENTARY CONNECTOR CONTROL PANEL | 30 weeks prior to scheduled shipment |
| A068 | FIRE PROTECTION SYSTEM, CO2 | 20 |
| A130 | AIR PROCESSING UNIT | 20 |
| EO25 | COMPRESSOR & TURB WASHING SYSTEM | 20 |
| AO59 | CONTROL CENTER PKG, OFF BASE | 20 |
| A111 | GENERATOR TERMINAL ENCLOSURE | 20 |
| A141 | TRANSFORMER, ISOLATION, STAT STR | 20 |
| A150 | XFORMER, PWR POTENTIAL-OFF BASE | 20 |
| A192 | LCI/EX2000 COMPT W/O HV | 20 |
| 0 | O & M INSTRUCTION MANUALS (10 final sets in English) | See Section 10.1.1 (85 days after delivery) |

Drawings annotated with * are subject to Document Liquidated Damages.

DRAWING PROCESSING

A copy of each drawing reviewed will be returned to Seller as stipulated herein.  Copies of drawings returned to Seller will be in the form of a print with Purchaser’s marking.  The parties agree that the only document for which the assignment of Status 3 shall be applicable, will be the Electric One Line drawing.

A.	DEFINITION OF SELLER DOCUMENT REVIEW STATUS

The guidelines listed below are followed in assigning the document status number to Seller prints.  These status numbers serve as hold points for starting or continuing manufacture of the covered commodity.  The document and its transmittal letter indicate the reason for the status.

Status 1: Work may proceed.

The document conforms to Contract requirements.  The document requires no changes or additions.  Matters remaining to be resolved do not require document change and will be handled by correspondence.  Where it is known that the design information on a supplier document is not complete and resubmittals will be made, such as “hold” areas, the document is assigned another status number.

Status 2: Revise and resubmit.  Work may proceed subject to resolution of indicated comments.

The document is in basic conformance with Contract requirements.  Minor deviations from Contract requirements (not including minor changes for Purchaser’s convenience) have been noted or other minor technical or physical changes in the equipment are required.  Such changes may include those affecting dimensions, material, colors, etc.  Administrative type changes such as inclusion or equipment or tag numbers and shipping notes may be combined with technical changes in this status.  Seller shall resolve comments and resubmit documents prior to shipment of commodity.

Status 3: Revise and resubmit.  Work may not proceed.

Work may not proceed because the document:

•	The contents of the document do not reflect or materially contradict the requirements of this Contract or the document is not useable by Purchaser for its intended purpose.

Status 4: Review not required.  Work may proceed.

Document is not subject to Purchaser review.  Typical uses for this status are in the review of items that are supplier standard products, small internal parts of major equipment, or Seller standardized data.

Permission to proceed does not constitute acceptance or approval of design details, calculation analysis, test methods, or materials developed or selected by the supplier from full compliance with contractual obligations.

FINAL DRAWINGS

Upon receipt from Purchaser of drawings marked Status 1 or Status 4, Seller drawing shall be considered acceptable and no further corrective action shall be required.  After completion of fabrication and release for shipment, all drawings shall be resubmitted showing the “as installed” configuration of the Equipment.

The parties agree that the only document for which the assignment of the Status 3 shall be applicable, will be the Electrical One Line drawing.  Seller shall deliver eight (8) complete sets of drawings, to Purchaser, or as otherwise mutually agreed.