G3512 EMISSIONS DATA

Caterpillar G3512 Low Emissions

GKGE06                TMI - ENGINE AND COMP PERF              DATE: 10/11/2001

20 - GENSET ENGINE PERFORMANCE                                 TIME: 11:07:17

TURBO QTY:

G3512  SI TA SC FUEL: NAT GAS    FUEL PR:  30 PSI  CARB:  IMPCO C/R: 11.0:1

570.0 EKW 60 HZ 1200 RPM NOX LVL: 2 g/bhp-hr   IGN: EIS    JW TEMP:DEG F 210

DM0745-02  ELEK A/F CONT: NO   CAM TYPE: STD PISTON:       A/C TEMP:DEG F 129

RATING TYPE: CONTINUOUS                                     EFF S/N:

INFO CODE 05 - EMISSIONS DATA * * * * * RATED SPEED  * * * * * * * * * * * * *

O2 (DRY)

GEN          ENG      NOX            TOTAL  NON-METH        IN EXH

PWR   %      PWR   (AS O2)   CO       HC      HC     CO2    (VOL)

EKW  LOAD    BHP   * * * * * * * *  LB/HR   * * * * *TNS/HR    %    LAMBDA

570.0  100   814.0    3.59    2.83    9.68     1.45      .4   8.80    1.67

427.5   75   610.5    3.47    2.15    6.70     1.00      .3   8.21    1.55

285.0   50   407.0    2.96    1.58    4.34      .65      .2   7.33    1.46

Caterpillar G3512 Catalytic Combustion

-GKGE06                TMI - ENGINE AND COMP PERF              DATE: 10/11/2001

20 - GENSET ENGINE PERFORMANCE                                 TIME: 11:10:34

TURBO QTY:

G3512  SI TA SC FUEL: NAT GAS    FUEL PR:  25 PSI  CARB:  IMPCO C/R:  9.0:1

555.0 EKW 60 HZ 1200 RPM NOX LVL: CATALYST     IGN: EIS    JW TEMP:DEG F 210

DM5209-00  ELEK A/F CONT: YES  CAM TYPE: STD PISTON:       A/C TEMP:DEG F 129

RATING TYPE: CONTINUOUS                                     EFF S/N:

INFO CODE 05 - EMISSIONS DATA * * * * * RATED SPEED  * * * * * * * * * * * * *

O2 (DRY)

GEN          ENG      NOX            TOTAL  NON-METH        IN EXH

PWR   %      PWR   (AS O2)   CO       HC      HC     CO2    (VOL)

EKW  LOAD    BHP   * * * * * * * *  LB/HR   * * * * *TNS/HR    %    LAMBDA

555.0  100   791.2   18.41   18.05    3.09      .46      .4    .30     .99

416.3   75   593.4   12.92   15.43    2.76      .41      .3    .30    1.00

277.5   50   395.6    8.31   11.02    2.59      .39      .2    .30     .99

Caterpillar G3512 Standard Combustion

GKGE06                TMI - ENGINE AND COMP PERF              DATE: 10/11/2001

20 - GENSET ENGINE PERFORMANCE                                 TIME: 11:12:18

TURBO QTY:

G3512  SI TA SC FUEL: NAT GAS    FUEL PR:  25 PSI  CARB:  IMPCO C/R:  9.0:1

555.0 EKW 60 HZ 1200 RPM NOX LVL: STD          IGN: EIS    JW TEMP:DEG F 210

DM5207-00  ELEK A/F CONT: NO   CAM TYPE: STD PISTON:       A/C TEMP:DEG F 129

RATING TYPE: CONTINUOUS                                     EFF S/N:

INFO CODE 05 - EMISSIONS DATA * * * * * RATED SPEED  * * * * * * * * * * * * *

O2 (DRY)

GEN          ENG      NOX            TOTAL  NON-METH        IN EXH

PWR   %      PWR   (AS O2)   CO       HC      HC     CO2    (VOL)

EKW  LOAD    BHP   * * * * * * * *  LB/HR   * * * * *TNS/HR    %    LAMBDA

555.0  100   791.2   36.13    2.65    2.16      .32      .4   2.00    1.09

416.3   75   593.4   23.96    2.20    1.82      .27      .3   1.25    1.06

277.5   50   395.6   15.83    1.54    1.58      .24      .2   1.60    1.09