Services provided by Northern Natural Gas

And Transwestern Pipeline Company

- Enron Transportation Services

- Gas Control Event Log

0630 to 1830 Shift Tues., Jan. 15, 2002  (Hardy, Muntz, Munson, Spain, Monden)

| 0640 | Ogden | Unit 13 back on line. Kyle said the unit had over torqued. Pumping east. Monden |
| --- | --- | --- |
| 0645 | LaPlata | Larry called in from LaPlata. He has the unit alarm cleared at that location. He had been called out earlier before Jesse went home to look at this unit alarm. Larry said it was caused by a high scrubber level. He has made arrangements for the trucks to come by today and empty the tanks. He doesn’t think we’ll be getting this alarm anymore. Also at this time since I had Larry on the phone I asked him about an AC power alarm that we received last week at the time of all the problems over at the Outlaw location. Larry informed me that the reason the AC power alarm that we have up here has not gone away is that there is not a hook up available for the alarm feature on the battery charger that was installed to take the place of the old one. Larry said that the replacement battery charger is a different style and does not have a physical attachment for the alarm feature so that the alarm that we’re receiving will remain as long as that battery charger of that type is on location. Munson |
| 0735 | Warren Monument | I’ve got delmar malfunction alarm and a high H2S alarm. I got a hold of Duane with the Eunice team. He is going to find Greg to send him out. Greg is going to call in to let us know what he’s found. Hardy |
| 0915 | Spraberry | Tom called. He lost unit 5 pumping out to Valero. He asked me to put a –15 setpoint in their flow rate until he could get a unit back on line. Hardy |
| 0910 | NGPL Gray | There seems to be a problem with the setpoint control at NGPL Gray. I’ve asked Joe Martinez to go take a look at things. He said that he may need to do an adjustment on the gain control. I’ve sent my setpoint this morning and it hasn’t responded in a timely manner. Munson |
| 0950 | Roger Mills | Talked to Jim. He shut down unit 2 there. I’ve also put a zero setpoint into the 16”. We’re going to close off the flow of gas on that line but still try to maintain a little pressure for Aquila to come in with their 16 million. Hardy |
| 0950 | Tescott | I just sent a remote start to unit 5 at Tescott on the “E” line. Muntz |
| 0950 | Beatrice | Had OCC get a hold of the contact person, Larry Brenneis. Asked Larry to put on the turbine going “E” to “E” at this time to send more gas north, fill out the “BC” line up past Beatrice since it’s cracking over up there to the “BC” and then on up Ogden. Monden |
| 1030 | North Branch | Ted called in and said that their plant had ESD’d. He will call me back and inform me of the situation as soon as possible. Monden |
| 1058 | Alexandria | Put the unit on line to hold up the pressure on the Benson delivery. Monden |
| 1101 | Alexandria | Had valve fail to operate alarm. The unit went back down. Notified OCC for the contact person. Monden |
| 1102 | Beatrice | Unit 27 the turbine is on “E” to “E”. Monden |
| 1119 | North Branch | Jim called back and said they had a BSD, gas leak in the engine room. They got that fixed and #2 is back on pumping west. Monden |
| 1130 | Eddy Co. | I noticed that the El Paso flow at Eddy Co. went to zero. I contacted their operations center and talked to James. He said they took their compression down for some PM. He expects to be back up in 3-4 hours. He plans on making all of the gas up and coming on rate for the day. Their nom today is 32. Munson |
| 1133 | Alexandria | It is back on line. Mark said he’s got things reset, brought it back up. Appeared to line out. Monden |
| 1326 | Great Lakes | Gary Spraggins gave me a call and said that they owe us 10 million and it was OK to go ahead and come in with an extra 10 million at this interconnect. Monden |
| 1440 | Mitchell Ellenberger | Have been getting intermittent spikes on H2S. We’ve been getting .25 and .26 reading from there. The CO2 has just now jumped up from about 1.9 up to 3 and 4. I called out to the plant and talked to James. He said they lost a refrigeration compressor. They’ve got everything lined out now and the gas should be coming back down within spec. Right now H2S is showing .23. CO2 is still 4.1. Hardy |
| 1548 | NGPL Glenwood | Spoke with Karen Clapper. She said she had spoken with NGPL schedulers and they had no problem with leaving it shut in for Wednesday and Thursday also. The nom she said was the same which is 5.759 for present day and Wednesday and Thursday. Then she said she would discuss it with Steve on Friday, truing up the imbalance. Monden |
| 1622 | Ventura | Requested Jim to put the turbine on the “C” to “BC” so they would have a unit there pumping north for the evening load. Monden |
| 1650 | Bloomfield | At approximately 1500 the #4 unit at Bloomfield went down. The unit was bought back on at approximately 1630. The reason for the approximation on the downtime was that there was no alarm given. The guys at the site were not sure what time it went down. They were not able to look at accurate data where they could see what time the actual unit went down. This unit did not show an alarm to us here in gas control either. I thought there might be a problem when I noticed the flows backing down in the San Juan area and our high pressure suction climbing and discharge dropping. That’s when I called Chris at Bloomfield and let him know that he might have a problem. He went out and confirmed that #4 was indeed down. They proceeded to work on it and get it back on line. I did inform Larry at LaPlata. He went to the LaPlata site along with Dave and they were able to back their HP down to keep it within MAOP parameters. I also informed personnel at Bisti and Gallup that we’re having these problems at Bloomfield. Munson |
| 1715 |  | I got a call from Marvin Begees with EOTT. They are wanting to launch a pig from New Parish TX to Longview. This is part of a pigging project that AEP is starting. They are going to have to put the pig in on our part of the line because they don’t have a launcher on their part. They are going to start the pig here in about 1800 hours. They will give us a call when they are done. Hardy |

1830 to 0630 Shift Tues., Jan. 15, 2002  (Hall, Armitage, Barry, Braswell)

| 1800 | Ventura | The day crew had called the OCC. Got a hold of the on call person Jim Roseland who called fellow out. He tried to put on #15. Could not get 15 to go, the problem being that it’s wheeled for 800# suction for running on the “D” line and we’re trying to run it on the “C” line. Hall |
| --- | --- | --- |
| 1900 | Citizens Griffith | Talked to Tom Tucker. He called me a few minutes ago and said that the power called him and told him that they were going to start up their ______ boiler and that they were going to need a little bit of gas to keep that going, probably throughout the night. That’s what he is out there for now, to open up the valves or whatever he needs to do. We already had 100 million setpoint in there for them, just there so it would be out of the way. I did touch bases and called Griffith, touched bases with him, talked to Kevin there. He did say that they were going to take a little bit of gas for the boiler that they were getting ready to fire. It will probably be throughout the night and maybe sometime in the morning. Schedulers are also aware of this as well. Called them and talked to Chris. Braswell |
| 1954 | Western Gas Midkif | Currently we are flowing a 39 flow rate on a 46 schedule. I called the Western Gas Midkif plant. I requested that they cut back on their regulator in order to push more gas back over to us to get up on rate. Barry |
| 1957 |  | I called Western Gas Benedum. Currently we are flowing a 28.5 million on a 22.7 schedule. I requested they cut back to come in on rate. Barry |
| 1957 |  | I also called Phillips Plymouth and requested that they cut back. We’re currently flowing a 31.5 on a 27. Barry |
| 0100 | Burdett | Called a man out to find out what was going on at the station since the station suction and discharges were showing one thing and the units were showing something else. When he got to the station he found #6 was down. #6 had bypasses, one opened up and one of them was blowing gas and yet the unit was still showing as down. He called back in after he put #4 on line. #4 was now showing it was running here in Houston. In fact the suction and discharges on 3 and 6 were different from what was on the station. He has called a tech out and they looked at the station. They got 3 and 4 up and talking. Suction and discharges are almost matching with the station now but #6 is still showing it’s on line and #6 is still showing a different suction and discharge on it. They are going to look at it in the morning. Armitage |
| 0113 | Sublette | 23 and 24 have gone down. They were on the field. The suction is down to 108. The man has called in because he had gotten paged on them. He said to have them re-page him at 125 or if we wanted to we could try to put a unit on. If it would go on that’s fine but he still needs to be paged even though we successfully get one on the line because we might have to put the other one on too. Armitage |

slb