Services provided by Northern Natural Gas

And Transwestern Pipeline Company

- Enron Transportation Services

- Gas Control Event Log

0630 to 1830 Shift Sat., Jan. 12, 2002  (Hall, Armitage, Barry, Braswell)

| 0805 | ANR Janesville | Got a call from Todd. He wanted to know what our volume was doing. It was doing 31. He said he lost communication to it. He is going to get someone to go out and check it out for him. Hall |
| --- | --- | --- |
| 1025 | Clifton | Tried to put on #31 “E” to “E”, it didn’t go. I called the OCC and they got a hold of Stan. He’s going to go out and clear the alarm. Got the boiler alarm and shut down alarm combination on it. He’s going to clear the alarm and see if we can get it going. Hall |
| 1116 | Clifton | Got a call from Stan. They got #31 on. Hall |
| 1205 | TransColorado | Kinder Morgan called and was inquiring about the erratic flow that he’s getting out at the TransColorado point. I did call OCC and got a hold Chris. Explained to him what was going on. The nom is 93 and the flow has been fluctuating between 100, then 90, then down to 86. Chris told me that there really wasn’t a whole they could do at this time. That valve hasn’t been working for awhile and it does fluctuate like that, swings. He feels like there is something wrong with IDP inside the flow controller and their management knows about it. Right now they need to replace the valve but they just haven’t got around to replacing that valve for right now. I did inform TransColorado that there is nothing we can do about that right now. She said to leave the setpoint that we have in there right now of 93. We’ll just have to work from there. Darrell was informed of this conversation. Braswell |
| 1224 | Macksville | Called the OCC. They got a hold of Brian the on call. Asked him for two turbines on the high side. We have 250-300 million coming up from Beaver and the pressure is climbing down at Mullinville. Also have the 41 million coming in from ANR and then an additional from Cunningham of 50 million. Have over 400 million for us to move. Hall |
| 1508 | Macksville | Just got a call from Brian. We’ve got the units on and just got the setpoints taken care of. Hall |
| 1720 | Sublette | Called the OCC. Communication is out. Had Chris check it here. The only one that is not working is the SUBL. The SUEX and the HASK and HASK1 are all working out there. Russell is going to go out and check it out for us. Hall |

1830 to 0630 Shift Sat., Jan. 12, 2002  (Alvarado, Barnes, Moore, Cochran, Coash)

| 1818 | Station 2 | Unit 203 has gone down. I’ve contacted OCC and spoke with Hank. Hank is on his way out. Alvarado |
| --- | --- | --- |
| 1839 | Station 2 | Hank called in and said that he spoke with the man that lives on site and it looks like we’ve lost a piston on the unit. They are going to start unit 202 and then work on unit 203 to get it back available to us. Alvarado |
| 1848 | Skellytown | H2O at 7.8#. It’s normally .6#. Advised the on call Steve on the Pampa team. While I was speaking with him it went up to 9#. He will check that out and get back with us. Barnes |
| 1909 | Coronado Pecos | POI 2230 – The nom today is 10 however our minimum flow rate is 15 which we’ve been doing today. At this time the flow rate dropped down to 11. I spoke with Hector. He has a setpoint which was restricting our delivery to him at the needed 15 flow rate to get correct measurement. He agreed to raise his setpoint and allow us to make up a couple of million. He also would see what he could do about making up 1-2 million everyday until we balance. Barnes |
| 2000 | Cunningham | At approximately 1900 Cunningham was withdrawing 50. Had them go ahead and shut in. At this time having them go to 100 injection. Cochran |
| 2038 | Station 2 | Unit 202 is finally on line. They had problems with this unit, bringing it on. It was brought on due to unit 203 going down on a piston. Alvarado |
| 2021 | Skellytown | According to Eric Haiduk who called in, he said the water problem is under control. Barnes |
| 2042 | Maxus Dumas | Oxygen of –29.3 from 16.8. Advised the Sunray operator. Barnes |
| 2038 | Atoka 3 | Unit 761 is back on and available and is running at this time. Alvarado |
| 2153 | Maxus Dumas | Oxygen now a correct reading of 17.9. Barnes |
| 0024 | Jal | Unit 2 down. Advised Oscar. Barnes |
| 0040 | Perryton Barlow | Station ESD’d, units 1 and 3 are down. Steve Rima the on call operator is in route. Barnes |
| 0045 | Western Gas | Benedum is sending NNG 31 which is 10 over on the spot rate temporarily until Western can re-establish flow to El Paso. El Paso’s H2S instrument malfunctioned and shut their valve. Barnes |
| 0124 | Skellytown | Oxygen a .22%, up from a .15%. Advised Steve the on call operator. Barnes |
| 0136 | Beaver Co. 5 | Unit 4 down on low suction, 34#. Operator will leave it down until morning. Barnes |
| 0200 | Skellytown | Oxygen – Eric Haiduk called to say that he spoke with Skellytown station personnel. They will bring the oxygen content back into spec. Barnes |
| 0158 | TW Beaver | The flow rate went from around 30 up to 122 MMBtu. I contacted OCC and spoke with Bill. He said he would have to get a hold of one of his techs on the pipeline team. Alvarado |
| 0202 | Western Gas | Benedum flow rate is back to 22 spot rate. Barnes |
| 0241 | Skellytown | Oxygen now back in spec. It’s OK at 0.21%. Barnes |
| 0255 | TW/NNG Beaver | Billy Howard has called in and he said that he is on site. It seems like the interconnect is shut in. He is going to have to contact his tech to go out and reset this interconnect so we can get it flowing again. Alvarado |
| 0250 | Eldorado | DAS communication has been out since 0147. It could be an AC failure. Advised the Big Lake on call operator Larry. Barnes |
| 0303 | TW Beaver | The interconnect is starting to flow again. Billy Howard said that he found one of the transmitters that was frozen and also the heater had gone out. He is re-lighting that heater. He going to be around there for another 30 minutes to an hour to make sure everything is all right. Alvarado |
| 0300 | Cunningham | Just took them from 200 injection up to 300. Cochran |
| 0312 | Perryton Barlow | Station is back on with units 1 and 3 again. Barnes |
| 0333 | Eldorado | Operator called in to say that the station which is not running should be OK until morning even if it’s an AC failure, a loss of air pressure or even DC batteries die. Barnes |
| 0350 | Clifton | Just lost unit 31 on the “E” line. The alarm is reset. As soon as it equalizes we can give it a start command but for now just leaving it down, waiting for it to equalize. Cochran |
| 0521 | Jal | Unit 2 back on. It was flagging out on lubricators. Barnes |

slb