Services provided by Northern Natural Gas

And Transwestern Pipeline Company

- Enron Transportation Services

- Gas Control Event Log

0630 to 1830 Shift Sun., Oct. 14, 2001  (Monden, Muntz, Hardy, Spain, Henley)

| 0720 | Tate | The station is down. The on call is on the way. Hardy |
| --- | --- | --- |
| 0745 | WT1 | Have a station alarm. Rick is going to check it out. Muntz |
| 0815 | Willmar | I got a low battery voltage at Heartland Corn Products. It’s 10.4 volts. The alarm is set at 11 volts. I called the on call person for the Willmar district, spoke to Mark Werner. He is going to place a call to Jim Nelson who handles the TBS so he’ll be informed of the low/low alarm that we have on the battery voltage. Spain |
| 0856 | WT1 | Got a station alarm. Rick is on his way back out. Muntz |
| 0940 | EOG Pitchfork Ranch | Flow rate went to zero. I called Dirk Ellison and left a voice mail. Muntz |
| 0941 | LaPlata | We lost a unit at LaPlata. Terry is on his way out. We called NWPL, also Amoco and WFS and let them know that the unit was down. Muntz |
| 1013 | Keystone | We’re flowing 25 million at this point. The nitrogen reading on our side is showing 3 ppm and seems to be hung up there. I spoke with Isaac in their gas control. He said he had about 2.4. Monden |
| 1015 | Cunningham | Put in an order with Linda to take injection to zero. Also called Larry at Bushton to inform him and to get him to turn the gas around and send it north for us. Hardy |
| 1115 | Sublette | Unit 13 is down. Frank is on his way. Hardy |
| 1200 | Sublette | The station on AC power failure. Talked to Mike. He is going to go out and give Frank a hand to get the station back on line. In the meantime I called and talked to Roger at Hugoton and let him know. He is going to go back out to the plant and watch things to make sure none of the units fall down. Also called and talked to Mullinville to let him know too. He was going to slow down some of the units to keep his on line. Hardy |
| 1305 | Sublette | Mike called. They’ve got one unit up so far. Called and talked to Roger over at Hugoton to let him know. In the meantime I had sent an additional 10 million from Hugoton up to Holcomb. I called and left a message with the Holcomb operator to let him know the extra gas was coming his way until Sublette gets on line. Hardy |
| 1344 | Woodward Co. 2 | Unit #2 is back on line. Alan got it on. Monden |
| 1530 | NNG Gray Co. Bi-directional | Started picking up a 10 million flow rate on the MMcf side. The interconnect has been shut in since the day before yesterday. Actually we’re not showing any flow rate on MMBtu at all. We called Joe Martinez and let him know that we had the point inhibited to a zero. He is going to check into it tomorrow. Muntz |
| 1647 | El Paso Keystone | Spoke with Paul in their gas control. He said they were having some operational problems and were starting to stack up and that they would probably just do the nom rate for today. Still owe them 7 million from yesterday and they were going to do the Waha delivery that was 3 today at the Keystone point. Let him know so they can add this on tomorrow’s delivery to El Paso. Monden |

1830 to 0630 Shift Sun., Oct. 14, 2001  (Braswell, Hall, Armitage, Ellington)

| 1751 | WT2 | Lost unit 3. Called the OCC for the on call. Braswell |
| --- | --- | --- |
| 1822 | Station 2 | Called the OCC for the on call for the person at station 2. Have received a unit 3 alarm. I ended up talking to Tracy from station 2. Informed him about the alarm on unit 3. Also talked to him about the Citizens Flagstaff point with the gas outlet temperature of about 128.9. Right now it’s showing in a low alarm. They wanted us to let them know when the temperature reached that point. He said he would try to get a hold of Glen there and have him check that out. Braswell |
| 2000 | Palmyra | Called the OCC and they got a hold of Mike. He’s going out and put a fifth unit on for us on the “BCD” suction to “D” discharge. Trying to get off of the central end. Got an 854 showing at Macksville on the “E” line bypass. Try and get some of this gas moved up into the upper zones to get ready for the cool front that’s coming in. Hall |
| 2053 | Station 6 | Received a station alarm in that area. Called the OCC for the on call. Braswell |
| 2059 | P3 | Lost unit #3 out there as well as received a station alarm. Called the OCC for the on call. Braswell |
| 2211 | LaPlata | Unit 2 alarm. Called the OCC for the on call. Braswell |
| 2245 | Cunningham | Called Cunningham to put a unit on and start injection of about 60 million. Pressure at Macksville got as high as 858. Ellington |
| 0019 | Hugoton | Unit 11 is down. Notified OCC. Ellington |
| 0044 | Morton Co. 1 | Unit 7 is down. Notified OCC. Ellington |
| 0242 | Galena | Called the OCC. They got a hold of the on call. Told him I was trying to get one of the turbines started at Galena and haven’t had any luck. I have tried both of them and neither one of them has done anything. They did take the start command but nothing else has happened. Hall |
| 0315 | Artesia Team | Talked to Jerry about the scada that is out at all of the Atokas, Atoka 1, 2 and 3. We made a call out earlier for them to clear that intrusion alarm that we’ve got at Atoka 1. I informed him at that time that we needed to check out the scada. It’s been out for awhile, probably sometime this afternoon about 3:15 or 3:30. He informed me that he and Armando went out to the radio tower and found that the air condition unit was turned off in the radio building. The instruments and of course the panel tech box was extremely hot, so hot that they weren’t even able to touch it. It’s probably the reason why the radio is not transmitting the information to us at this time for all of the Atokas and all the areas that are tied into the radio. I think it’s valve 110, valve 109 and the Atokas. Braswell |
| 0158 | Hugoton | Unit 11 is back on the line. Ellington |
| 0440 | Atoka 1, 2 & 3 | They all are talking right now, are communicating. I talked to Jerry out there. I guess someone had turned off the air conditioner out in the radio tower building which is an insulated building. The temperature in the building got up to about 150 degrees and it burned up the panel tech. That’s why these points weren’t communicating to us. It’s all back in service and talking now. Braswell |

slb