Services provided by Northern Natural Gas

And Transwestern Pipeline Company

- Enron Transportation Services

- Gas Control Event Log

0630 to 1830 Shift Fri., Jan. 25, 2002  (Calhoun, Munson, Welsh, Cummings)

| 0740 | Stevens Co. 6 | I received a call from Jerry Knight with Oneok concerned about low flows coming out of Stevens Co. 6. I called the Stevens 6 location and I talked to Brent. Brent told me that the electric is down at that location and that’s the reason for the low flows at this time. Jerry said the flows have been kind of low for the last two days. Brent confirmed that the HP has been down for a couple of days and they expect to have it back on this afternoon. He said the electric HP that’s down was scheduled PM. I called Jerry back and explained this to him, that the HP should be back up this afternoon. Jerry was satisfied with the reasons for the low flow and he was happy to hear that the HP would be back this afternoon. Munson |
| --- | --- | --- |
| 0740 |  | I received a call from Don Hickey with Exxon Mobil. He was concerned about low flows coming out of Stevens 4. I called Stevens 4 and talked to Jeff. Jeff explained that there were no issues or any problems at all coming out of Stevens 4, that perhaps the problem with the low flows that Don is seeing could be due to the low flows coming out of Stevens 6 because of the connection between 6 and 4. I then called Don Hickey back and explained all of this to him, that we’re having no issues with HP at Stevens 4 and that the reasons for the low flows that he is concerned about could be connected with the low flows that we’re getting out of Stevens 6. I explained to him the same HP issues that I explained to Jerry Knight. Told Don that these should be resolved and the flow should resume to a higher rate as soon as the HP comes back on later this afternoon. Don and Jerry both seemed satisfied with the explanations. Munson |
| 0830 | Cunningham | During pressure call I asked Gloria to go to a new withdrawal order at Cunningham of 100 million. This is a cut from the 225 order that she previously had. Also at this time I asked Macksville to drop their HP that they were running. They had two units on line. Bill said that as soon as his analyzer was done within the next 30 minutes he would be able to take the HP down if it was OK with us. I OK’d him to finish with the analyzer. Then he is going to coordinate with Gloria on the shut down process and cutting back at Cunningham. I made all of the operators on the mainline aware since they were on for pressure call they all know about these changes. Munson |
| 0835 | Clifton | I requested Deanne at Clifton to drop the vertical, unit #28, at this time due to the plan numbers being lowered and the flows cut back on the north end. Rory is making HP changes, in particular taking down the turbine at Beatrice and it’s rolling back into the central system. We’re trying to make room. That’s the reason for all of these changes at Clifton, Macksville and Cunningham. Munson |
| 0630 | Ogden | They shut unit #10 down, the horizontal that was on Redfield. Calhoun |
| 0635 |  | I gave Redfield an order to go from 335 down to 300. Calhoun |
| 0654 | Beatrice | Lost unit #25, 4000 HP running on Trailblazer to the “D”. At 0704 I put unit #23 on in its place. Calhoun |
| 0720 | Madison | They went from 29 to 12. Calhoun |
| 0730 | Ogden | Got a call from Ron. He’s operating this week. They needed to get unit #18 down to work on a leak on the tubing. They were going to put unit #17 and #15 on in its place. Calhoun |
| 0810 | Beatrice | Shut unit #27 down, the turbine on the “E” line. Calhoun |
| 0815 | Oakland | Had them shut one unit down on the “D” line. They shut unit #18 down. They were also needing to do some work on it. Calhoun |
| 0822 | Minnegasco | They were going to bring 19 million back to storage at Glenwood. Calhoun |
| 0900 | Madison | They increased their flow rate from 12 to 22. Calhoun |
| 0925 | Madison | They called back and increased their flow rate from 22 to 60. Calhoun |
| 1025 | Farmington | They were needing to shut unit #1 down on the Willmar discharge to replace some fuel valves. The other two units were slowed down. It looks like we had good pressures going out towards Willmar. Calhoun |
| 1020 | Tescott | We shut #5 down at Tescott by remote after visiting with Kim at the location. We let him know that we’d like to shut it down. He suggested that we do it by remote. I notified Ed at Bushton and Mike at Clifton. I also notified Rory on the north end. Munson |
| 1025 | Farmington | They took unit #1 down to replace some fuel valves. Calhoun |
| 1100 | Hubbard | Put the electric on. Our loads had picked up, almost 120 million going out on the east leg and pressures were starting to fall off. I also called Corn Belt to notify them. Calhoun |
| 1430 | Clifton | Unit #31 down, no demand. Munson |
| 1210 | Farmington | Unit #1 put on line. Shut unit #2 down so they could work on a fuel valve. Calhoun |
| 1215 | Owatonna | Shut the turbine down. The loads had died off and we didn’t need the unit on. Calhoun |
| 1224 | Ogden | Shut unit #15 down. Calhoun |
| 1250 | North Branch | Sent a code to bypass the station. The units were already down but the station hadn’t been bypassed yet. Calhoun |
| 1305 | Beatrice | Shut unit #20 down on the “D” line. Calhoun |
| 1305 | Palmyra | Shut unit #25 down. Calhoun |
| 1318 |  | Shut both units down on the “D” line and bypass the “D”. Calhoun |
| 1350 | Waterloo | Shut unit #7 down. Calhoun |
| 1420 | Ogden | Closed valve 91, split out the “D” from the “BC” suctions. At 1500 I shut unit #13 down at Ogden. Calhoun |
| 1510 | NBPL | CC was done testing. We bumped the flow rate up from 705 to 735 to come in on rate. We were running about 30 short at the time. Calhoun |
| 1515 | Hubbard | Shut the unit down. That’s because LS Power had called in earlier at 11:00 and was going to shut down early. A lot of the other TBS’s were backing off. Calhoun |
| 1625 | Waterloo | Shut unit #1 down. Calhoun |
| 1630 | Madison | They wanted to go from 60 to 40. Calhoun |
| 1645 | Redfield | I had them go from 290 to 275 to the low end of their target. They had a target of 300 +/-25 so I went ahead and took them to 275. Calhoun |

1830 to 0630 Shift Fri., Jan. 25, 2002  (Hardy, Henley, Spain, Monden)

| 1918 | Hubbard | Called Corn Belt and spoke with Paul in their control center. Told him I was going to bring up the Hubbard station and asked him if he had any problem if I brought it up immediately because they had asked for a 20 minute grace period before we kicked it off. He said he had no problem with me starting it up at this time. He said he would watch it to come up on his power load. Monden |
| --- | --- | --- |
| 1946 | Waterloo | Shut the station down because we were losing our differential since we brought Hubbard on. We brought Hubbard on with plans of shutting Waterloo down in hopes to pack the line between Hubbard and Earlville since we are going into the weekend in anticipating lower volumes demands in the east leg. Monden |
| 2035 | Waterloo | Showing an alarm on BSD units 7 and 8. Had spoke with Russell about this alarm. When I pulled history up on it, it showed it came in alarm around 9:00. He said that they had been out there in that time but just to play it safe he is going to go out there and check the BSD on units 7 and 8 to make sure there is no gas blowing. As far as what I can tell in volumes through the station they are comparable to what the flow was when I shut the station down. Monden |
| 2126 | Waterloo | BSD status for units 7 and 8 on the alarm, it seems to be bogus. Russell went to the site and checked everything out. There was no BSD. Units 7 and 8 were fine. Monden |
| 2134 | Cedar Rapids Quad Cities | Spoke with MidAmerican, Dave. He said that on Cedar Rapids they plan on under pulling by 20 and Quad Cities they plan on under pulling by 20. The rest of the nom they would take to FDD. Monden |
| 10:35 | Perryton Barlow | Units 1 and 3 are down. Got a hold of Melvin. He’s going to go check everything out. Hardy |
| 0005 | Perryton Barlow | Melvin called. He’s got the station back up. It went down due to low air pressure. Hardy |
| 2300 | Valero Ward | Flow went to zero. I contacted PG&E and spoke with them. They said that rather than calling somebody out they’d prefer to have the gas moved over to Pecos. I sent a zero to Ward and opening up the Pecos interconnect. Henley |
| 2330 | Valero Pecos | I put a setpoint in there on run 1 for 50 million. It is only registering 7. I’ve looked at it. I called PG&E. That is what they are reading also. I put another setpoint in run 2. It’s doing the same thing. Going to call somebody out for the Monahans team and have them check it out. Henley |
| 0030 | Valero Pecos | The station is actually flowing. I can tell that by our pressures and everything. Dean from the Monahans team is going to go out there and check it out for us. In the meantime I’m going to send zeroes to both runs since it’s not measuring correctly. I’ve talked with PG&E. They are going to have somebody go out and look at Ward and open that back up. We’ll just try to flow there at Ward and disregard the Pecos delivery. Henley |
| 0145 | Valero Pecos | Just spoke with Dean. He’s leaving the station. He said that one of the problems was that the plate wasn’t all the way down in the run so that it wasn’t getting accurate measurement. He also thinks there may be a problem with flow transmitter. He wants to take that point out of service for the weekend and look at it again on Monday morning. I looked at the next days nom and currently that shouldn’t be a problem. I did tell him about that. He said that if things do change to give him a call. They’ll get it fixed before then but for right now we’re going to try not to use the Valero Pecos point. Henley |
| 0230 | Cunningham | I just gave Linda an order to shut in the withdrawal rate. We’re doing about 85. Spain |
| 0330 | WT2 Kermit | Lost unit 202. OCC is getting a hold of the on call. Henley |
| 0430 | WT2 | Shane went out and put unit 202 back on line for us. Henley |
| 0450 | Beaver Co. 5 | Unit 4 is down. The operator said that they were just going to leave the unit down until Monday. It’s been going down for the past couple of days on low suction. Duke is aware of it. They were told not to waste anymore overtime going out to put the unit back on. Hardy |

slb