Services provided by Northern Natural Gas

And Transwestern Pipeline Company

- Enron Transportation Services

- Gas Control Event Log

0630 to 1830 Shift Wed., March 20, 2002  (Barry, Hall, Armitage, Muntz)

| 0600 |  | Randy is out at WT1 starting the #2 unit, getting it ready to come on line. This morning we do have a total shutdown outage at WT2 station. At this time we’re going to utilize the time between about 6:30 and 9:00 to build the pressure up to try to maintain and keep our deliveries stable south of WT2. Barry |
| --- | --- | --- |
| 0700 |  | This morning with the outage at WT2 the 24” line south of WT2 we have a scheduled volume from NGPL Winkler of 50 million. What I’m going to do is at Halley we’re going to set Halley up coming from the 24” from TW going to the 24” NNG. We’ll take the gas from NGPL and just move it over to Halley as we do have that gas scheduled today. Barry |
| 0820 | Cunningham | They are in the process of taking the electrics down and leaving two dual fuels running at Cunningham. The flows will drop off until they get all of their electrical work done and then they will come back on line back to withdrawals. Armitage |
| 0830 | WT2 | At this time we commoned up the 30” north and south. Barry |
| 0925 | Oakland | Called the OCC. They got a hold of the on call. Asked him to put another unit on the “D” line there. Also called and asked him for the on call for Palmyra. Got a hold of Dale and he’s going to put another one on at Palmyra on the high side also. Just keep the gas moving up towards Ogden, get their suction back up a little bit. Hall |
| 0955 | Coyanosa | Rick called and said that he has the Coyanosa regulator repaired. He requested I put a 900 setpoint in it. Muntz |
| 1322 | Amoco LaPlata | I called the Floreda plant. Right now we’re running short of our schedule of 160.48, current spot is 152 and we’re only averaging 154. I spoke with Nester. He said he was working on trying to get some more gas coming our way. Barry |
| 1320 | Cunningham | They’re on the way back up to full capacity of 225-230. Armitage |
| 1410 | Hubbard | Lost Hubbard so I called the OCC. They got a hold of the on call. He looked the alarms and everything and was able to clear them. He said there was just a blip in the power to it. I gave it a start command. It is coming up on line. Hall |
| 1438 |  | Ken called from Griffith Energy. He said that the start up date would be Friday instead of this Thursday. Barry |
| 1445 |  | Dennis with El Paso called in. He informed us that in the Gallup area they would be doing some work tomorrow and they would be venting some gas to the atmosphere so if we happen to have any kind of phone calls reporting gas in the atmosphere they are working on their line. Barry |
| 1523 | ONG 3 | Just sent a zero to ONG 3. We have accumed the nom rate for today. It shows that we have accumed 7.0 on a 6.5 nom. Muntz |

1830 to 0630 Shift Wed., March 20, 2002  (Moore, Alvarado, Barnes, Cochran, Coash)

| 1805 | LaPlata | Received an alarm in here. The discharge pressure jumped up to 1046# which has got to be a bad read. The units are on. It did drop back down to 1011 in about 5 minutes. I talked to David the on call. He’s going to run out and check it. During our conversation it got back down to 1001#. I did receive a station alarm. He’s going to go out. Moore |
| --- | --- | --- |
| 1818 | Stevens Co. 2 | AC power failure – The station is down, no flow. Mike Zielke called in. I advised him that all of the units that were on, 6, 7, 8, 9, 10 and 11 are down. Unit 3 was not on. Barnes |
| 1828 | Hugoton | Unit 5 and unit 3 down. I advised Danny. Barnes |
| 1901 | Hugoton | Unit 4 down. Barnes |
| 1910 | LaPlata | The discharge jumped up to 1018# again. It’s bouncing around. I got a hold of David again. He is back on site there. I think he’s called someone else out. They are going to check that unit out and see what’s causing that pressure to jump around like that. Moore |
| 1918 | Stevens Co. 2 | AC power back on, alarm cleared. Barnes |
| 1923 | Hugoton | Units 3, 4 and 5 on line. Barnes |
| 1948 | Stevens Co. 2 | Units 6, 7, 8 and 9 back on. Barnes |
| 2018 | Hugoton | Unit 3 back on. Barnes |
| 2018 | Stevens Co. 2 | Units 10 and 11 back on. Barnes |
| 1930 | Monument | I received an alarm on unit 1. The units are down. I got a hold of Randy and talked to him about it. He’s going to make a call. He said he may go out but he’s going to talk to someone about it because it may be able to wait until morning. He’ll let me know. Moore |
| 1933 | Dagger Draw | Received a call from John out there. He let me know that our valve shut and we lost flow which that did happen. I made a call out and talked to Carl on the Artesia team. We did lose Atoka 3 after that. Carl has made it to Atoka 3 and Terry is headed to Dagger Draw. Moore |
| 2044 | Dagger Draw | It is flowing again. At Atoka 3, unit 761 is back on line. Moore |
| 2034 | Stevens Co. 2 | Units 6 and 9 down again. Barnes |
| 2047 | Stevens Co. 2 | Units 6 and 9 back on. Barnes |
| 2124 | LaPlata | Received a call from David. He let me know that they rescaled the transmitter there and they pulled a lightning transmitter. He said right now everything is running pretty steady. We are hitting right at 1008 on discharge but he said it’s running steady. It looks like everything is OK at the time and to give him a call if we have anymore problems. He doesn’t believe that we were actually getting 1040 or 1016 discharge pressures that were coming in here earlier. He said through the night as it cools off the discharge should come down as things speed up. Moore |
| 2125 | PNM Rio Puerco | We are flowing at that point finally. At this time we need to be doing about 60 there to make rate for the day. We are doing about 52 and it’s coming up. Moore |
| 2200 | PNM Rio Puerco | We lost flow there again. With their big unit on they were sending up 100 million, it jumped up. Our valve ended up shutting in again so I’ve got OCC trying to get a hold of someone to get them to go back out and get this valve opened back up. I’m not having any luck here. Moore |
| 0137 | Meridian | I called there and talked to Mary. The CO2 has come up to 2.1. She is going to cut some gas. Moore |
| 0053 | Sublette | Unit 23 down. Steve the on call operator called in to confirm it and will attempt to restart. Barnes |
| 0133 | Stevens Co. 2 | Unit 10 down. Mike is in route to the location. Barnes |
| 0150 | Sublette | Unit 23 is down on low suction pressure from Oneok. Steve who is out the Sublette station has paged Oneok with no answer. Unit 23 is now in remote start and we’re waiting for more pressure. Barnes |
| 0222 | Sublette | Haskell field pressure is 157 and unit 23 is on by remote start. Barnes |
| 0228 | Stevens Co. 6 | Unit 5 down. Mike Zielke who is still at Stevens Co. 2 with unit 10 that is down, he said he’ll leave Stevens 6, unit 5 down until morning. It looks like the volume impact is negligible at this time. Barnes |
| 0302 | Station 2 | Unit 10 will remain down due to an electrical start malfunction. The volume with unit down is 18.5, averaging 19.5 and the nom is 19. Barnes |
| 0236 | Ellis Co. 1 | Unit 2 has gone down. Contacted OCC and spoke with Steve Ridenour. He is going to be going out to check on this unit. Alvarado |
| 0359 | Ellis Co. 1 | Unit #2 is back on. Alvarado |
| 0408 | Ellis Co. 1 | Unit 2 has gone back down. Steve Ridenour is turning back around to head back to the station. Alvarado |
| 0459 | Ellis Co. 1 | Unit #2 is back on. Steve said he’s going to hang around the station and make sure that this unit stays on. He is having some problems with it. Alvarado |

slb