Services provided by Northern Natural Gas

And Transwestern Pipeline Company

- Enron Transportation Services

- Gas Control Event Log

0630 to 1830 Shift Mon., Jan. 21, 2002  (Hall, Barry, Braswell, Armitage)

| 0620 | Ogden | Just got a call from Jerry. He put 11 on because he couldn’t get 13 to clear. He is going to go home for a couple of hours and then he’ll call somebody out and have them get 13 back up. Hall |
| --- | --- | --- |
| 0846 | Station 9 | Lost unit 4. Called the OCC for the on call. Braswell |
| 0944 | NNG Estes | AC power failure – called the OCC for the on call. Braswell |
| 1125 | Spraberry | Unit #5 is down due to hot valves. They are in the process of changing them out. They are going to bring them back up on line once they finish. Barry |
| 1157 |  | Ken Poole informed me that the Walton tower is not communicating. At this time I called the OCC and requested the on call for the Kermit team. Darrel Mason called in. Darrel said he will check it out. Barry |
| 1020 | Farmington | Called the OCC. They got a hold of the on call. Asked him about the auxiliary generator. He said it’s supposed to come on on Monday. That’s the normal thing for it. At the same time I saw Guthrie Center’s generator come on too but it went off then about 5 minutes after it came on so evidently they must have had a little spike up there. Both of them have cleared now. Hall |
| 1200 | North Branch | Got a call from Jim the on call person. He said he needed to take #2 unit down and fix it. It has an oil leak. He said it probably be down 30 minutes to an hour or so. Hall |
| 1000 | Cunningham | Issued Cunningham an order to go up to 250 withdrawal. Armitage |
| 1245 | Cunningham | Issued Cunningham an order to go to 300. This is all due to central line pack is not recovering. We are actually pulling more gas through Clifton than the central zone has got in it. We are trying to catch the central zone. Armitage |
| 1335 | Oakland | Called the OCC and got a hold of the on call person. Asked for another unit out there. Joyce is going to see if she can get a hold of somebody else possible to go out and put it on. She said she’s quite a ways from there and it might be two hours before she could get over there to put them on. Hall |
| 1325 | Western Gas Midkif | I noticed that Western Gas Midkif flow rate had dropped down to 15 million from 45 scheduled. I called out to the plant and was not able to get a hold of anyone. It seems evident that they’re probably having problems at their station at this time. I did leave a message for them to call me back. Barry |
| 1422 | Oakland | Just got a call from Mike. He’s got the third unit on for us. Hall |
| 1425 | Western Gas Midkif | Manuel called in and said they had an ESD out there. They are just now trying to get their station back up. Barry |
| 1550 | Monument | Unit 2 alarm – called the OCC for the on call. Got a call back from Ernest. Told him what I had over there. He said he will probably leave that down until tomorrow morning. As long as it wasn’t a station alarm it shouldn’t be a problem. We don’t have anything right now running over at Monument so he’s going to leave it and clear it in the morning. Braswell |
| 1625 | WFS Milagro | Talked to Terry and Mike there. They were saying earlier this morning that they were having problems with freeze-offs and all kind of things going on there. They had a train that was down and they still have a train down. They haven’t really been making rate all day. They finally got some of the stuff unfrozen and their rate is starting to come up but it’s still not close to where they need to be. At Milagro they are scheduled do about 313, spotting right now 281.5 MMBtu. He did say they are still working on the problem and asked me if I had some room up at Ignacio, if I could take some extra up there. I told him at this time I could possibly squeeze 5 in there but that’s about it because I didn’t want my discharge to get up too high. Right now I’ve got 990 discharge at that point. He did say that they are expecting to come back on or at least to give us some more gas at Milagro sometime about 10:00 tonight our time and that everything should be up and ready and running there. When they do get up they’ll probably have some pressure problems. Right now they’re having too much gas to be able to treat. They are backing up on pressures and stuff right now. They are trying to wait and get all of that settled down but about 10:00 tonight they should be up and running at Milagro, try to come in as close as they can to being on rate. Also in the meantime he said that they might also end up cutting some gas on the next cycle, put it close to what they feel like they can come in on at this late stage. Braswell |
| 1700 | TW Beaver | The H2O right now is 8.6. We’ve had some problems in this area before. We believe the water is coming in from above the Ivanhoe station. We’ve talked to the Beaver field team. They had some people out there yesterday checking that. He checked his H2O monitor and the water did come down. Didn’t have anymore problems with it and then it came back up today. Randy and them believe they did have a power failure yesterday, about 4 hours, up in that area. That could have been the cause whereas those dehys were affected. Now everything is back in service. They say the gas is coming from Oneok. Right now there’s just nothing they can do about it. We just wanted to make sure that the H2O readings are reading correctly out there. We’ll just have to keep an eye on that tonight and see what happens. If it still continues to read high tomorrow they will have to go out there and check it and do something. At this point right now we’re just monitoring that point and making sure that the H2O doesn’t get any higher than what it is right now. Earlier today it did go up some and then went back down and now it’s back up again. Braswell |

1830 to 0630 Shift Mon., Jan. 21, 2002  (Calhoun, Munson, Welsh, Cummings)

| 1801 | Atoka 1 | Compressor 794 down. Cummings |
| --- | --- | --- |
| 1915 | Cunningham | Due to a change in the plan for increased demand north through Clifton we’ve asked Cunningham to go from 300 order to a 375. Munson |
| 1945 | Cunningham | Due to a change in the plan numbers for increased demand going south through Beaver we’ve asked Cunningham to increase withdrawal from 375 to a 500. Munson |
| 2030 | Valero Spraberry | We lost unit 5 again this evening. It looks to me like the same problem, maybe a bearing sensor. They had to call for help. They said they’d be down approx. an hour. We called Valero and told them that we were shutting that in until they got it fixed. Then we would resume as soon as they got the unit back on. Welsh |
| 2100 | Cargray | They called and said they are experiencing an upset at the plant. They’ll be able to watch their H2O, oxygen and their BTU’s may increase a little bit. They will call as soon as they got it straightened out. Welsh |
| 2220 | Bushton | We’ve asked Dan at Bushton to bring on some HP on the “D” to “E” service to help pull down the pressure to help Cunningham increase their withdrawal flow. Dan said he had a 2000 unit that he could bring on that service and see if that would help us pull that pressure down far enough. If that doesn’t do it we’ll switch over. He can put on a 5500 instead of the 2000. Munson |
| 2320 | Lyons | Our flow showing up on the computer at Lyons has gone to zero. I called Dan at Bushton. He confirmed that the actual Lyons flow is OK, that we are still flowing 50-55 million out of there. As a matter of fact the flow reading that he reads off the RTU calculation is also on zero but the flow measurement shows that everything is OK. He said that there is obviously a problem with the RTU calculating process. He said he would have a tech look into it in the morning but he assured me that there is flow at Lyons even though we’re showing a zero up here. We are not able to inhibit this particular Lyons flow rate since it is calculated off the Bushton RTU. The readings for Lyons for gas day of 1/21 are going to be erroneous. Munson |
| 0058 | Valero Spraberry | Units 4 and 5 are back on. We went ahead and tried to deliver a little extra to Valero Spraberry. We’re able to get about 70 million through there, that’s about it. We need to do about 100 to come in even for what we lost the day before and this evening but we’re doing all we can. That’s about as much as we can get through there. We tried to do more and it backs off so we’re about where we can go, 67-70 million at this point. Welsh |
| 1815 | Galena | Put #2 on line. Our pressures were low out at LS Power. Calhoun |
| 2015 | Ogden | Swung all of 17 to the east to get the pressures back up going out on the east leg towards LS Power. Calhoun |
| 2230 | LS Power Whitewater | They were on their way down. They said they’d be back on about 4:30 in the morning. Calhoun |
| 2245 |  | I got a call from NBPL. They said that Joel was done testing. Calhoun |
| 2330 | Ogden | Shut #16 down. It was going east. I was starting to stack up out at Hubbard. Calhoun |
| 0140 | Hubbard | Lost the unit. Going to try to get it back on. Calhoun |
| 0142 | Galena | Shut unit #2 down. It was coming into alarm on minimum differential. Calhoun |
| 0144 | Guthrie | Shut the unit down. That’s because I was stacked up at Ogden and needed to get out from underneath at least until I could get Hubbard back on line. Calhoun |
| 0156 | Hubbard | Was able to get the unit reset and got it back on line. Calhoun |
| 0430 | LS Power Whitewater | Got a call from Tom. He said they were getting ready to come back on line. Calhoun |
| 0445 | Madison | They called in and wanted a flow rate change. Took them from 60 to 50. Calhoun |

slb