Services provided by Northern Natural Gas

And Transwestern Pipeline Company

- Enron Transportation Services

- Gas Control Event Log

0630 to 1830 Shift Thurs., Jan. 24, 2002  (Hall, Barry, Braswell, Armitage)

| 0550 | Harrisburg | Called OCC and they got a hold of Rick. Told him that our pressure at Brookings is down to 470. Our pressure at Harrisburg is down to 556. He said he’d do something when he gets out there. Hall |
| --- | --- | --- |
| 0712 | WT2 | Received a station ESD alarm, station alarm as well. Called the OCC for the on call. Braswell |
| 0752 |  | Warren from WFS called. They have lost flow at the LaMaquina point. They lost a heater out there. He doesn’t know at this time when they will be back and flowing again. They will keep us informed. Braswell |
| 0830 | Beatrice | Called the OCC. They got a hold of Ron. Asked him for a unit on the “D” line. At this time they’re balancing some units but they will put another one on as soon as they get through. Hall |
| 0850 |  | Called the OCC back and talked to Ron again. They are going to see if they can get the “E” line turbine on for us. Hall |
| 0840 | Palmyra | Called the OCC. They got a hold of the on call. Asked for another unit “CD” to “D”. Hall |
| 0905 | Pierz | Called the OCC because I put a 2.8 in there and the unit did not start. We finally got a 14# spread. Mitch is going to see if he can get it going. Hall |
| 0955 | Pierz | Just talked to Mitch. He said he couldn’t get it to go with laptop so he’s going to go out to Pierz. I also called NSP and talked to Gene. Let him know that it’s going to be awhile yet before we get the flow going at Pierz but we are going to bring it in there rather than moving it to Polk. Hall |
| 1146 | Atoka 3 | Unit 762 down. Called the OCC for the on call. Braswell |
| 1218 | WT2 | Received a station alarm and low air pressure alarm. Called the OCC for the on call. Braswell |
| 1550 | Pierz | Got a call from Mitch. He said the reason he couldn’t get Pierz to go for awhile is it had a bearing temp that was showing a false high temperature reading. He got it on and he got the tubing fixed also that they were having a problem with. Hall |
| 1435 |  | Robert Baker called and relayed information about the Valero Pecos point. He informed me that the point right now is available but not as a bi-directional point. It can only flow right now from TW to Valero. Until El Paso decides what they want to do with the other run it’s only just one direction. Braswell |
| 1725 | Wrenshall | Just got a call from the operator. He said they’ve had a partial ESD. He requested that we have OCC page the people for Wrenshall and have them go out. He needs some help getting the plant back on. Hall |
| 1725 | OCC | Called the OCC and talked to Don. Passed on the information from the operator at Wrenshall. He is supposed to be paging the people for Wrenshall to go out and help the operator get the plant all situated. Hall |
| 1725 |  | Randy called from WT1. They’ve been working on unit 102. They are changing out GTO’s and the VFD (variable frequency drive). The unit will be available tomorrow evening. Braswell |

1830 to 0630 Shift Thurs., Jan. 24, 2002  (Barnes, Moore, Coash, Cochran, Alvarado)

| 1930 | Texas Co. 1 | Just had a full blown ESD out there and of course units 2 and 3 are down along with it. Got a hold of Dee Chapman. He’s headed out there to take care of it. Cochran |
| --- | --- | --- |
| 2005 | Sublette | Lost unit #21. Mike Burnam is going out to see what the problem is. Cochran |
| 2025 | Cunningham | Just requested they go from max withdrawal down to 300 withdrawal. Presently doing 417. Cochran |
| 2025 | Bushton | Just requested they take the turbine down going “E” to “E”. Cochran |
| 2043 | Station 4 | Requested a third unit on, unit #2. Barnes |
| 2101 | Station 4 | Unit 2 on as requested. Barnes |
| 2134 | TransColorado | POI 500632 – It is zero flow rate. They have compressors down. The nom is 98.507. I spoke with Randy with Kinder Morgan gas control at 2000 to discuss the pressure drop on his pipeline. He had lost communication with the downed compressor. He then at that time was going to dispatch a station operator. I advised Bloomfield operator Brian Dils and Randy with Kinder Morgan that I have a zero setpoint in place at this time until I see pressure enough to constitute a flow. Barnes |
| 2228 | TransColorado | Pressure is building and flow rate returning. Barnes |
| 2259 | Station 9 | Unit 4 alarm – advised Bob Powell the on call operator. Barnes |
| 0010 | GPM Linam Ranch | I contacted GPM Linam Ranch control room and spoke with Tom. Advised him that they had reached their nom for today. They had a nom of 11.3. I advised him to go ahead and shut it down. He advised me that their new nom was starting at midnight. I advised that they had already accumed their nom for the day and that our gas days run from 9:00 to 9:00. Also him that if he was going to continue flowing to me that it was going to cut into their new nom and that I would eventually have to cut him off sometime this morning when they accumulate their 15.7 nomination for the new gas day. They have cut the flow rate from around 20 to about 10.3. The reason we were flowing 20 is because we have a low/low differential alarm that comes into alarm status when they flow in the low nominations. We were trying to get them to accum their nom so that we could shut them in. At this time they are still flowing to us. If they continue flowing to us we’ll go ahead and take their gas. Whenever they accum their new nom of 15.7 we’ll just have to cut them off. Alvarado |
| 0029 | Kermit | Unit #2 has gone down at Kermit. Contacted OCC and spoke with Shane. Shane is going to be going out to put this unit back on. I’ve also notified Sid Richardson over at their Jal plant. Advised them that we had lost the Kermit turbine which pulls gas around from the Jal units into Kermit. I advised him that if Shane didn’t get the unit on quick enough we might lose the Jal units on high discharge. I’m just making him aware of it. Alvarado |
| 0045 | Station 9 | Unit 4 alarm cleared. It was due to a high exhaust temperature. Barnes |
| 0109 | Jal | Units 1 and 2 have gone down. I’ve contacted OCC and spoke with Russell. He’s going to be going out to put these units back on. These units went down due to Kermit being down. I’ve also contacted Sid Richardson again. Alvarado |
| 0209 | Jal | Unit #1 is back on. Alvarado |
| 0239 | Kermit | Unit #2 is back on. Alvarado |
| 0339 | Skellytown | I received an AC power failure for Skellytown and McConnell. I contacted OCC and spoke with Tony Teakell from Pampa team. He said he will check it out in the morning. Alvarado |
| 0425 | MidAmerican | It looks like they are running short at Quad Cities and Cedar Rapids, running well below their allotted. They said they were going to take some of that gas to storage on their final run. Coash |
| 0430 | WT2 | Unit 2 down. Advised Joey Green. Barnes |
| 0433 | Skellytown & McConnell | AC power failure alarm is back in normal status. Alvarado |
|  | Note | Agave Bitter Lakes receipt POI 500239, flow measurement is still out of service. Bob Powell said that it needed parts and he will be repairing it later this morning. Also Oneok Ward delivery POI 500168, flow measurement as compared to Oneok’s is drifting apart and that TW’s appears to be inaccurate. This has happened before and we’ll report it to a measurement tech this morning. Barnes |
| 0520 | Cunningham | Just gave them order to cut from 300 withdrawal down to 225. Cochran |

slb