Services provided by Northern Natural Gas

And Transwestern Pipeline Company

- Enron Transportation Services

- Gas Control Event Log

0630 to 1830 Shift Sun., Feb. 10, 2002  (Hall, Muntz, Braswell, Armitage)

| 0536 | Oakland | Called the OCC. They got a hold of Mike Gleaves the on call. I told him I had a low air pressure alarm. He said he would get it as soon as the sun comes up. I just got a call also from Jeff out there. He asked me if I had gotten a hold of anybody for that alarm. Told yes, I had just talked to Mike. Hall |
| --- | --- | --- |
| 0542 | Burdett | Have gotten an auxiliary generator alarm on the station. The generator is down but I have talked to Floyd about it. He is going to go out and check on it to see what might be causing the problem so we don’t have any problems with the generator if it happens to be needed. Armitage |
| 0639 | Palmyra | Just got a call again from Kramer. He said there was nothing to the 40% gas detection alarm that we got. Don’t know why it came in. He is also going to check to see if the “E” to “D” block is open. Hall |
| 0945 | Palmyra | Called the OCC because I got this gas detection 40% alarm again. They got a hold of Kramer. He said that he is not getting that alarm out so I gave it to Bob Hagen and he will check it out for us. Hall |
| 0953 | North Branch | Called OCC. They got a hold of the on call Mark on this Lake Elmo #1B. I got a call from NSP from Todd saying that his temperature was showing –6. At the time I was talking to him the first time it was showing 39.5 on our temperature. Our RTU is updated with the time of 9:30 and the date is 2/10 which what we’ve got showing here right now. Temperature now is showing 40.145. Mark said he wasn’t sure exactly how they get their information but it sounded like the problem is on their side. I called Todd back and passed the information on. He said they would probably get somebody out there to look at it tomorrow on their side. Hall |
| 1113 | Stevens Co. 1 | #7 is down. Have contacted the on call person. He is on his way over to Stevens 2 to put a unit on. Then he will go back by Stevens 1 and put this unit back on. Armitage |
| 1127 | Stevens 7 | Unit 1 is down. Have contacted the man who was going got Stevens 2. Told him once he got Stevens 2 on then he would have to go to Stevens 1 and then Stevens 7. Armitage |
| 1250 | NGPL | Just talked to Juan over there. Told him that we would be allocating Trailblazer down to 300 tomorrow because we haven’t been able to get much more than 315 in for the last couple of days. He is going to check on the outage and let me know as soon as he can on how they are coming with it. Hall |
| 1345 | Northrop | Touched base with Lupe out there. Just informed him that I had a high discharge H2O alarm there at the station earlier and that they were needing to check that out at that time, it was 16.1. He did call me back and check it out and said that there was some problems in the programming out there which was causing him not to be able to switch the dehy. There were two techs that were familiar with the programming and they weren’t available at this time. They will have to bring out their laptops and see if they can get the programming done. Since they weren’t available he would try to get a hold of them or the people he needed tomorrow morning to get that programming fixed and get the dehys switched around. Braswell |
| 1553 | Citizens Griffith | Dave called and informed us that they will be starting to pack their header in about an hour. He said they will be starting their auxiliary bore(?) and the around 2:00 a.m. they will be coming back on. Muntz |
| 1528 | Stevens 7 | Unit 1 is down. The men are still at the station trying to figure out the panel on this thing to try to get it back on line. Armitage |
| 1708 | Ellis Co. 1 | AC power failure and also AC power failures at Beaver Co. 6 and Ellis Co. 3. I called the OCC for the on call. Braswell |
| 1720 | Beaver Co. 1, 2, 11 NNG/TW Beaver | All of these points have AC power failure at this time. Also lost units 3 and 5 at Beaver Co. 1. Called the OCC for the on call. I also talked to Eddie for the TW/NNG Beaver point. They are going out and check it. They have some type of storm or something in these areas. Braswell |

1830 to 0630 Shift Sun., Feb. 10, 2002  (Moore, Cochran, Barnes, Coash, Alvarado)

| 1745 | Cunningham | I’ve given Cunningham an order of zero. Right now we have no demand for the gas. Alvarado |
| --- | --- | --- |
| 1752 | Clifton | Unit 31 – I’ve done a remote stop on this unit. No demand on this unit at this time. Alvarado |
| 1840 | Beaver Co. 1 & 2 | We lost power at both locations along with many other locations. Power is back up at Beaver Co. 2 though. Personnel are going out to both locations. They should be able to start getting the units back on at Beaver Co. 2. Cochran |
| 1900 | Station 7 | Received a call from Kevin out there. He did a manual ESD bypass. He wanted to check the fire eye problem that they’ve had. He did say that they are going to have to work on it tomorrow. If we have anymore alarms tonight we’re to give him a call. Moore |
| 2010 | Oneok Ward | Flow there went to zero. The block valve showed shutting in. I called. They said their controller shut but they got it right back open. Moore |
| 2128 | LaPlata | Received a station alarm there. Got a hold of the on call Larry. He’s headed out. Moore |
| 2120 | SW Kansas Irrigators Northeast 1B | I received a low/low battery voltage alarm. I contacted OCC and spoke with Steve on the pipeline team. He advised me that this battery does not belong to us. It belongs to Southwest Irrigators. They will call in the morning and let them know. Alvarado |
| 2150 | LaPlata | Received a call back from Larry. He let me know that he’s got the alarms cleared there. It was due to a power failure but everything is good now. Moore |
| 2157 | Station 5 | Lost unit 3 there due to high temp on the discharge. I talked with Charlie. He said we’re just going to have to leave it down for awhile. We don’t have enough gas to run that unit. It’s recycling too much. I told him we’d probably have to put it back on later. Moore |
| 2245 | NWPL LaPlata | Received an alarm in here. My pressure had dropped about 10#. I’m showing at this time it’s dropped about 15-20# overall. I made a call out to NWPL to find out if they had any problems, if they were seeing that drop. He said he opened up a recycle out there because his pressure was getting high. That was the reason for the drop in the pressure. Moore |
| 2250 | P1 | Received a control panel unit alarm there. I talked with James. He is going to go out and clear that. He said that’s a problem that they’ve been having, possibly with the control panel there. They are still trying to figure out what’s causing that. He is going to go out and clear it. Moore |
| 2300 | Clark Co. 1 | I lost unit #1. Personnel is headed out there to see about getting the unit back on. Cochran |
| 2328 | Station 7 | Received a station malfunction alarm. I got a hold of Brent. He went out and cleared it. It’s due to the problem with the fire eye again. Again, he did say that they are going to look at that tomorrow. Moore |
| 0145 | Kermit | Lost the turbine. Clitus is headed out there to try to figure out what the problem is. Cochran |
| 0145 | Atoka 3 | Unit 842 went down. Got a hold of Armando. He is going out. Moore |
| 0150 | Oasis | Made a call over there and talked with Amy. I asked her if maybe they could take about 20 at block 16 for the remainder of the gas day and just allow that gas to go towards the OBA. I’m showing we owe them about 66.879 and at that flow rate for the remainder of the gas day we’ll accum between 6 and 6.5 on the MMBtu. She said that she would. She is going to open that up. This is to help relieve some pressures off of station 9. Moore |
| 0147 | Tate | All units are down at this time. I’ve contacted OCC and spoke with Dave Farris. He’s going to be going out to put these units back on. Alvarado |
| 0200 | Atoka 3 | Armando called me back. He let me know that there was freeze up out there on unit 842. He is going to shut both the suction and discharge, going to blow it down. They will get to it first thing this morning or let it thaw out and then they will get the unit back on line first thing this morning. Moore |
| 0405 | Station 7 | Received a station alarm malfunction. Got a hold of Keith. He’s on site. He is going to take care of that. I asked him to go ahead and put a unit on at 7 to pull away the pressure from station 9. Moore |
| 0405 | Tate | Units 4, 10 and 11 are back on. Alvarado |
| 0405 | Cunningham | I’ve given Cunningham an order for 100 withdrawal at this time. We’ve also put the Clifton unit back on, unit #31. Alvarado |
| 0425 | Kermit | Got the #1 turbine back on. It had an oil line leak and it drained all of the oil out of the unit. They got the leak fixed and the unit back on line. Cochran |
| 0425 | Burdett | Unit 3 went down at 0412. I contacted OCC and spoke with the on call. He is going to be going out to check on unit 3 but in the meantime he told me to go ahead and do a remote start on unit 4 which I have done and it’s coming on line. Alvarado |
| 0426 | Tate | Units 5, 6 and 14 are back on. Alvarado |
| 0538 | Stevens Co. 2 | Unit 6 has gone down. The Stevens on call called in and said that they were going to wait until they get to work this morning and put that unit back on. Alvarado |

slb