Services provided by Northern Natural Gas

And Transwestern Pipeline Company

- Enron Transportation Services

- Gas Control Event Log

0630 to 1830 Shift Mon., Jan. 7, 2002  (Munson, Calhoun, Welsh, Cummings)

| 0708 | WT2 | Unit #3 has gone down. I notified the OCC. Munson |
| --- | --- | --- |
| 0731 | WT2 | I just spoke with Shane through the OCC to let him know that he has some HP down at WT2. He is now headed that way. Munson |
| 0840 | WT2 | Shane has unit #1 on in place of unit #3. Munson |
| 0725 | Macksville | Got a hold of Darrel. Asked him to put units 2 and 3 on the high side on line. That’s due to picking up the Clifton flow from about 1200 to about 1375. Calhoun |
| 0730 | Cunningham | Called Gloria and gave her an increase in the rate, going from 400 to 575. We’re picking up our Clifton flow rate. Calhoun |
| 0742 | Stevens Co. 2 | They put unit #11 back on. It had gone down earlier in the night. Calhoun |
| 0810 | KP&L Mullinville | I talked to Mel their gas controller. We’ve had the point shut in for the last few days. I’ve also called Chris the scheduler and found out that we’ve got almost an 8 million imbalance to us, receipt gas. So we’re going to bring it on line, flowing about 8 million today to clean up the imbalance. Calhoun |
| 1020 | WT2 | Called the station and talked with Clitus. I requested that they either increase the torque and the load on the #1 unit enough to get us on rate with all of our customers and increase the throughput through the station or else put on an additional unit to help us make our rates. We are not able to make up the line pack we lost earlier from them being down and we are having trouble making all of our flow rates. Munson |
| 1030 | Tate | Got a high level on the H2O. I called Jeff at the Tate station. He said they were adding glycol to the dehy and that is why it came up. He said that the glycol was saturated with water and that’s what they had put in it. It’s going to take it awhile for it to cook it back out. He said it should start coming down through the morning or early afternoon. Calhoun |
| 0908 | Tescott | Unit #5 went down. They got it back on at 0940. Calhoun |
| 1038 | Mullinville | Got a pig in on the Texas “A” line. Got high scrubber levels on moisture so it knocked all of the units down on the Texas “A”. As soon as he got all of the scrubbers dumped and the water out of there they were going to put the units back on. Calhoun |
| 1155 | Follett TBS | I noticed that the pressure on the low side of the TBS seems to be dropping at a very slow rate. This could be the sign of a possible freeze problem. I notified Stanley. He said he would pass it on to one of his team members who is a little bit closer to that station. Munson |
| 1159 | P3 | The team at P3 has made a swap at our request. They’ve taken down units 2 and 4 and put on the much larger unit #5 to help us maintain our proper flow rates on the Panhandle. Munson |
| 1202 | WT2 | WT2 staff have put on unit #2 as requested earlier in order to help maintain our delivery flow rates. Munson |
| 1235 | WT2 | At approx. 1220 Shane lost both units at WT2. He just touched base with me and said at this time he is bringing them both back on line. We don’t show RPM’s at this very moment but he is in the process of bring them back on. He had to go out and check yard valves. He had a false indication on a valve position. Once he got the cleared up he would be able to bring the units back on. Munson |
| 1125 | Mullinville | They got their units back up on the Texas “A” line. Calhoun |
| 1249 | WT2 | Shane has the HP back on line. Munson |
| 1249 |  | I received a call back from Randy regarding the Follett TBS. Randy Kliewer said that he went by there and checked into it. He believes that the drop in pressure is being caused by increased usage at the town and that there is no freeze problem at this time. We’ll continue to monitor this pressure very closely. Munson |
| 1355 | Station 1 | We’re showing a unit alarm, a station alarm and an LEL alarm at station 1 even though there is no HP on line. I called out to the station to confirm that someone is indeed on site and aware of these alarms. I touched base with Sonny. He said that they are going to clear the alarms as soon as they are through working on some of their valving. Munson |
| 1355 |  | I have touched base with Oneok. It seems that they are still having problems with their delmar at the Ward location. We’re not able to flow our gas for today at that point. If they can get their delmar problem fixed we can accum that gas, it’s a fairly low amount, on the nom so we can probably still make the gas rates up for the day. I have touched base with Oneok and they are working on it. Munson |
| 1355 | Finney Co. 2 | Got a high moisture level alarm at 6#. I called and talked to Jay who went out to check the dehy. They found an electric motor that had gone bad. They are not able to circulate as much glycol over the cooling towers so the temperature of the glycol is running hotter than normal. He said they won’t be able to get it changed out or fixed until tomorrow. He’s also hoping that when the sun goes down and the ambient temperatures cool off that the high moisture level will fall off overnight and hopefully they can get it repaired tomorrow. Calhoun |
| 1445 | Morton Co. 6 | They lost unit #2. I got a hold of Doug Toombs. He also said he was going to take unit #1 down. He had hot valves. He got them put back up at 1600. Calhoun |
| 1610 | Stevens Co. 6 | Unit #4 went down. Got a hold of Tom Bromwell. He was going out to put it back on. Calhoun |
| 1605 | WT2 | Shane called to say they are having some more problems with unit #1. They now have a crack in a weld on one of the headers and they are going to have to take a unit down. He’s going to try to put #3 unit on to take its place however he’s not sure if the repairs have been finished on #3. It seems that earlier today they were having problems with the starter on #3 and that’s why they could give that one to us and had to switch over to 1 to begin with. He is going to try to get #3 on shortly. Munson |
| 1640 | SoCal Needles | We show an intruder alarm at the Needles station. I notified Randy through the OCC. Munson |

1830 to 0630 Shift Mon., Jan. 7, 2002  (Monden, Hall, Ellington, Braswell)

| 1845 | Palmyra | Called the OCC. They got a hold of the on call Bob. He’s going to go out and see what happened to 19 and see if he can get it back on for us. Hall |
| --- | --- | --- |
| 1900 | JL Davis | I just got a call from Larry on the Big Lake team. Before I came in tonight Ed had him looking into H2S alarm at the JL Davis Rocker plant. He said that we are getting some H2S there. It’s spiking and then going back to normal. He said the reason why it’s happening is JL Davis is bypassing their processing plant and giving us some very rich gas which is not real good for us. He has made contact with one of their technicians to go out and see if they can trim this back. In the meantime we’ve got about 35 million coming in at Conoco Mertzon. Then we’ve got about 15 million going out at WTU San Angelo. We’ve got about 20 million in the pipe coming up the 16 that we can commingle that JL Davis with. As far as contaminating our we shouldn’t be in a problem there however that’s going to be really hot gas. That’s not real good for our pipeline. He said that he was going to take control of that in the morning and get with the appropriate people to try to get them to either process it or trim this flow back. Ellington |
| 1944 | Palmyra | Just got a call from Bob. He’s got 19 going again. He said it could go down again. He didn’t really find anything wrong with it. He said it could be a fuel valve shutting down on it. He’ll see if they can’t get it replaced tomorrow but he wasn’t sure if that’s what wrong with it but anyhow he’s got it going. He said if it does go down again to give him a call. Hall |
| 2100 | Quad Cities | Called the OCC. They got a hold of Kurt Ritter for me. He’s the one who takes care of that point. Just let him know that for some reason the part where we piggyback off of MidAmerican’s equipment out there is not responding but our check meter is working and it is communicating. The other one quite about 12:30 this afternoon. He said he would swing by there tomorrow and look at it. Hall |
| 2302 | Palmyra | Just got a call from Bob. He said that the problem with 19 is in the fuel valve in the program of it. They’ll get it changed out first thing in the morning. We’re not going to lose that much volume or anything with it being down. Pressure is really not climbing that much. We’ve only got 519 right now and they’re still better than 200# spread on the units that are on. Hall |
| 2325 | Farmington | Lost #4 unit. Called the OCC and they got a hold of Bob Tornio the on call. Told him that I had talked to Mike Schneider earlier and he said that if 4 should go down and I wanted something else on that 5 was available, just go ahead and put a start into it. It looks like it is coming on fine. I told Bob it was fine, just go ahead and leave #4 down. He said if anything happened just to give them a call and they’d go out to get it ready and get it back on. Hall |
| 2328 | Sioux Falls Pooling Point | The temperature being low is because of the way that the pipe is set up. There is no flow through it. Talked to Darrel Belt. The OCC got him for me. He said that everything is fine. Hall |
| 0040 | Waterloo | Called to OCC because I lost #6. They got a hold of the on call Larry. Told him that the way things are looking we’re covering pretty good out there on the east leg. Got 531 and 851 at Earlville. The suction was pretty low at Waterloo anyhow. As long as I don’t lose #5 there at Waterloo we should be OK and we’ll just go ahead and leave #6 down. He said they would check it out first thing in the morning. Hall |
| 0145 | Sublette | Unit 21 has gone down. Notified OCC. They got a hold of Rick Titus. He’s going to get it checked out to see if Oneok has got a problem or it’s the unit. Monden |
| 0228 | LaPlata | Lost unit 2. Called the OCC for the on call. Braswell |
| 0347 | Sublette | Unit 21 back on line at 3:00. Rick Titus had gone out. Monden |
| 0350 | Beaver Co. 2 | Unit 5 and 6 down. Notified OCC. Stanley called in. He said that there was a pig coming in so it’s probably there and it shut those units down. He said he would take care of it. Ellington |
| 0512 | Earlville | Called the OCC. They got a hold of Larry the on call. Passed on to him that for some reason his generators came on out there. He said he would be there about 0615 and would check it out to see if it’s still on or not and take care of it for us. Hall |
| 0518 | Beaver Co. 2 | Beaver Co. 2 is back on the line. Ellington |
| 0530 | Seminole | Seminole is still down. They’ve been trying to get it on all night. They’ve been calling me about every hour saying that they were trying to make it go but nothing happens. Kermit #2 is still on. We’re pretty low on our deliveries in the subsystem. Kermit #1 has to be monitored all night as well. It’s got a problem with it that it can’t be left alone. Talked to Jim Myers several times during the night. He assured me that they were trying to get Seminole fixed and running but just not sure a this time what’s causing the problem they are having. Ellington |

slb