Services provided by Northern Natural Gas

And Transwestern Pipeline Company

- Enron Transportation Services

- Gas Control Event Log

0630 to 1830 Shift Sun., Jan. 6, 2002  (Henley, Spain, Monden, Hardy, Muntz)

| 0620 | Oasis | Bruce called and said that they were showing high H2S readings out at Oasis Waha delivery point. We show no H2S readings in here. The valve has closed in the flow but he’s going to send somebody out to look at it, check it out and open it back up for us. Hardy |
| --- | --- | --- |
| 0649 | TW Beaver | Talked to Eddie Pool. Told him about the problem out there with high flow with the valve closed. He thinks that there was probably just a differential transmitter that froze up. He’s going to head out there to meet Stan and fix it for us. Hardy |
| 0805 | Eagle Interconnect | Don Soppe called in and said that he had a main sense rotor failure. It will take about an hour to repair. Monden |
| 0905 | Linam Ranch | The operator called. They lost an inlet turbine. Flow rate is down to 24. It will be down for awhile until they can get it back on he said. Hardy |
| 0940 | Mt. Hope TBS | Steve in OCC called in and said that they had a relief valve opening up at this TBS. He had notified Dave Batie to get it checked out. Monden |
| 1020 | Owatonna | Put the unit on line. Monden |
| 1044 | Ogden | Stacey called in. He said they’ve got their auxiliary unit back off and they are back on purchase power. The power company had to replace a transformer. Monden |
| 1100 | Alexandria | Put the unit on line to help build the pressure out towards Benson. Monden |
| 1100 | Eagle | Don Soppe has completed the work on the interconnect and it is now operating correctly on the measurement. Monden |
| 1100 | Clifton | Added unit 31 on the “E” line. Henley |
| 1108 | Mapco Whiting | Darrel from the South Sioux team called in. He said that the charging unit is bad at the interconnect. Tomorrow he will have to put a recording unit on at the interconnect because we probably won’t have live scada coming in until he can get the charger fixed. Until that time he feels like the battery will hold up until he can get a recording unit on. Monden |
| 1118 | Mt. Hope TBS | Spoke with Steve in OCC about the call we got earlier about the relief. He said he had spoke with Dave Batie and they didn’t have any gas blowing at the time of their arrival but were talking to the lady that called it in. Monden |
| 1131 | Mt. Vernon & Mechanicsville | Waterloo field team, spoke with Rick Dorsey about low voltages at these interconnects. He said that they were having Bristol problems on the number of times of polling during the day. It’s running the battery down on charge capacity which is lowering the voltage. Monden |
| 1210 | Guthrie Center | The unit is on line. Monden |
| 1223 | North Branch | Put unit #3 on in service code 4, cracking west, suction from the south, discharging north. Monden |
| 1230 | Farmington | Got unit #6 on line after trying to start it earlier at 10:42 and not coming on. About 20-30 minutes tried to start #5 and it didn’t come up on line. We called the Farmington team. Scott called back. He checked it out from his computer and got #6 reset and we’ve got it on line now. Monden |
| 1400 | Minnegasco | Medford Storage – They would like to withdraw 49 million. I cut back on the regulator at Ventura and brought unit #6 on the “A” line at Farmington pumping to the “BC”. Monden |
| 1418 | Terra Chemical | Scada has gone out, it’s in history. Had George Margoliner check it out. He said it was out there at the site. I’m going to call OCC to get the on call person, it was Clark Matzon. He is going to Darrel Belt on his team to give me a call about the interconnect. Monden |
| 1538 | Terra Chemical | Darrel called in from the South Sioux team. He said he was going to have to get a trouble ticket on this. Will be able to investigate it further with all of the land lines that come in there that polls the information, it just keeps the MTU too busy. Monden |
| 1604 | Palmyra | T-control alarm, shut down alarm – Bob from Palmyra is going to check it out. Monden |
| 1638 | Atoka 3 | I just spoke with Armando about the H2S alarm at Atoka 3. I’m reading 0.163 on station H2S. It’s trending upward. Armando is going out to check it out. Muntz |

1830 to 0630 Shift Sun., Jan. 6, 2002  (Barry, Hall, Ellington, Braswell)

| 1913 | Oakland | Called the OCC. They got a hold of the on call Dana. He’s going out to put the “D’ line station on for me. Hall |
| --- | --- | --- |
| 1919 | Ogden | Called the OCC and they got a hold of the on call Stacey. I asked him about switching 13 from east to north. With the spread that we’ve got discharge-wise, he said it would be better to shut it off first. The other reason for the call was I tried putting 17 on and it went down. He’s going to go out and get it on for me, half of it going east and half of it going north. Hall |
| 1930 | Faribault | Called the OCC and they got a hold of Larry the on call. The reason for the call is I have a lube oil tank temp high/high, 164.7. When I called it was just a high alarm of 161. Larry said he would call VonRuden and see if there is anything to really worry about. Waiting for the call back from Jim. Hall |
| 1945 | Faribault | Just got a call from Jim. The oil temperature has cooled back down. He said that the fan takes a little bit sometimes to get caught up with the oil and everything and get it cooled back down once you get the unit going. It has cooled back down now and looks good. Hall |
| 1955 | Pierz | Called the OCC and they got a hold of the on call Tim. He’s going to call another guy. I told him that I had lost Pierz this morning early. The alarms are not clearing. With the pressures and all we should be able to free flow with the unit not being on anyhow. I gave it a setpoint of 10 and no response. He’s going to call Mitch or one of the other guys and see if they can figure out what’s with it and get it to free flow for us. Hall |
| 1900 |  | Called Doug at Cunningham. Requested him to bring withdrawal of 150. Barry |
| 2030 | Willmar | Just got a call from Mark. He tried to reset the Pierz location. He could not get it to respond. They will go out there first thing and check it out. He said for some reason it’s not responding, not communicating with his PC and everything. They will check it out first thing in the morning. Hall |
| 2042 | Oakland | Gave an order to Dana at Oakland for three units to be on the “D” line, for the “D” station to be on. Hall |
| 2150 | Beatrice | Called the OCC. They got a hold of Ron the on call. I asked him about which one they would prefer to have started to be added to the “D” line. He suggested 19. That was the most recent one on that had been taken off, fairly recent. I tried it and 19 came right on line. Hall |
| 2240 | Waterloo | Called the OCC. I was trying to put the station on. It looks like 1 may be running, 5 started to come on and isn’t, 7 started to come on and it went back down, 8 looks like it is on. Only two out of the four units that started to come on are on. Jim is going to go out and take a look at it for us. Hall |
| 2240 | Ogden | Called the OCC because 17 went down. Stacey is going to go out and put it back on. Hall |
| 2245 | Carlton | Called the OCC. They got a hold of the on call because it had a station remote alarm, ESD bypass alarm and ESD actuated alarm. They were only in alarm for one scan and then they turned normal. He said he might talk to Mike and see what he thinks about it and go from there. They may check it out tonight or leave it for first thing in the morning. The unit does seem to be running OK. Hall |
| 2300 |  | Called Cunningham and spoke with Doug. I requested to withdraw 250. This was an increase of 100 million. Barry |
| 2300 | Carlton | Got a call back from Vern. He said that since the unit is running fine they will check into that tomorrow morning. If we should get the alarms again then he will go out and check the printer and see if they are coming in out there as well. Hall |
| 2304 | Waterloo | Just got a call from a fellow out there. He’s going to see if he can get some of the units going for us. Told him the main thing was just enough on to pull a good spread for us this morning. Hall |
| 2309 | Ogden | Stacey just called in. He said 17 went down on crankcase pressure again. He said that it does that whenever it’s been down for awhile and you first start it up. He’s got it corrected now and the unit is back on. He said it shouldn’t go down on that again. If it goes down again it will be on something else. Hall |
| 0230 |  | Received a station H2S alarm at the Oneok Ward point. Randy called from Oneok soon after I received the alarm. He said that it is probably their H2S monitor. He said instead of calling someone out right now with no more than what they were flowing at this time of about 14 million they will get someone out in the morning to check the monitor out and be sure that it’s working properly. Braswell |
| 0328 | Hubbard | Called the OCC. They got a hold of Pierre the on call. Told him I have a substation common alarm at Hubbard. He said he would go out and check it out for us. Hall |
| 0341 | Beatrice | Got a hold of the OCC. They got a hold of Beatrice for me. Ron is going to try putting the two 4’s over on the “E” line and then we’ll put the rest of the 2’s on the “D” line with 19 and 20 and see how that works out for us. Also got a hold of Rodney up at Redfield and gave him a 400 order. He said it would be a little bit. He’s got to get another fellow out to help him out with it. Hall |
| 0406 | Hubbard | Just got a call from Pierre. He said he’s about an hour away from the station. He is going to check out the substation common alarm there. Hall |
| 0412 | Beatrice | Got a call from Ron. He’s ready to start switching the HP. Hall |
| 0420 | Beaver Co. 12 | Unit 4 is down. Stanley called in to say he is on his way out. Ellington |
| 0307 | Stevens Co. 2 | Unit 11 went down. After speaking with field personnel they said they were going to leave it down tonight. They had some gas off in the field. They said it’s down on low suction pressure. Barry |
| 0507 | Quad Cities | I had called for the on call. They called back in, talked to him as well as Kurt Ritter. Kurt said that the equipment that is failing out there at Quad Cities belongs to MidAmerican because our check meters are still working. I just called Bob back with MidAmerican and passed that information on to him. He’s going to get somebody called out on his side. I told him if he needed any flow rates or anything later to give us a call because we do still have them and we have the accumulated totals. Hall |
| 0505 | Hubbard | Got a call back from Pierre. He said it was just a little glitch out there and nothing to really worry about there at Hubbard and everything is fine. Hall |
|  | Tescott | At about 1:30 this morning I brought on the turbine, unit 5 on the “E” line. Also after that at Clifton I brought on a recip along with the turbine on the “E” line. Barry |
| 0330 | Cunningham | I issued a new order to increase up to 400. Barry |
| 0513 | Waterloo | Called the OCC. They got a hold of the on call. I told him that I just lost #6. I had lost 5 shortly after he left but I was doing fine as long as 6 was still on. It’s gone down now so I don’t have enough spread on the units. I’m down to less than 80#. He will go out and take a look at it and see if he can get us going again. Hall |

slb