Services provided by Northern Natural Gas

And Transwestern Pipeline Company

- Enron Transportation Services

- Gas Control Event Log

0630 to 1830 Shift Sat., Jan. 19, 2002  (Cochran, Barnes, Coash, Alvarado, Moore)

| 0550 | Station 5 | Received a station alarm and a BSD alarm. Got a hold of the on call. Eugene is headed out. Moore |
| --- | --- | --- |
| 0553 | Bloomfield | I received a unit 4 alarm and a station alarm there. I got a hold of Blackie the on call. He’s headed out. Moore |
| 0630 | Gallup | I received a unit alarm there. I talked with Pat. He’s going to go out and check it. He said it’s probably due to low surge margin, down to about 18. More |
| 0637 | Station 5 | Received a call back from Eugene. He let me know that the alarm there is on a valve position alarm on valve #5006 which is the mainline. He said there is no problems there. This is due to a wiring problem. They do have an outage scheduled for Tuesday and he’s going to make note to get that fixed. We will see the alarm until that time. He did say if we needed the unit before they get this repaired that they would have to go out and do it before so. Moore |
| 0810 | Redfield | I just gave them an order to go from 375 down to 325. Also visited with Jerry at Ogden. Going to drop one of the horizontals going from Redfield to the “D” north. Cochran |
| 0810 | Sublette | ESD pressure is 139, down from 148# at 0300. Advised the on call operator and he will check for possible freezes at the station and the ESD system. Barnes |
| 0806 | WT2 | Unit 201 down. Got a hold of John. He’s headed out. We did talk about it with the deliveries south of WT2 dropping off from 210 to 180. We’re just going to leave that unit down and make the deliveries with unit 3. We’ll torque it out. Moore |
| 1010 | WFS | Received a call from Mike. He asked me to put a zero setpoint in at LaMaquina. They are still having problems there. It had been flowing about 4-5 million but it looks like it may be unprocessed so we had to shut that in there. We’re trying to do a little more at Milagro. To get closer on rate. It may be several hours before they get LaMaquina back on. Moore |
| 1003 | Red Cedar | The CO2 came up there, showing about 3.1. I made a call and talked with Jack and let him know. He said he would get that down. Moore |
| 1028 | Station 2 | Received a station alarm there earlier. Wayne went out and got that cleared. He decided he needed to go ahead and take unit 1 down to change filters because of the high differential. He said it would be down for about ½ hour. Moore |
| 1122 | Clifton | Unit 29 down, no demand, by remote stop. Barnes |
| 1130 | Cunningham | Order changed from 500 withdrawal to 300 withdrawal. Spot flow is 455. Barnes |
| 1140 | Ogden | Just had Jerry shut down the other horizontal going “BC” to “D” north, no demand. Cochran |
| 1145 | Ventura | Dropped unit #11, no demand. Cochran |
| 1200 | Ventura | Dropped unit #12, no demand. Cochran |
| 1210 | Ventura | Dropped units #13 and #15, no demand. We’ll now bypass the station. Cochran |
| 1230 | Minnegasco | I just received a call from Danny. They are cutting the Grundy receipt which is 28.9 million. I visited with Jodi at NBPL and we went ahead and made the 30 million cut at Ventura to come in on rate for the day. Cochran |
| 1320 | Station 5 | Had Eugene open up the mainline block valve there. The station was bypassed. In opening that block valve 5006 it cleared the alarms that we had gotten earlier. Moore |
| 1340 | Station 7 | Had OCC get the on call person Norm. Told him that I want to put a unit on at 7 to pull away pressure from 9. I’m up to 1006 on the discharge and the _______ line checks at about 1008. Moore |
| 1415 | Oakland | Just visited with personnel there. Requested they go ahead and shut the nine units down on the “BC” and go ahead and bypass. Cochran |
| 1448 | Bushton | Turbine unit #32 is down, no demand. I requested it down at 1220. Barnes |
| 1500 | Ogden | I just shut unit #13 down going “BC” to “D” north. Cochran |
| 1500 | Seminole | Seminole unit is back on. They took Seminole down at 0941 this morning to download a new program to the unit. I did lose a small amount of delivery to Norval but I’m going to be able to make it up. Alvarado |
| 1508 | Beaver Co. 5 | Unit #4 is back on. This unit went down last night. They elected to leave it down due to not enough gas out in the field so they let the field build back up. Now they are bringing it back on. Alvarado |
| 1510 | Faribault | Just shut the unit down, no demand. Cochran |
| 1510 | LaCrescent | Just shut the unit down no demand. Cochran |
| 1515 | Alexandria | Shut the unit down, no demand. Cochran |
| 1520 | Harrisburg | Visited with Rick who takes care of that. He is going to go back out there and put the Harrisburg regulator back in service. Aberdeen is starting to pressure out some due to the warmer weather. He is going to put the regulator back in service and take care of it. Cochran |
| 1535 | Ogden | Just shut unit #16 down going “BC” to the east, no demand. Cochran |
| 1540 | Seminole | Jerry is requesting me to go ahead and take Seminole back down. They’ve got to do one more minor program load to the unit and then they’ll be bringing it back on. Alvarado |
| 1620 | Guthrie | Just shut the unit down, no demand. Cochran |
| 1640 | Station 7 | Still don’t have that unit on line there. I made a call out and talked with Kevin. He said he tried to start one time but didn’t make it. He’s waiting on the air right now. He said he should be able to try again in 2-3 minutes. I let him know that my pressure at station 9 is 1008 discharge and I’m at 1010 on the mainline behind check at 9. Need it ASAP. Moore |
| 1655 | PNM Rio Puerco | I made over there and talked with Brent. Asked him if I could raise up at Rio Puerco and cut some at the hub to try and help relieve my pressures. We still haven’t got a unit on at 7. Moore |
| 1711 | Seminole | The Seminole unit is back on. Alvarado |
| 1711 | GPM Linam Ranch | I’ve contacted Ray Nosef to go out to Linam Ranch interconnect and shut down one of the meter runs. We do not have enough gas to run both runs at this time and it’s alarming on low differential pressure going across the two runs. Ray is going to go out and shut one of the runs in. I advised him that it looks like we have the same amount of nomination of 29.7 for tomorrow as well. The reason I didn’t send him out earlier is because GPM was over delivering to us and we were finally able to get them to come down to their nom for the day. We’ll be able to close that one run now. Alvarado |

1830 to 0630 Shift Sat., Jan. 19, 2002  (Calhoun, Munson, Welsh, Cummings)

| 1900 | Stevens Co. 6 | I received a high H2S alarm at Stevens 6. I notified Craig through the OCC. In the time that it took the OCC to find him the alarm cleared up. I advised Craig of this. He is not going to go out there. He asked that we just continue to monitor it as usual and let him know if it spikes again. He said he would pass it on to the team next week. I did give him the numbers where it spiked up, from .15 and .2 range up to 1.8 and then back down to .18 and .15 range. Munson |
| --- | --- | --- |
| 1815 | Madison | They called in and wanted to take their rate from 60 to 50. Calhoun |
| 1854 | Farmington | Took unit #3 down going to Willmar. That’s because all three units were down on bottom and unloaded. I got an alarm on the unit so I took it down and let the other units speed back up. Calhoun |
| 1912 | Farmington | Unit #5 – Took it down. We were getting up on top on the “BC” going north. I had plenty of pack up north at North Branch and also we were growing at Carlton. Calhoun |
| 2000 | Beatrice | Took down unit #27, the turbine on the high side. They had backed off the “BC” at Oakland and also had dropped Guthrie Center to get off of Ogden. It had rolled back at Palmyra so I dropped the turbine at Beatrice to help that situation. Calhoun |
| 2005 |  | Station 8 lost it’s power. It did ESD the fuel run system so I called Ron Arnold to visit on the phone and Troy Tucker to come out and help him. Cummings |
| 1908 |  | Merlyn shut station 1 down for me. The block valves did not open. He worked quite awhile to get the station to where bypassed. Cummings |
| 2100 | Seminole | Jerry on the Seminole team said they needed to take Seminole down for approx. one hour while they fix a control on it. Then they would be starting it back up. We’ve alerted everybody that needs to know. They said they would be done in about an hour. Welsh |
| 2200 | LS Power Whitewater | They called in and said they were shutting down for the night. They were going to start back up about 1330 tomorrow afternoon. Calhoun |
| 2400 | Skellytown | H2O is 9.9#. Dorchester delivers into that and it’s at 10# plus. We called Eric Haiduk who seems to be the person out there that knows who to call. He said he would call Cargray plant and see if they can find the problem and get it shut off. Welsh |
| 0135 | Beaver Co. 5 | Unit 4 went down. We were instructed earlier today by Randy with that team to leave that unit down and they will start it up first thing in the morning. I believe it goes down on low suction. They prefer not to start it until daylight. Welsh |
| 0230 | Skellytown | Eric Haiduk with the Pampa team checked on the H2O monitor. We were reading 10# here on our monitor. He went out and actually pulled a tube on it and it was 2#. He said he would go out in daylight tomorrow and dry it out and reset it to get a good reading. He was quite a ways from there and it took him a long time to get out there and actually get to it but he said it’s really only reading 2# out there so we don’t have all of the moisture that we think we’re getting. Welsh |
| 0210 | Seminole | Jerry and Jim out on the Seminole team brought that unit back on. It had been down since 2100 last night for work on their controls. They said the only way it could be fixed was to take the unit down. It took longer than they anticipated but the unit is back up. We did lose some deliveries to Norval, seems to be the only one that suffered. We reset the setpoint and they are coming up to rate right now to rate out by 9:00 in the morning. Welsh |
| 0256 | Seminole | Jim Myers called. It looked like the unit went back down. They are still checking the problem. They are not sure exactly what the problem is but there are people there and they are still working on that unit. He said it would be approx. one hour. Seminole is back down at 0256. Welsh |

slb