Services provided by Northern Natural Gas

And Transwestern Pipeline Company

- Enron Transportation Services

- Gas Control Event Log

0630 to 1830 Shift Mon., Dec. 31, 2001  (Cochran, Coash, Moore, Barnes)

| 0650 | Farmington | Just brought unit #6 on line. Cochran |
| --- | --- | --- |
| 0650 | LaCrescent | Brought that unit on line. Cochran |
| 0650 | Hugo | Just brought that unit also on line. Cochran |
| 0658 | Jal | Unit 2 – Just received an alarm on it going down. I got a hold of Lorenzo the on call and let him know. Also called Sid Richardson and let them know that we lost a unit. Their nom to us dropped from a 45 to a 25 for the new gas day. They are going to check the nom. If that’s correct we may just leave this unit 2 down there because we won’t need them both for the new day. We have already accumed about 46 MMBtu on a 45 order for the old day. Moore |
| 0715 | Sid Richardson Jal | Received a call back from Mondo. He let me know that he got the OK. There is a 25 nom for today is what they show. With the accum that we already have it’s OK to leave that second unit down going into the new day. Moore |
| 0718 | Jal | We lost unit 1 there now. Lorenzo is on his way out. I’m also showing an H2S alarm there. Moore |
| 0720 | El Paso 26” | I received a delmar H2S monitor malfunction. Made a call out. Louis is on site. He’s supposed to call me back. Moore |
| 0725 | Warren Eunice | I received an H2S alarm, grains critical high. This point did shut in about 3:00 or 3:30 this morning and the valve shut. We have not been flowing but it looks like the valve tried to open up and start flowing before the H2S got down. It might have flowed maybe 5-8 minutes. There is guy out there, didn’t get his name but I’ll find that out, he called in. He said he does have it manually shut now at this time. Not sure why that opened up with the H2S still up there but he is supposed to call me back. Moore |
| 0743 | Jal | I received a call from Bill. He has unit 1 back on line. He said there was a little H2S there that caused that to go down. It is clear now. Moore |
| 0527 | P3 | Unit 5 back on. Supply air for loading valve froze off. This unloaded the unit causing high recycle thus causing a high temperature discharge thus causing the unit to stop. Barnes |
| 0737 | WT1 | Unit 3 alarm. Barnes |
| 0818 | WT1 | Unit 3 alarm cleared. It was due to an AC power surge. Barnes |
| 0829 | Western Gas | Benedum – The flow went to zero there. I made a call out and talked with Blake. He said they are having some HP problems. They will get it back as soon as possible. Moore |
| 0923 | Beaver Co. 3 | Unit 3 is down. Billy is on his way out. Moore |
| 0925 | Roger Mills | Received a call from Jim. He let me know that they are working on the Sandstone point so we may see some alarms. Moore |
| 0941 | Hemp 3 | Received a call back from McLeroy. He said that he is going to leave unit 3 down and put unit 2 on. Moore |
| 0941 | P3 | Unit 5 down. Unable to control the unit. Tony will start other units. Barnes |
| 0945 | Roger Mills | Received a call from Ken. He let me know that they’ve got the Sandstone point flowing now. They had to clean out the manifold controller. Everything looks good. We’re going to try and flow 20 at that point to make up for the 10 yesterday and 10 today’s nom. I talked with Chuck at Sandstone. He said that he would try as long as he doesn’t run out of gas. Moore |
| 1000 | Oneok Bushton | Vargo called and said their lean side went down about 8:00 this morning. He said they’d try to get it back on as soon as they could. Coash |
| 1009 | P3 | Unit 5 is back on. Barnes |
| 1130 | P1 | Station alarm – Called Butch Bentley. Barnes |
| 1141 | P1 | Unit is down. Barnes |
| 1158 | Woodward 2 | Received a call from Dennis who let me know that he is on site there at the station to keep an eye on the units. He said there is a possible freeze up. Moore |
| 1204 | Hemp 3 | Received a call from Rudy. They swapped units. They took the #2 unit back down. They put unit 1 on line. Moore |
| 1204 | Woodward 1 | Received an ESD and AC power fail alarms here. Got a hold of Al. He said that there is someone on site there also and he’s headed that way. Moore |
| 1225 | TW Canadian | Units 1 and 3 down. Advised Rudy. Barnes |
| 1248 | P3 | Unit 5 down again. Barnes |
| 1248 | LaPlata Red Cedar | Zero flow rate on the receipt. I advised Jim with Red Cedar. Barnes |
| 1350 | Hugo | Just shut the unit down, no demand. Cochran |
| 1355 | Skellytown | Earlier I received an oxygen alarm, came up to .23, showing .24 now. Got a hold of Eric. He is there on site. He said he’s going to check it with his portable and he’ll let me know. Moore |
| 1320 | Canadian River | Units 1 and 3 back on. Barnes |
| 1406 | P3 | Unit 5 back on. Barnes |
| 1409 | GPM Linam Ranch | At this time they are only flowing about 75.8 MMBtu. I show a nom of 102.6. Made a call to the plant. He said that he was told to give us 88 for the new gas day which like I said at this time he’s only flowing 76. He said he doesn’t really have the gas. I did let Robert in scheduling know. He’s going to contract someone and find out. Moore |
| 1423 | El Paso Plains 26” | Received a delmar H2S monitor malfunction again there about 20 minutes ago. Louis is on site. We’ve got that cleared. Moore |
| 1504 | Skellytown | Received a call from Eric Haiduk. He let me know that coming out of the plant right now it’s .16 and he’s showing .22 at Skellytown. He said it’s going to take awhile for it to come down at the interconnect with that low volume but it should come down. Moore |
| 1521 | P1 | Unit is now back on. Barnes |
| 1534 | Beaver Co. 1 | The H2O there had come up earlier today and looked back into history and it looked like for the past few days it has been coming up to around 9-10# and then gradually falling back off. It’s at 10.197 now. It’s been between 9-10 for the past few hours now. I called out and talked with Alan. He said that he was there and he worked on the dehy and that we should see the moisture come back down. Moore |
| 1545 | Oneok Bushton | They are processing again on the lean side. Coash |
| 1630 | Redfield | Just requested they cut from 400 withdrawal back to 325. Cochran |
| 1640 | Hubbard | Just shut the compressor down. There is a possibility we’d have a peak alert between 5:00 and 7:00 tonight. To play it safe we just went ahead and shut it down. We’ll look at again at 7:00 and see if we need to bring it back on. Cochran |
| 1646 | Maxus Dumas | The H2S came up to .27 there. Made a call and talked to Wayne. He said they loaded up an engine. There was some H2S there and it would take a few minutes to clear. They’ve already got it purged within about eight minutes I guess. It’s now down to .03. Moore |
| 1710 | Pierz | I’ve been trying to get that flow in here now for about three hours. Mitch is out there working on it. He said there is a problem with the program. He can’t figure out or understand why it’s not working. He’s going to try to get a hold of Mark and see if he’s got any better ideas or any ideas on what to do. Cochran |
| 1805 | Spearman | The H2O there has been up above 5.8 for about two hours now. Made a call and talked with Alan. It’s on the dehy #3 outlet. He said to give it another ½ hour. He’s going to call back in ½ hour and if it’s not down then he’ll go out. They have been having problems with it. Moore |

1830 to 0630 Shift Mon., Dec. 31, 2001  (Hardy, Henley, Spain, Monden, Muntz)

| 1910 | Linam Ranch | Tony called. Their flow rate has gone to zero. They lost their treater. Their flow rate is shut down to keep them from delivering sour gas. He said he will call me back with more details on when they will be able to bring everything back up. Hardy |
| --- | --- | --- |
| 1915 | SP1Q & Carver | Scada is in history. I spoke with Bob Tornio. He said that the utility company monitors these interconnects and they would be good until they could look at them tomorrow and get the interconnect reset. Monden |
| 1930 | Sublette | Unit #21 went down. Rick is going back out. He was almost home. He had put that unit back on about 1910. He was telling me that it had some air in the lubricator and he thought he had it bled out but that might be the problem on why it went down again. Spain |
| 2030 | Cunningham | I gave Linda an order to cut the withdrawal rate down to 225. We’re running about 330 right now. Spain |
| 2034 | Palmyra | Keith had gone out to the site because he got an alarm on his dial-up. Unit 19 had gone down. He put 18 on in its place. The unit had gone down on control air problems. Monden |
| 2034 |  | Called Corn Belt to notify them that we were putting Hubbard. I sent a start command to Hubbard. Monden |
| 2043 | Linam Ranch | Talked to Ray Nosef the on call for the Hobbs team. He said he had talked to Tony out at Linam Ranch. He said it looks like it will be at least a couple of more hours before they get the treater plant on. He said that our valve should be open so whenever Linam Ranch starts flow he shouldn’t have to go out there. Since we didn’t get any H2S alarms here our valve should be open. If anything changes to where once they start up we do get a spike of H2S and our valve does close he will be on call to go out and take care of it for us. Hardy |
| 2050 | Columbus #4 Interc. | It has been in history. Notified the person that takes care of it Duane Debutts. We will monitor the pressures on the line from Columbus 1. He said they will try to get out there in the morning, either he will or someone else from the team to check it out and get the communications back. Monden |
| 2111 | Willmar TBS | Scada is in history. Had OCC get a hold of the contact person Mitch. He said he would get it checked out first thing in the morning. Monden |
| 2145 | P1 | Sent a remote stop command to P1. Butch will go out and check the unit over. Sent the remote stop due to reduction in Enrates and needed to take P1 down to keep from pushing suction up too high at P3. Showing the volume needed at P3 currently is 104. Tomorrow it’s calling for an 80 at P3. Muntz |
| 2200 | Bushton | Larry just called in. He lost a turbine up there. He’s going to try to get it back on line. Spain |
| 2225 | Citizens Griffith | Tom called from Citizens to inform me that Griffith had called and said they were going to fire up their auxiliary boiler. He said he’s going to open up the valve and requested that we open up the flow setpoint. Tom said that they had informed him that Griffith would be coming on line Thursday. Muntz |
| 2242 | Ventura | Shut down unit 11. Monden |
| 2327 | P1 | I just spoke with Butch at P1. It looks like possibly they had a block valve close over close to Curry interconnect. P1 suction pressure at this time is 907, discharge is 910. P2 suction is 770. I checked the pressure at Curry interconnect and it’s trending up. When you look at the suction at P2 it looks like it is trending down. It looks like we’ve possibly got a block valve closed. Butch is going to go check it out. Muntz |
| 2341 | Ogden | Robert is going home. The station is unmanned and is now in auto control from Houston. Also at this time we shut Faribault down. Monden |
| 2350 | Bushton | Larry called back. He had the turbine back on line just for a few minutes and it went down again. It’s got some kind of vibration problem. Starting to stack up pretty good on the north end. I’m going to try to put 31 on at Bushton, the 5500 vertical. We might be able to move the gas that we need to with it. Spain |
| 0004 | P1 | Butch called in and said that the block valve was closed down by Curry. He’s beginning to equalize at this time. Muntz |
| 0013 | Ventura | Shut down unit 15 at 0003. Monden |
| 0058 | P1 | Butch just called in. He said he had the block valve opened back up and he’s headed to the house. Muntz |
| 0113 | LaCrescent | Shut the unit down, bypassed it open and the station block did open. Monden |
| 0225 | Linam Ranch | Their flow rate is back up to 56. No call from them yet but they are flowing. Hardy |
| 0315 | Bushton | They lost the turbine again. Spain |
| 0345 | Hugoton | Alex called in. He’s got unit #9 back on. Spain |
| 0425 | Bushton | They got the turbine back on line. Spain |
| 0425 | Sublette | Units 13 and 14 went down on the “B” service. Rick is going out for us. Spain |

slb