Services provided by Northern Natural Gas

And Transwestern Pipeline Company

- Enron Transportation Services

- Gas Control Event Log

0630 to 1830 Shift Thurs., Feb. 21, 2002  ()

| 0730 | Macksville | OCC got a hold of the on call for us. I spoke with Bill. He’s going to put two units on the high side to help pull the pressure down for Cunningham and make it easier for the flow to come out. I notified Doug at Cunningham and he’s looking for that. Henley |
| --- | --- | --- |
| 0845 | Ogden | Got a hold the OCC. They got a hold of the on call, John. He’s going to get a hold of a tech to take care of Ft. Dodge IA South battery voltage. It’s showing low/low, showing a zero. He said he would call me back and let me know who it is. Hall |
| 0845 | Cloquette/Carlton | Got a hold of the on call. He transferred me over to Loren. I passed on to him that the battery voltage is showing low/low, showing 10.9. Hall |
| 0850 | Tescott | Unit #5 went down. I called the station and Gary is going to have Kim call me back. Henley |
| 0853 | Tescott | Unit #5 – Just spoke with Kim. He said the reason the unit tripped was due to him taking an oil sample. He did get it back on line so it is coming back up to speed. Henley |
| 0917 | Ft. Dodge South | Stacy just called from Ogden. He’s going to go up and look to see if he can fix the battery charger on it. Hall |
| 0940 | Burdett | Lost unit #2. Jay put unit 3 on in its place. We’ll have units 3 and 4 running. They are going to a safety meeting so we’ll be on our own. If we need something we’ll have to contact OCC. Henley |
| 1014 | Palmyra | Received a t-control alarm. I contacted the on call, spoke with Keith. He said that he will pass that information on to Bob who is actually operating today. He thinks that it is probably a generator alarm. He will get back with us. Henley |
| 1140 |  | Talked to Amoco LaPlata. I wanted to find out whether or not he was going to come up on nom today. His nom is 157. He told me that they were waiting on some more gas from Red Cedar. They were shorting them. I told him that they need to get up on nom. He said he would try everything he could to get as close to rate as he can. I did inform him that I will be calling Red Cedar to find out what was going on. Braswell |
| 1145 |  | I talked to Red Cedar. He was telling me that they have a unit that was down, scheduled for maintenance. Also they had a tie-in that was going on out there today. Of course this is causing their field pressure to be down, the reason why they weren’t able to come up on nom for right now. He doesn’t expect it to last too much long, maybe another 1 to 1.5 hours. Then he will try to get up as close as he can on rate. Braswell |
| 1:15 | TransColorado | Talked to Sam at Kinder-Morgan gas control. He informed me that they were doing all that they can at the TransColorado point. The nom is 91.2 million. They are actually spotting right now about 71.9. He said he had all of his HP on. He did bring some gas from up north. It’s just going to take awhile before we actually start seeing the flow come up, at least 24 hours but they are doing all that they can to get on that nom. They are trying to talk to El Paso to see if they can cut them back a little bit so they can come in a little closer on their nom for us. Braswell |
| 1325 | Black River Falls WI | Got a low alarm on the station flow temperature. Called the OCC. They got a hold of the on call at Farmington. He said that he would pass it on to the person who takes care of it who according to our records is Tim Pietsch. Hall |
| 1426 | Station 4 | I’m showing all three units down at this time. I called Howard. He said they had some type of malfunction on the loop line. Barry |
| 2:32 | Macksville | Just spoke with Bill. #3 unit had an oil leak. He has tried to repair the oil leak and had to take the unit down and #2 went down on it’s own accord. He will repair the oil leak and put the unit back on line. Henley |
| 1710 | Pierz | Called the OCC. They got a hold of Jim. I also called NSP and let them know that a unit had gone down at Pierz. They were experiencing low pressure anyhow in that area. They’ve had low pressure all over on their system today due to the loads. I told Jim it looked like ours might have gone down because of the spread on the unit, it was spread out pretty good. Had a little over a 200# spread between their pressure and our discharge. North Branch had gone down earlier. I told him I wasn’t in a read great hurry to go ahead and get the unit back on but we do need to try to get this gas in from NSP at Pierz. He’s going to call Mark and see if he can get it reset from home or whatever needs to be done. Hall |

1830 to 0630 Shift Thurs., Feb. 21, 2002  (Barnes, Alvarado, Moore, Cochran, Coash)

| 1855 | Sublette | Lost unit #21. Rick Titus is going to go out there and see about getting it back on. Cochran |
| --- | --- | --- |
| 1815 | Spearman | Unit 1 down. Ronald the operator is in route. Barnes |
| 1843 | Spearman | Unit 1 back on. Barnes |
| 1915 | Plainview | Station alarm cleared by Andrew. Barnes |
| 2028 | Station 4 | Unit 402 has gone down. I’ve contacted OCC. I’m waiting to hear from the on call at this time. Alvarado |
| 2125 | Maxus Dumas | H2S jumped to .642 grains at a 18.5 flow rate. The 18.5 is also the average rate so far for the day. I called their plant and they had a unit go down and they put it back on. That’s the reason for the spike of H2S which they say is already coming down. I also at that time notified the Sunray operator. Barnes |
| 2147 | Maxus Dumas | H2S at a .318 grains. Barnes |
| 2147 | Plainview | Station alarm – Advised Andrew. He said it’s still related to some of the gas sniffer false readings that they’ve been getting out there. It will stay in alarm through the night. Barnes |
| 2157 | Sunray | H2S of .40 grains. Barnes |
| 2159 | Maxus | .046 grains. Barnes |
| 2209 | Sunray | H2S 0.128. Barnes |
| 2206 | Skellytown | Oxygen of 0.216%. Our maximum allowable before calling someone is 0.210. Advised Vance Griffith on the Pampa team. Barnes |
| 2236 | Skellytown | Oxygen is now 0.185% and well in range. Barnes |
| 0117 | Phillips Plymouth | POI 661012 – They received a pig at 0016 that overloaded the separators and dumps. Thus, they slowed units, _____ liquids and stayed slowed until liquids are again manageable. The flow rate at this time has dropped from 25 to 12. They will resume as soon as possible. Barnes |
| 0150 | Hugoton | Lost unit #14 out there. Personnel is headed out to see about getting it back on. Cochran |
| 0150 | Minnegasco | They increased their nom at Grundy by 39,000. Coash |

slb