Services provided by Northern Natural Gas

And Transwestern Pipeline Company

- Enron Transportation Services

- Gas Control Event Log

0630 to 1830 Shift Fri., Feb. 1, 2002  (Hardy, Spain, Monden, Muntz)

| 0537 | Station 1 | Unit 102 has gone down. I notified Mike Pavey through the OCC for station 1 that we’re down and that we wouldn’t be needing the unit. He’s going to go out and look things over. The unit went down pretty much on no demand. I was running all of the units backed off because of high pressure at the border and the unit took itself down. I let Mike know that we were running them backed off. The other two sped up and picked up the load. The station looks fine. He’s going to go out and give it the once over. I told him we’d leave that unit down until further notice. Munson |
| --- | --- | --- |
| 0615 | Gallup | We received another unit alarm at Gallup. I’m going to notify Mike Boatman through the OCC and let him know. The last time he went out and cleared it. It was indeed a surge alarm. It’s probably the same item. We’ve lost some of our flow from the WFS group coming in from San Juan and that’s probably what’s causing the surge problem. Munson |
| 0630 | Hugoton | Rocky just called in. He was called out by the auto dialer to the station. Had a station alarm. It turned out to be a high scrubber alarm. He’s got that taken care of and the alarm reset. Spain |
| 0636 | Owatonna | Sent a start command to the station. Put it on line to pump up to Farmington. Getting a high differential and losing out on the west leg pressure, it’s 890. Monden |
| 0705 | Perryton Barlow | Unit 1 is down. Larry is going to check things out for us. Hardy |
| 0710 | Hubbard | On the line at 0658. Monden |
| 0755 | Roger Mills | Called and talked to Ken to get a status report on the station. He’s still on his way. He said he will give me a full report once he gets there. Hardy |
| 0755 | Continental Beaver | Called and talked to Ron to ask them if they were back on line. He said they were back up and processing at about midnight out there. They’ve got power and everything looks good. Hardy |
| 0808 | Hubbard | When I put the unit on it did not seem to come up with a full load. I talked to Pierre who takes care of the Hubbard station. He said it was blocked out on HP and it had been in limited HP for the week. I called Corn Belt and spoke with Paul. He said that the limit on the load pull was released to full load for the compressor station. Pierre upped the HP limit on the unit. Monden |
| 0810 | Aquila | Talked to Pat. He said they’ve got power out there but they won’t be ready to come up and start delivering gas to us until about 12:00. Asked him to give us a call whenever they were ready. Hardy |
| 0815 | Cunningham | I gave Linda an order for max withdrawal. The max withdrawal rate will probably be in the neighborhood of 425. They still have #6 dual fuel that’s got a valve problem. They are working on it. Should be back available before the end of the day. That will put us back up around 500 withdrawal rate. Presently we’re doing about 374. Spain |
| 0845 | Texas Co. 1 | Got both units down at Texas Co. Alvin called in and informed me that they had a freeze off. They are working on the problem right now. Spain |
| 0927 | Oakland | Spoke with Mike and asked for two verticals “D” to “D”. Monden |
| 0959 | Clark Co. 2 | Unit 7 is down. Dennis has got somebody on the way out to put it back on line. Hardy |
| 0948 | Ogden | Spoke with Darrel. They’ve got unit 17 up and running. It is pumping to the east. He did have 13 and 15 up. Those both were down. He said he did have a problem with 17 on the panel and now it’s up and running. He’s going to take 15 back down to prepare for the gas that’s going to be coming back in from the day nom with NBPL. Monden |
| 1001 | Atoka 3 | Atoka 3 has unit 761 down. They are going to do some repairs and bring it back up. Muntz |
| 1007 | Bloomfield | Blackie called me and said that they had launched a pig at 0830 their time. Discharge pressure at the time was 1145 and flow was 865. Muntz |
| 1015 | Clark Co. 2 | Dale called. He’s got unit 7 back on line. Hardy |
| 1048 | Bisti | Brian called and said that the pig passed valve S108 at 0943 their time. He’s going to shut Bisti down at 1005 their time. I slowed Gallup down by raising the suction from 750 up to 775 until after Bisti gets back on. Muntz |
| 1056 | Ogden | Asked Darrel to shut unit 13 down to make room for more gas coming in at the interconnect with NBPL because that gas was going north out of Ogden. Monden |
| 1115 | Bisti | Brian took Bisti down at 1110 until the pig passes. Muntz |
| 1134 | Canadian River | I show that unit 1 and unit 3 are off. I contacted Chris. He’s going to get a hold of someone and have them restart the units. Muntz |
| 1208 | Farmington | Unit #3 has gone down. I see no reason for it to go down because it wasn’t slowed down, making it go down on low oil pressure or anything. Had OCC get a hold of a contact person. They got a hold of Bill Schmeling. He said he would go check it out. Monden |
| 1218 | Farmington | Tony called back and said unit #3 went down on high fuel differential. They are going to change out some fuel injectors. Will have it ready and available as soon as possible, estimated two hours. Monden |
| 1255 | Northrop | Unit 1 is down. Talked to Steve. He’s going to go take care of it. Hardy |
| 1340 | Sublette | I just called and spoke to Mike Burnam. I requested some HP changes up there. They’ve got two turbines on the “B” line. I asked him to put a vertical on and a turbine. We’re pulling his suction down too low and Holcomb is running out of gas over that direction. Mike did advise me that he thought it would work out better if I went ahead and opened up the Hugoton to Holcomb valve, and they’ll take a turbine off and just run with one turbine. He thinks we’ll be able to take care of our low suction pressure problems running in that mode of operation. Tekas Bradshaw went to zero today so that left Holcomb a little bit short. I did anticipate CIG coming in with an extra 13 million would probably keep our Holcomb station in pretty good shape but it looks like he’s running out of gas there. He’s got about 285 on the suction side of Holcomb. I need to get some more gas over that direction and this is the way we decided to do it. Spain |
| 1410 | Cunningham | Linda just called in and said that maintenance needed to take unit #5 down for about ½ hour. They are working on a problem with it. It should be back on line soon. Spain |
| 1430 | Woodward Co. 2 | Dennis called. He’s got the station back on line. Hardy |
| 1430 | Westar Carson | Talked to Joe. He’s looking into the H2S monitor showing .34. The trend on it has showed the same reading for the last hour. We think it’s a bad reading. Joe is going to check it out. It’s probably malfunctioning due to the cold weather. Hardy |
| 1524 | Farmington | Unit #3 is available and ready to run whenever required. Monden |
| 1534 | Gallup | Korey just called and said that they received a pig in at 1350 their time. He has cleared the station alarm there at Gallup. He also told me he was going to be doing some work on the fire eye and that we would be seeing some alarms for about the next 30 minutes. He will call back when he’s finished. Muntz |
| 1541 | Amoco LaPlata | I called the Floreda plant and check with the nom. Let them know I was seeing a nom of 158.3. Currently we’re projected to come in at 137.9, that’s about 20 short. According to the projection I need to run a 166 at this time. They said they would try to get up to that rate. Muntz |
| 1630 | Stevens Co. 4 | Unit #4 went down out there. I didn’t receive a call from the field. I didn’t know whether they were going to leave it down or what. It went down about 4:00. I called the on call person and spoke to Paul Dobie. He said they took it down and they intend to leave it down tonight. I also asked him about Stevens Co. 7, unit #1. It’s the same situation. It went down about 4:00. No one called. He said they were planning on leaving that unit down also. Spain |
| 1642 | Ogden | Shut unit 13 down which was pumping east. I was cracking roughly 130 million going north. I’m getting full in zone EF. Got a 1075 line pack. Monden |
| 1645 | Hugoton | I got a few bogus alarms in here from the Hugoton station. I got alarms on units that are down. Also showing units unavailable that are running. I got a hold of Rocky out there. He said they are working on the PLC so I will be getting some alarms in here. When they are through Ken Adams is supposed to call gas control so we’ll know everything is back to normal. Spain |
| 1654 | Oakland | Had OCC get a hold of the contact person Jeff Bartlett. Asked him to shut the units, two units on the “D” to “D” down. He said he would get out there and shut them down within 15 minutes. Monden |
| 1700 | Sublette | Unit #22 went down about ½ hour ago. I didn’t hear anything from the Sublette station. I called the on call person, spoke to Bill Lee. He informed me that they are going to leave the 22 down. Oneok has some compression out there and has some problems, blown intake or something on their unit. It doesn’t provide us with enough suction there to run two units on the “A” service so we’re just going to run with one unit. Spain |

1830 to 0630 Shift Fri., Feb. 1, 2002  (Barry, Armitage, Hall, Braswell)

| 2000 | Phillips Plymouth | We have a schedule of 27 million, flowing 22.7. I called the plant and asked if they could raise it up to schedule. They said they would. Barry |
| --- | --- | --- |
| 2002 |  | Called Western Gas Benedum plant. We’re showing a 15 million scheduled, flowing 9.5. I did requested that we come up to the 15. They said they would raise it on up. Barry |
| 2144 | Sublette | Just got a call from Bill Lee. He’s putting the turbine back on. Pressure had been climbing out there every since I came in. When I first got here it was 354 and we’re up to 375 now. Also the suction at Holcomb has gone from 296 up to 306. I have sped up the two units at Burdett. They were running about 246. They are both running 283 now. It should help to get the gas moving again. He said that Oneok did get their problem fixed on the “A” line so he put that unit back on also. Hall |
| 8:30 | WT1 | I was on a conference call with Randy at WT1 and Darrell and Randy decided he needed to take down unit 2. There was some arcing going on inside the unit. He wanted to take it down and take a look at it. He’s going to leave #1 unit on. Wanted me to get some of the discharge off of him at WT1. He said it would be a couple of hours before he could tell whether or not to see what he needed to do with that unit. Braswell |
| 2135 | Station 7 | Lost unit 3 there. Called the OCC for the on call. Braswell |
| 2318 | Station 7 | Unit 3 went down again. Called the OCC for the on call. Braswell |
| 0505 | Rolla #1 TBS | Called the OCC. They got a hold of the on call, Joy on the Hugoton team. She said she would get with Bill and they’d go out and check it out today to see what’s wrong with the battery out there. Hall |

slb