Services provided by Northern Natural Gas

And Transwestern Pipeline Company

- Enron Transportation Services

- Gas Control Event Log

0630 to 1830 Shift Fri., Jan. 18, 2002  (Cochran, Barnes, Coash, Alvarado, Moore)

| 0630 | Beatrice | They just got the turbine back on going “E” to “E”. Cochran |
| --- | --- | --- |
| 0615 | P3 | Received a call from Tony. He let me know that he’s going to have to isolate the station and blow down part of the station. It’s going to be down for 3-4 hours. He’s going to have to do an ESD. He is going to bypass the station so we can do what we can on deliveries. This is all due to he lost a block on the control valve and it will have to be replaced. At 0640 I did a remote kill on P1 station because of the high pressures at P2. Moore |
| 0700 | Oakland | I just requested they bring the “BC” on at this time. Cochran |
| 0720 | Ogden | We had four units on Redfield. We only need two. We took two of those and put it on the “BC” and we’re going to take those east, crack the excess north. It looks like we’ll probably bring 1 or 2 horizontals on going “BC” to “D” north. Cochran |
| 0725 | Paullina | Got low ESD pressure. I visited with Steve up there and made him aware of it so they could check it out. Cochran |
| 0730 | Meridian | The CO2 came up to about 2.14. Made a call out and talked with Sean. He said that he has already cut his bypass and that we should see it come back down pretty quick. Moore |
| 0814 | Monument | Received a station alarm there. I made a call out and talked with Ernesto. He said he would check it this morning. There are no units running there at this time nor has been. Moore |
| 0845 | Ventura | I just requested they bring the “BC” station on at this time. Moore |
| 1014 |  | Mullinville reports the 8.5# of water is a correct reading on the “A”, “B” and “C” lines. Advised Jim the Beaver plant operator to check all possible points and also to call the Beaver field team to check the Continental Beaver interconnect and the TW Beaver interconnect. Gary Spraggins was advised. The water has been steadily trending upward since 12/25/01. Barnes |
| 1026 | Mullinville | The station is down due to receiving a pig on the “A” line. Barnes |
| 1035 | Ogden | Just requested they put another horizontal on going “BC” to “D” north. Cochran |
| 1050 | Monument | Received a call from Bob who is out there. He let me know that the reason for the station alarm is a Brick communication failure. He said the Opto people, communications experts, are on vacation and that it would be Monday before they are able to look at that. Moore |
| 1100 | Mullinville | The station is back on. Barnes |
| 1121 | Ogden | I just requested they bring another horizontal on going “BC” to “D” north. Cochran |
| 1128 | Monument | We have all alarms cleared there now. Bob got a hold of someone and they were able to reset and clear the communication failure alarm. Moore |
| 1105 | Bushton | Requested unit 32 the turbine to be put on line. Barnes |
| 1228 | Hugoton | H2S of 0.7 grains and with digital alarms. Advised the operator. Barnes |
| 1301 | Atoka 1 | Unit 737 is down, this is for some maintenance, probably for about one hour. Received a call from Gene. Moore |
| 1245 | Bushton | Unit 32 on line. Barnes |
| 1500 | Meridian | The CO2 has come up again. I’m showing 2.04. I had called there and talked to Sean. He said he’s cut the bypass again. He’s having problems with one of the trains but he is working o it. Moore |
| 1505 | P3 | Unit 5 is back on line and has been for maybe an hour now. I just talked with Tony. He said it’s good to go. I’ve called P1 and Fogg is going to put a unit back on line there. Moore |
| 1505 | Duke Energy | At the GPM interconnect, #1 at Beaver – Duke conferenced us in along with Chris Greaney on a problem that they are having at this time. They are going to divert about 8 million through this interconnect due to an ice blockage that they have on their Slapout booster station near Perryton. They need to move this gas off of their system. They are going to move it through this interconnect to us for 12-18 hours. There is no nom at that interconnect at this time and Chris is aware of this. We’ve given Duke the OK to go ahead and bring it through. They are supposed to be calling us whenever they get ready to switch this gas back because we do control the interconnect. I’m going to start flowing at a rate of 8 million to us from them. Alvarado |
| 1525 | PNM Rio Puerco | I’ve got an 80 setpoint in there. I’m showing a flow rate of about 59 at this time. It’s been at least 1 to 1.5 hours now and that valve is only open to 64%. I made a call out and talked to Johnny on the Laguna team. He’s going to go out and check it. He thinks it is possibly the 10” run is not opening for some reason. Moore |
| 1600 | Hubbard | Dan Wilson called from the electric company and said there was going to be a peak alert today. Due to the fact of the loads on the east leg I visited with Pierre and also with Steve January. Steve visited with Tom Gilbert. We elected to allow the unit to just go into the slow down phase instead of completely shutting down for the two hours due to the fin system and the strong loads that we’ve got out there today. Cochran |
| 1530 | P1 | Unit is back on line. Moore |
| 1542 | Canadian | We lost units 1 and 3 there. Got a hold of Eddie the on call. He’s headed out. Moore |
| 1635 | Beaver Co. 5 | Unit #4 is back on. We lost this unit at around 1306. I contacted OCC and we had problems getting a hold of anyone on the team for that unit. We finally made contact with Randy Kliewer at 1514. He was over at Ivanhoe on an AC power failure that had happened earlier this morning. They were finally able to get the electricity back on so he had to put some units, other machinery on. He was over there taking that so that’s why he was so late in getting back to Beaver Co. 5 and putting the #4 unit back on. Alvarado |

1830 to 0630 Shift Fri., Jan. 18, 2002  (Calhoun, Munson, Welsh, Cummings)

| 1800 | Bushton | Got a call from Dan Smiley. He said they lost the turbine on the high side. They will get it back on as soon as possible. Calhoun |
| --- | --- | --- |
| 1825 | Bushton | They got the turbine back on. Calhoun |
| 1815 | NBPL | Got a hold of Jodi. Had her move 60 million from Grundy back over to Ventura. We just went ahead and shut Grundy in. Calhoun |
| 1940 | Ogden | Got a hold of Robert at the station. He was going to switch unit #13 over from the “BC” going east to going north. Calhoun |
| 1945 | Galena | Shut #2 down. Both units were down on bottom and didn’t have very much differential across the unit so I went ahead and shut it down and let #1 carry the load. Calhoun |
| 1945 | Palmyra | Got an alarm on unit #26. Keith called me. At 2015 he had gotten the alarm cleared. Calhoun |
| 2100 | Wakefield | Our pressure was falling off and their pressure was coming up so the flow rate had started dropping. There was a 10 million flow rate setpoint in there and I was down to about 6 million. I lowered my setpoint to 5. At 2120 our pressure equalized and the flow rate went to zero so I just went ahead and sent a zero to it. I’m in the process of raising the east regulator out of Carlton to try to get our pressure back up high enough to where we can start flowing that again. Calhoun |
| 2257 |  | Noticed the downstream interconnect pressure at Citizens Griffith had fallen off fairly dramatically since 10:00 this morning. I talked to them. They had to put a boiler on. It looks like on the imbalance sheet that we owe them gas so I cracked the interconnect just so they wouldn’t run out of gas. Cummings. |
| 0035 | Bushton | Dan just called to say that they’ve lost the turbine on the “E” line. He’s going to get it back on as soon as possible. I notified Gloria at Cunningham. Munson |
| 2133 | Carlton | Got alarms on units 1 and 2. Roy Ober went out there and found out the station air pressure was low. He said they had put that on a timer where the air compressors didn’t run from 4:30 p.m. until 9:30 p.m. As soon as it got after 9:30 on the time that the air compressors would kick back in and those alarms should clear. Calhoun |
| 2300 | LS Power Whitewater | They called in and said they were on the way down and that they’d be starting up about 6:45 in the morning. Calhoun |
| 2330 | Farmington | Took unit #6 down. Our pressures were starting to build on the “BC”. That’s primarily due to the load dying off. Also I needed more suction for the units going to Willmar. Calhoun |
| 2345 | Minnegasco | They called and wanted to cut their withdrawal rate at Grundy Center. They had a nom in there for 68.2. They wanted it taken down to 29. We made the adjustments. Calhoun |
| 0025 | Waterloo | Took unit #6 down. Our pressures were starting to build out towards Earlville and Galena. Earlville was slowing down. Calhoun |
| 0045 | North Branch | Took unit #4 down. Calhoun |
| 0339 | Beaver Co. 5 | Unit 4 went down on low suction. I talked to Randy with the Beaver 5 team out there. He is going to opt to leave the unit down until the suction pressure comes back up and until daylight. Welsh |
| 0200 | Ogden | Darrel took down unit #10, one of the horizontals that was running “BC” to the north. That was because I was able to crack over from the east crackover valve and make up the difference so we really didn’t need the unit on. Calhoun |
| 0205 | Waterloo | Shut down unit #2. We were stacked up out on the east leg and Earlville was slowed down. Calhoun |
| 0414 | Hemphill 3 | Dehy unit #1 is down. I called Eddie with that team. He said he will start that up at daylight. Welsh |
| 0415 | Ogden | Darrel took down the second horizontal he had on the “BC” going north. That left them with just two horizontals running. They felt comfortable with going home at this point in time. So they are not on shift. Jerry is going to be in this morning to do a walk through the station. He will get with Jeff Cochran to see if there needs to be any changes made at that time. Calhoun |

slb