Services provided by Northern Natural Gas

And Transwestern Pipeline Company

- Enron Transportation Services

- Gas Control Event Log

0630 to 1830 Shift Thurs., Feb. 7, 2002  (Munson, Welsh, Calhoun, Cummings)

| 0630 | Station 1 | Merlyn has the station alarm and the intrusion alarm cleared at station 1. Munson |
| --- | --- | --- |
| 0805 | Atoka 2 | Unit 760 is down. I notified Jerry through the OCC. Munson |
| 0940 | Station 4 | Units 401 and 403 are both down. I called out there and talked to Robert. He hopes to have them back on as soon as possible. Munson |
| 0640 | North Branch | Shut unit #2 down. We were up on top going west and I needed the gas in the Cities. Calhoun |
| 0655 | Hubbard | Shut the unit down. We had Earlville on bottom and our noms are going down even some more today. Calhoun |
| 0850 | Pierz | Brought the unit on for 12 million delivery. Calhoun |
| 0910 | North Branch | Brought the unit on line. They brought unit #3 on line because they wanting to do some testing the unit. It’s been down and unavailable for the about the last week. They got it repaired and they were wanting to run some tests. Calhoun |
| 0930 | Galena | Got a call from Dave Buddig. They had some work to do on unit #1 which was on line. They shut #1 down and put #2 on line. Calhoun |
| 1025 | Palmyra | Had them put a unit on the “CD” to “D”. That was primarily to help pull in our Trailblazer flows and also keep differential across the turbine. Calhoun |
| 1040 | Station 4 | Units 401 and 403 are back up. However the rollback has knocked down a unit at station 5. Charlie is on his way out there to take care of that. It has also caused us a surge alarm at the Gallup compressor. The Gallup team has got someone headed over there. Munson |
| 1140 | Clark Co. 2 | We called Alan with the tech team out there to check on a high H2O alarm. At this point we’re reading about 7# of H2O at Clark Co. 2. Alan pulled the tube and he said it’s really 4#. He said the monitor is off and it’s saturated. He didn’t think he would be able to have time to dry that out until tomorrow sometime, Friday. We told him that we would document this and watch it. He said it should be a lot lower than what it is reading and we’re trusting that’s the case. Welsh |
| 1500 | Norval Pecos | We had some problems with our turbine meter out there. Rick with the Monahans team has been out there most of the morning. He did say that both rotors were gone and the screen had blown in there and damaged the meter. They re-installed the whole unit and rebuilt the whole turbine meter. We’re just now coming back on. I just called PG&E and told them we were going to have to bring that volume up to about 63 million just to come in on rate for tomorrow. They said that’s fine. That is what we are in the process of doing. Welsh |
| 1550 | PG&E Topock | I received a call from Alfred with PG&E letting us know that there is some scheduled maintenance on their side at the Topock compressor station starting tonight after midnight. They said it will run about 22 hours, right through the next gas day tomorrow. They do not expect Topock flow to be affected. Munson |
| 1555 | SoCal Needles | I called SoCal gas control and spoke with Bob. I reminded him of his rate for today of 668. I pointed out to him that they would have to pull close to 690 for the rest of the gas day in order to come in on rate for the day. Bob said no problem. He’s planning on picking up the pace tonight through the night and he’ll come in on rate for the day. Munson |
| 1050 | NBPL | Joel was taking a break from testing. We were able to make our first changes. I took Ventura from 670 to a 600. Calhoun |
| 1330 | NBPL | Joel took another break. We cut the Ventura nom from 600 down to 540. Calhoun |
| 1500 | Redfield | Got a hold of Brian. Had him cut the rate back from 305 to a 275. That was primarily because his pressures were coming up at Ogden and we would have had to put another unit on pulling Redfield gas going north. The north was packed up pretty tight and we really didn’t want the gas going north so we elected just to cut them back. Calhoun |

1830 to 0630 Shift Thurs., Feb. 7, 2002  (Hardy, Henley,  Monden, Spain, Muntz)

| 2150 | Red Cedar | Just spoke with the operator. Their CO2 level came up. She said that it was due to some pressure problem in their yard. They have that taken care of and it should be coming right back down. Henley |
| --- | --- | --- |
| 2215 | Stevens Co. 6 | All units are down. I’ve got a station ESD alarm but Steve Hedrick is on his way out to the station now. Hardy |
| 2332 | Lamar Point | I noticed that Transok is still flowing at Bennington. I contacted Transok gas control. They said they are unable to get it shut off at this time. They’ve got a technician that is on the way out there to try to close off the valve. Currently the pressure is at 803 and it looks like we’re gaining about 35# an hour. Muntz |
| 2340 | EOG Pitchfork Ranch | We lost flow there. I notified Dirk Ellison with EOG. Henley |
| 0205 | Northrop | I just spoke with Lupe. The water started trending up at about 1130. It’s up to 28.9# at this time. It’s been about 2.5 hours. He said that sometimes it takes about four hours for it to start trending back down. He asked me to keep an eye on it and if it’s still up around 4:00 this morning to give him another call. Muntz |
| 0215 | Griffith | Just spoke with Trace with Griffith Energy. I had talked with him earlier tonight. They had taken the unit down a couple of hours ago. They just went ahead and took their second unit down. They are now down until Monday. I advised him that I’m going to shut the block valve feeding their plant and that they will have to give us a call when they go to start back up so we can open that back up for them. He said he would make a note of it. I believe they are scheduled to come back on line on Monday. Henley |
| 0330 | Stevens Co. 6 | Steve called. He said he’s got the station back on line. Units 1, 3 and 5 are running. He said they had a valve freeze off on them which activated the ESD but it did not blow the station down completely. Hardy |
| 0400 | Interconnect MN1D | It is in history. I had Roderick check it out. He said the telephone line is giving a quick busy signal. He said this isn’t a VSAT interconnect. Also at mnemonic ELKR went out about the same time roughly about 1:30 and Chisago mnemonic CHSG. Monden |
| 0419 |  | After Roderick had determined that the long distance provider could not fix our telephone lines, it had to be done by the local telephone company, I notified OCC for the on call person for North Branch for the Minneapolis 1D and LS Power Cottage Grove and Elk River interconnect. These all seem to go out at roughly the same time. Informed him of these being in history and the local telephone company needed to be contacted on these. I suggested that Minneapolis 1D probably would be an emergency one to try to get fixed so we could see the gas demand to Minneapolis at this interconnect this morning. Monden |
| 0435 | Palmyra | Unit #19 has gone down. Notified OCC. They got a hold of Mark Kramer. He is headed to the site. Monden |
| 0435 | Northrop | I just spoke to Lupe. He is going to go out and check the dehy. We’re still showing that we’ve got 30.9# of water. Muntz |
| 0507 | Minneapolis 1D | After Greg from the North Branch team got it up on his laptop, said he had no problem hooking up to it through the local telephone line. He spoke with Roderick and they had determined that it is probable to be the local telephone company here in Houston. Monden |
| 0509 |  | Unit 19 at Palmyra is back on line. Monden |
| 0530 | Northrop | Lupe called in. He said that the moisture is trending back down. He’s showing a 21 at this time. He said he’s got a monitor that is going bad. He is going to have the daylight crew check it out. Muntz |

slb