Services provided by Northern Natural Gas

And Transwestern Pipeline Company

- Enron Transportation Services

- Gas Control Event Log

0630 to 1830 Shift Tues., Jan. 29, 2002  (Cochran, Coash, Moore, Alvarado, Barnes)

| 0619 | Beaver Co. 5 | Unit 4 down on low suction of 35#. Kelly Lewis will restart it later when the field pressure has increased. Barnes |
| --- | --- | --- |
| 0700 | Wrenshall | I just requested they go from 100 million vaporization to shut in. Cochran |
| 0710 | Oakland | Requested they drop one of the four units that are on the “D” to “D”. Cochran |
| 0745 | Farmington | Brought unit #3 on line going west. Cochran |
| 0820 | Dagger Draw | Terry is going to be calibrating at this interconnect this morning. Alvarado |
| 0830 | Lips Mulcane 12” Lateral | Randy Kliewer with the Beaver pipeline team has called in to let us know that he’s getting ready to launch a pig on this lateral. Alvarado |
| 0839 | Skellytown | Oxygen of .229% - Advised Eric Haiduk of the Pampa team. Barnes |
| 0854 | Jal | Unit 2 on as requested. Barnes |
| 0908 | Station 2 | Unit 2 has gone down. Alvarado |
| 0919 | Atoka 3 | Terry Youngren has finished calibrating at Dagger Draw and is on the way to Atoka 3 to start calibrating at that interconnect. Alvarado |
| 0919 | Station 2 | Unit 202 is back on. It’s not loaded but they do have it back on. Alvarado |
| 0902 | Skellytown | Oxygen now back to a good number of .19%. Barnes |
| 0920 | Owens-Corning | Eric Haiduk is testing transmitters at this interconnect. Alvarado |
| 0920 | Station 2 | Unit 202 has been loaded out at this time. Alvarado |
| 0958 | Station 4 | Unit 403 has gone down, high discharge, due to the problems that we had out in front of it at station 2. Alvarado |
| 1023 | Phillips Dumas | POI 18058 – They have a unit down and cannot make the nom of 28.8. They are only doing 19. Advised Randy Janzen in scheduling. He said it would be all right, that they had over delivered to us and we’ll use towards imbalance. Barnes |
| 1027 | Seminole | Unit down as requested, no demand. Barnes |
| 1200 | Hugo | I just brought the unit on line pumping west and out to the branchlines, and pumping north up to North Branch so we can get some more gas west out towards Benson. Cochran |
|  | Note | ONG 3 delivery POI 176, to be 5 over for make up today. Nom is 13.212 plus 5 equaling 18.212. This is being done as requested by Joe Linhart. It’s not going to show up in the scheduling of this gas. Barnes |
| 1431 | Beaver Delhi Aquila | POI 269 – They’re doing 21 on a 16 nom. Advised Aquila, spoke with the station operator. They will adjust the flow rate. Barnes |
| 1512 | WT2 | Unit 3 has gone down. Joey Green called in and said that they had been working on another unit and they released some gas near one of the sensors which caught the gas sensors, set them off causing the unit to go down. Alvarado |
| 1517 | Lips Lateral | The pig is in. Randy said they had a very small amount of liquids that came in. Alvarado |
| 1518 | WT2 | Unit 3 is coming back on. Alvarado |
| 1640 | Hugo | Just shut the unit down, no demand. I’ve got the pressure built up at North Branch to where we’re on top going west, along with the gas coming out of Great Lakes so we don’t need the unit on at this time. Cochran |
| 1640 | Palmyra | Lost unit #19 on the “B” line. Got a hold of personnel, Randy. He’s headed out there to see about getting it back on. Cochran |
| 1656 | Loop area | I have received a call from the Loop Navajo fire department, station 80, in reference to a strong odor of gas smell along the TW pipeline in that area. I spoke with Emil Begay at 928-686-3253. They have two fire units in the area trying to locate to see if there is a leak on our pipe. I have contacted our personnel at station 3 and passed the information on to them. I have requested that they contact our people and try to get them on site as soon as possible. Alvarado |
| 1700 |  | In reference to the gas detection, possibly gas leak in the Loop area, I have contacted OCC and I have established a conference bridge for the Loop personnel and management. Alvarado |
| 1705 | Skellytown | Oxygen of 0.23% - Advised Eric Haiduk and he will call the Skellytown operator. Barnes |

1830 to 0630 Shift Tues., Jan. 29, 2002  (Munson, Cummings, Welsh, Calhoun)

| 1915 | Redfield | Took their order from 350 down to a 300. That’s due to we were starting to stack up at Ogden and zone C. Also we were running about 20 million short on our NBPL totals so I was needing to get them cut so I could get the NBPL gas in also. Calhoun |
| --- | --- | --- |
| 1915 | Faribault | Took the unit down because both Faribault and Owatonna were running on bottom. I had plenty of suction at Farmington and the units going west were down on bottom also so I just went ahead and got Faribault out of the way. Calhoun |
| 2001 |  | Spoke to Mitchell Ellenberger. They are running short to us. He said several operators behind him are doing PM’s on their compressors. Hopefully the gas will come back tonight. Cummings |
| 1840 | Station 3 | JB checked in from station 3 to report that they have closed down the conference bridge regarding the possible leak in the station 3 area. All of the team has gone home. They finished all the checks for the evening and nothing turned up. He said that they could find nothing. He in particular was the one who went to the actual site where the reported possible problem was where someone smelled gas and nothing was found. Earlier on Jesse’s shift there was a possible gas leak reported when someone in the area smelled gas. JB said everything is buttoned up for the evening, everything OK. Munson |
| 2015 | Madison | They wanted to go from 36 million down to 34.5. Calhoun |
| 2032 | Minnegasco | Got a call from Daugherty. They wanted to cut their withdrawal at Grundy. They had an order in there for 34.033. They wanted to cut it by 20 million down to 14.033. I told him it wouldn’t be any problem. Calhoun |
| 2100 | Ogden | Shut unit #15 down. It was on Redfield going north. We had already cut Redfield by 50. Valve #90 that cracks the “BC” gas in from the south had come open about 40% so I wanted to see if the other two units on Redfield service could go ahead and pull it in. Calhoun |
| 1950 | Burdett | Unit 6 went down. I tried to remotely start unit 2. It didn’t get a successful start so Mark and Ike went out. At 2206 they called back and they did go ahead and put unit 1 on. Unit 3 is available as well as unit 6 if we need them. Everything is restored. Welsh |
| 2120 | Medford | Got a call from Minnegasco that said they were taking their withdrawal rate at Medford from 48 down to 10. Calhoun |
| 2300 | Guthrie Center | Shut the unit down. That’s because we were stacked up at Ogden. Need to get off the north end also. Calhoun |
| 2317 | Ogden | Shut unit #17 down and put units 15 and 13 on in its place. It was going east. Calhoun |
| 2321 | LS Power Whitewater | They called in and said they were on their way down and they didn’t have a start time until 2:00 to 3:00 tomorrow afternoon. Calhoun |
| 2350 | Ogden | Shut unit #13 down. I still needed to get off of the north and I didn’t need as much going east either. Calhoun |
| 0000 | Ventura | Took unit #15, the turbine, down. Calhoun |
| 0010 | Owatonna | Shut the unit down. I was recycling about 55% and still needed to get off of Farmington. Calhoun |
| 0030 | Farmington | Took unit #6 down. It was on the “BC” north. I was getting up on top and the turbine was slowing down. Also shut unit #3 down on the Willmar discharge because all of the other units were slowed down on bottom. Calhoun |
| 0035 | Lone Star Pecos | I received the OK from William with Lone Star to flow the Pecos point an extra four hours tonight on the batch process. This will include tomorrow’s small volume of 7 million. Munson |
| 0304 | Oasis Block 16 | I noticed that the Oasis volume hadn’t shut in when they accumed their nom for the day. I called Oasis and talked to James and he said that they are running extra until morning and this extra will be applied to the imbalance. Munson |
| 0350 | Farmington | Put unit #3 back on the Willmar discharge. We were starting to see some load pick up out there. Calhoun |
| 0445 |  | Got a call from NBPL saying that CC was wanting to start testing. I told him to let him know that we were in the process of making some setpoint changes at the interconnect to help get some gas going north and also to get off of Oakland. Calhoun |

slb