Services provided by Northern Natural Gas

And Transwestern Pipeline Company

- Enron Transportation Services

- Gas Control Event Log

0630 to 1830 Shift Sun., Dec. 30, 2001  ()

| 0730 | Macksville | Got a hold of the Macksville operator and requested the third turbine be put on. He is headed to the station now to get it warmed up and get it ready to go on line. Armitage |
| --- | --- | --- |
| 0700 | Tate | Have lost unit 4 at Tate. Trying to get a hold of the Tate operator now to send him to the station to get it back on line. Armitage |
| 1030 | Western Gas | Benedum – It looks like their interconnect is down. I called George over there at Benedum. He said they have a unit down and they are having some problems. They do have a mechanic there and they are going to let me know just as soon as they can if this is a long term thing or a short term thing. He sounded like it might be short term. I alerted my person at the Spraberry station, Ruben. Told him that he would be losing about 30 million right off the bat. He said that he will deal with that. I’ll let him know just as soon as I know something. Welsh |
| 1050 | Roger Mills Sandstone | We had some measurement problems out there this morning. It looked like it started in the wee hours of the night and probably around 0100 this morning that point started to flow the opposite direction. We have every reason to believe it didn’t. We talked to Transok. Their pressure was a lot higher than ours. We don’t see how it could have but the measurement indicates that it did so we don’t have true measurement. We had Ken with the Roger Mills team, our on call person today go out to the point physically. I did send a setpoint to shut it off. He got out there and verified that it is shut off. We got Transok’s gas control and Ken on a conference call with myself and we decided with the snow, the weather, dangerous conditions out there that it didn’t merit calling more people out there today and that since it’s only 10 million and we’re sort of believing that we may have gotten the 10 million from yesterday even though we can’t verify it with the measurement that we have. It’s a matter of 20 million that is due to NNG and they can make that up and they agreed they would. In light of that we left the point shut in today. Monday when everybody is at work and they have extra help they will determine what the measurement was and get the problem fixed. Welsh |
| 0625 | Madison | They wanted to go from 43 to a 55. Calhoun |
| 0830 | Terra Chemical | Got a call from the plant manager. He said they were going to be increasing their rate throughout the day from about 22 million up to about 36 where they normally run. He said they should be there within 12-24 hours. Calhoun |
| 0930 | Beatrice | They went out and got unit #24 back available. They put it on line and took #23 down. Also they put unit #19 on. Calhoun |
| 1020 | Ventura | Jim called and said he was out at the station looking the units over. Unit #11 had an oil leak. He said he was going to have to shut it down long enough to fix an oil line and it wouldn’t take more than about an hour. Calhoun |
| 1120 | Ventura | Jim got unit #11 back on line. Calhoun |
| 1230 | NSP Viking | Had an intraday nom come in for about 10 million at Chisago, receipt gas to us. I talked to NSP and also Kathy Washington. It does look like there is an imbalance out there where we owe them about 8.5 for the month, 12.5 cumulative, so we decided to leave it shut in to help to balance that point. Calhoun |
| 1130 | Heartland Corn | They increased their rate from 2.6 to 3.6. Calhoun |
| 1335 | LS Power | Whitewater – They called and said they were going to come on line. They were going to come on line on a minimum load and pull until about 10:00 tonight. Calhoun |
| 1335 | Waterloo | Unit #8 went down. I was able to reset it and got a clear. Calhoun |
| 1435 | Beatrice | Shut #22 down on the “D” line. It was a 2000 HP unit. They were out there earlier today and they had done some switching around. They put on unit #19 which was a 2000 HP earlier. Really didn’t need it because the “D” line was up on top and the other units were slowed down. Calhoun |
| 1450 | Belleville | Shut down units 1 and 2. Our loads out east weren’t really high enough to have 1 and 2 running so I shut them down. I’ll speed Galena up to make up the difference. Calhoun |
|  | NBPL | I got a call from Loren. He said they lost CS13. They got it back on at 1500. He said it was up on exhaust temperature. They were going to try to walk it up slowly so they didn’t knock it back down on exhaust temperature. Calhoun |
|  | Farmington | Shut down unit #6 at 1530. Calhoun |

1830 to 0630 Shift Sun., Dec. 30, 2001  (Hardy, Henley, Spain, Monden, Muntz)

| 1905 | Stevens Co. 6 | Unit #5 went down. Stan is going out. Spain |
| --- | --- | --- |
| 2008 | Diesart(??) IA TBS | It has a low battery voltage. Called OCC ad they got a hold of Jeff Korey. He said that their field team was aware of it and were on top of it. Monden |
| 2315 | Tate | I’m showing about three units down at Tate. I called OCC. I spoke to Lonnie. He is going out for us. Spain |
| 0040 | Finney Co. 3 | Unit #3 went down. Jay Harris is going to send someone out. Spain |
| 0145 | Tate | Lonnie called back in. He’s got those units back on line. He did have a freeze off on the panel going to unit 13. It took him awhile to thaw that out. Spain |
| 0205 | P3 | Unit 5 shut down. Jerry is going to go check it out. Muntz |
| 0220 | Finney Co. 3 | Dave Powers called back in. He informed me that they have a freeze up on a controller out there on unit 2 that went down earlier when I called him out. Actually I spoke to Jay Harris earlier and he called Dave Powers out. They’re going to leave that unit down. They need a space heater run on the equipment out there. Their policy is there needs to be two people present when the space heater is running so they are going to let it go until morning. Spain |
| 0350 | P3 | Unit 5 is back on the line. Muntz |
| 0355 | Warren Eunice | They’ve got an H2S alarm of 3.1 out there. Called and talked to the operator. He said they had a boiler shut down and they’ve lost everything out there. They are working on getting it back on right now. Right now the valve is shut from Warren Eunice and we’re not taking any gas from them at this time. Hardy |
| 0357 | Red Cedar | Scada is out at Red Cedar. I had Roderick try to restart it from here. He wasn’t able to. I called out Terry and he is going to go see if it’s got snow on the dish and warm boot it, get the scada to come back in. Muntz |
| 0400 | Sublette | Unit #23 went down. It was on the Haskell service. Steve is going out. Spain |
| 0230 | Cunningham | I gave Linda an order to increase the withdrawal rate from 225 to 275. Spain |
| 0434 | P3 | Unit 5 just went down again. I paged Jerry. Muntz |
| 0436 | Heartland Corn | Pressure dropped below 300# to a 298. Called the plant and left a message that the pressure had dropped below 300. Also coming out of Farmington down the Willmar line, it was discharging 927. I did inform Steve January of this situation. Monden |
| 0505 | Heartland Corn | Someone did answer my call this time, Paul Ecker. Informed him that the pressure was at 284. They said they would take the appropriate action, when their downstream pressure got close to 60# then he would leave that decision up to his boiler man of when to go over to an alternate fuel. Monden |
| 0515 | North Branch | Unit #2 was put on line to pump down the Benson lateral. Monden |
| 0525 | Koch Rosemont | The RTU is communicating back to Houston. Bob Tornio was out. Monden |
| 0535 | North Branch | Unit #2 went down. Tried to start 4 and 1. They did not come on line or even seem to indicate a start. Will leave it for the daylight operator to resolve. Monden |
| 0547 | Heartland Corn | Pressure is down to 255. Spoke with Steve January. He said they need to get it switched over to alternate fuel, one of their boilers. I spoke with Paul Ecker at Heartland Corn. He said they would get one of the boilers switched over to propane. At this time Winthrop pressure is 238. Monden |

slb