Services provided by Northern Natural Gas

And Transwestern Pipeline Company

- Enron Transportation Services

- Gas Control Event Log

0630 to 1830 Shift Sat., Jan. 5, 2002  (Henley, Spain, Monden, Hardy, Muntz)

| 0600 | Bushton | The turbine is down. I don’t think we’re going to need it for today’s gas day but we want to make sure that it is available so I’m going to have them check it out and put it back on line. Make sure that everything is working properly and then take it back off line. Henley |
| --- | --- | --- |
| 0610 | Macksville | Both units are down. Darryl Henning is going to go out and check it out for us. Henley |
| 0628 | Oakland | Called the OCC and they got a hold of the on call person Dana. He asked him to go out and shut the station down. Also at this time shut down unit 22 on Palmyra going up the “D” line to make room for this gas to roll back from Oakland. Line pack is 3595. Monden |
| 0630 | Phillips Fullerton | Called over and talked to Henry. It looks like they are going to come in behind their scheduled nom of 20. It looks like they are going to only make about 8-9 million of that. Henry said that they did fix the turbine and it’s back on line. It had been down most of the night is why they were running behind on their delivery to us. Hardy |
| 0637 | WFS Milagro | It just went to zero. I spoke with Warren. He said they had lost power and would get back on as soon as possible. Muntz |
| 0700 | Cunningham | Gave them on order to go to shut. Currently they have an order of 450 withdrawal. Henley |
| 0700 | Tescott | Taking down the “E” line unit. Henley |
| 0758 | Roger Mills | Talked to Jim. He is going to go out and get the Arkla Red Moon delivery started. Once he gets that established he said the gas coming from Beckham may fall off a bit. After awhile he’ll be able to start going on the ONG delivery for today and possibly tomorrow, the 2.9 scheduled for today and tomorrow there. Hardy |
| 0758 | Keystone | I’ve got a station alarm. Mark Ethridge is going to go out and check it out. Muntz |
| 0759 | SoCal | I just spoke with Don at SoCal. I let him know that we had lost approximately 300 million in receipt gas. Asked him if he was in a position to help us out with any payback for today. Don agreed to stay where he’s at, at the 473 rate and not increase up to the new day nom of 557.9 until after we get our receipt gas back. I did let Don know that if he got in a bind and needed to increase some to give us a call and we would work with him on that too. Muntz |
| 0805 | PG&E Topock | I just spoke with Albright. I asked him if he was in a position to help with payback. He said that they could take as much as 50 payback for the new day to help us out. New day nom shows to reduce down to 157.7. He said he could flow at 107.7 rate. If we get the gas back earlier and need to have him increase he said to give him a call and they could work with that. Also let him know that if he needed to increase the rate we could bump it up a little bit to help him out too. Muntz |
| 0825 | Jal | I talked to Carlos. He’s going to go out and put a second unit on for us. Sid Richardson volume goes up to 45 today. Hardy |
| 0815 | Finney Co. 2 | Received a dehy fail alarm. The on call is going to go check it out for us. Henley |
| 0835 | Station 9 | I just spoke with Dustin Jolly. He is going out to the station and bring it back on line. He is going to set it up to pull off of West Texas discharge up the Panhandle into the mainline. Muntz |
| 0836 | PNM | I just spoke with gas control at PNM. They are going to bring Thompson on at the top of the hour for 8 million. Requested that we do our balancing today at San Juan. Muntz |
| 0854 | PEPL Hansford | I just spoke with gas control at PEPL. They requested that we stay shut in today. They want to batch flow the point tomorrow. Nomination for current day is 16.528. Muntz |
| 0930 | Keystone | Clitus have the #1 unit down at Keystone. The Sid Richardson nom dropped down to 38 for the new day. The only unit on at Keystone is unit #3. Muntz |
| 0935 | Bloomfield | Jeff called and said that he is going to shut the electric unit down at the top of the hour. He had called the electric company and they had OK’d this. He said he will need to contact the electric company one hour before they can bring the unit back on later today. Jeff had spoken with WFS. They had told him that it will probably be close to dark this evening before they can get flow rate back up. Muntz |
| 1010 | WT2 | Unit 201 just went down. Clitus is going to go check it out and put it back on line. Muntz |
| 1055 | Ellis Co. 1 | Steve a page from unit 3 that it’s going down. He’s headed out to the station. Hardy |
| 1110 | Milagro | Had a conference call with Warren the gas controller and Gene the scheduler at WFS, along with Darrell Schoolcraft and Beverly Miller. They decided to cut Milagro from 301.552 down to 201.552. At this time Warren thinks Milagro will be back up to rate 5-6 hours. Muntz |
| 1115 | Station 2 | Hank called in and said they are trying to get unit 3 on at station 2. He said they are going to have to take unit 2 down and change out the turbo. It will take approximately eight hours to do this. Muntz |
| 1130 | Ogden | Put unit 13 on. Shut down unit 17 at 11:15. Monden |
| 1145 | Farmington | Shut down unit #6 the electric. Zone EF is 1069 line pack. Monden |
| 1150 | Ellis Co. 1 | Steve called. He’s got unit 3 back up. Hardy |
| 1155 | Beaver Co. 3 | Unit 3 is down. Stan is on his way. Hardy |
| 1242 | Faribault | Shut down unit due to pressure climbing on the discharge side at Farmington to help cut back on the flow going up to North Branch. Monden |
| 1313 | Waterloo | Shut down the station in order to try to get one of the Galena turbines off. Peak power load on the east leg. Monden |
| 1315 | Spraberry | Jay called and said unit 9 would not be available today. The part they got in was the wrong one. They’ll have to switch it out. They are not sure when they’ll be able to get the right part in. He said he would call with more details. Hardy |
| 1331 | Belleville | Shut down unit #2 and put #1 on due to the low volumes going out past Belleville. Monden |
| 1345 | Galena | Shut #2 down in order to get off of Belleville’s suction. Monden |
| 1410 | Jal | Talked to Rick who is helping Carlos bring unit 2 up to help make our Sid Richardson receipt. Unit is still down. They’ve run into bearing temp problems and high oil pressure problems. They are going out to get a new oil filter now to put on the unit. Then they are going to try to start it up to see if it will run to bring the Sid Richardson gas in. Hardy |
| 1523 | Amoco Whiting | Had OCC call on the low voltage there at the TBS. Clark Matzon called back. He said he would get a hold of his field technician and have him give me a call. Monden |
| 1523 | Mechanicsville TBS | Had OCC get a hold of the contact person for that who was Rick Dorsey. He said that a team member had gone out to all of the sites that had low voltages and couldn’t quite hit them all but they would be able to get it corrected on Monday. The voltage is reading 11.3. Monden |
| 1533 | Mapco Whiting TBS | Darrel Belt is going to go to the site and check it out and make sure all of the information is coming in correctly. Monden |
| 1540 | Jal | Rick and Carlos called. They finally got the on. Everything looks good. They are headed home. Hardy |
| 1557 | Redfield | Flow has dropped down to around 243 million. I called Redfield and spoke with Gary Maddux. It appears that the flow has dropped coming from Mt. Simon. Monden |
| 1636 | Redfield | Spoke with Gary Maddux on the Mt. Simon flow that dropped off. He said it’s a possible freeze off on lines to wells. He said that’s still in question. He said all of the flow did return coming from Mt. Simon. They are still checking it out. Monden |
| 1645 | NGPL Eddy Co. | NGPL Eddy Co. is currently flowing 47.5 Mcf. Terry Youngren is on location and they are testing the meter at this time. He said they would probably be testing for 2-3 hours. Muntz |
| 1634 | Burdett | Lost the Burdett station. I got a hold of the on call, spoke to Dennis. He’s going to go out and check it out for us. In the meantime I notified Holcomb, the Bushton operator and Products. Henley |
| 1730 | Beaver Co. 3 | Stan called. He’s got unit 3 back on line. Hardy |

1830 to 0630 Shift Sat., Jan. 5, 2002  (Barry, Hall, Ellington, Braswell)

| 2018 | Kermit | I’ve got an H2S alarm of .67 at the back pressure regulator. It came straight up so it looks to me like it’s probably a delmar problem. I notified OCC. Mark Ethridge called back to say he will go out and check it out. He’s pretty sure it’s a delmar problem but I told him to look at it and let me know what he’s got. Ellington |
| --- | --- | --- |
| 2140 | Ogden | Just got a call back from Stacey again. He had called me just a little bit ago. The generator fired off at 1927 tonight up there. Our alarms are not set for it to alarm like it should here. It comes in as a green alarm instead of a red one like it should. I’ll make a copy of it and send it back to Angela and Dale and see if they can figure out why it’s not, get it to where it alarms whenever the generator fires off. Anyhow, Stacey had gotten the call on it and he called the electric company. There is a transformer they’ve got to go out to the plant and work on. Hall |
| 2215 | Kermit | Mark called to say that the H2S alarm he’s not real sure if the delmar hung up or why. He said there is a dark spot on the tape but it just jumped right up there and jumped right back down. He’s going to watch a little bit and see what it’s doing. We haven’t had any H2S problems from anywhere else so we’re still thinking that the delmar malfunctioned and went through a cycle more than once. Ellington |
| 0349 | Eagle | Called Wisconsin Gas and talked to Jim Keating. He said he did show the flow going to zero, the pressures haven’t changed. He has a measurement tech headed out there to check it out for us. Hall |
| 0250 |  | Received a station alarm at station 8. Contacted the station and talked to Mick. He was saying that the battery charger is failing out there. The battery charger failure is the reason why the alarm is in. He checked with the control tech at Roswell and he said that they did have a spare battery charger but they are not going to be able to work on that until in the morning. Braswell |
| 0350 |  | Called the OCC for the on call for TW Beaver interconnect. It appears to have an increase in flow rate. The valve appears to come wide open. OCC called back and I got a hold of Stan. Told him what was going on out there at the interconnect. Right now we have a flow of about 100 million so apparently the valve has opened up real wide. He’s going out there and check that out. Braswell |
| 0430 | Eagle WI | Called the OCC and they got a hold of Dave the on call. He said he didn’t know too much about the point. The reason for the call is the flow rate for some reason at 0330 went to zero. I’ve been talking to Jim with Wisconsin Gas. He’s getting a tech headed out that direction. Dave said that he would see if he could get a hold of Lenny or another fellow, one of the techs who takes care of that point and have him go out and check it out also. Hall |

slb