| Garrad Hassan and Partners Ltd The Coach House Folleigh Lane Long Ashton Bristol BS18 9JB ENGLAND |  | Tel: +44 (0)1275 394 360 Fax: +44 (0)1275 394 361 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| To: | Jay Godfrey, Jeff Maurer |  |  |  |  |  | Ref: 2624/B/016 |
| Company: | Enron Wind |  | Fax: |  | 00 1 213 452 4894 |  |  |
| CC: | Rich Simon |  | Fax: |  |  |  | Date: 05 Jan 01 |
|  | Andrew Tindal |  |  |  |  |  |  |
| From: | Adam Schwarz |  |  |  |  |  | Pages: 5 (including cover page) |
| Topic: | Indian Mesa II update |  |  |  |  |  |  |

# Issued via email – 05 Jan 01

Dear Jay

Further to my previous correspondence dated 02 Jan, we have completed our update of the predicted wind regime and energy production of the proposed Indian Mesa II Wind Farm (IM II).  There is an overall increase in the predicted energy production presented which has resulted from the following amendments to our analysis:

- As previously stated, the analysis methodology for IM II has been updated using mast 0642 as a site reference to allow incorporation of data recorded since the removal of mast 0641.  The methodology employs an hourly, directional correlation between King Mountain and 0642 to establish the long-term mean wind speed at 0642, with the results from daily and monthly correlations supporting the result presented.  All available data from the remaining site masts have then been correlated to 0642 on an hourly basis.

- The cause of the discrepancy observed in the monthly mean wind speeds at 0642 for March and April 1999 as calculated by GH and Rich Simon (RS),  has been identified and corrected for.  The lower mean wind speeds observed by GH were the result of ‘mislabelling’ of the first raw data file received for 0642.  Correcting the 0642 data set and updating the correlation to King Mountain has increased the predicted long-term mean wind speeds by approximately 2 %.

- The additional discrepancy in the monthly mean wind speeds for August 2000 at all masts was the result of the absence of explicit header information detailing the transfer functions applied to the supplied data for that month.  Consequently, GH had assumed the same transfer function as had been applied to the preceding data, the effect of which was to apply the consensus offset of 0.35 m/s, twice.

- The curtailment losses have been assessed based on the algorithm supplied by ENRON and a wind rose representative of IM II.

Please note that the results presented must be considered draft until issued in a formal report.

Yours sincerely

Adam Schwarz

## Projected energy production

The predicted energy output of the proposed Indian Mesa II Wind Farm is summarised in the table below:

| Rated Power | 135 | MW |
| --- | --- | --- |
| Ideal output | 577.2 | GWh/annum |
| Topographic effect | 102.9% | Calculated |
| Wake effect | 93.6% | Calculated |
| Electrical efficiency | 98.0% | Typical value |
| Availability | 97.0% | Typical value |
| Icing and blade degradation | 99.0% | Typical value |
| High wind hysteresis | 99.9% | Typical value |
| Substation maintenance | 99.8% | Typical value |
| Utility downtime | 100.0% | Must be considered on a site specific basis |
| Power curve adjustment | 100.0% | Not considered by GH |
| Columnar control loss | 99.4% | To be updated |
| Net output | 518.5 | GWh/annum |

The ideal energy production is the theoretical output of the wind farm with the hub-height wind speed at the mast location applied uniformly across the whole site.  The values for topographic and array effect have been calculated using standard GH methods.  Other assumptions are as defined in our report 2624/BR/01.

The standard error associated with the updated prediction of energy capture is yet to be calculated.

| Turbine Number | Grid Easting [m] | Grid Northing [m] | Mean hub height wind speed1 [m/s] | Energy output2 [GWh/annum] |
| --- | --- | --- | --- | --- |
| 1 | 779119 | 3422100 | 8.5 | 5.8 |
| 2 | 779226 | 3422285 | 8.7 | 5.9 |
| 3 | 779385 | 3422401 | 8.8 | 6.2 |
| 4 | 779745 | 3422515 | 8.7 | 6.0 |
| 5 | 779828 | 3422707 | 8.9 | 6.2 |
| 7 | 780369 | 3422416 | 8.7 | 6.0 |
| 8 | 780543 | 3422539 | 8.5 | 5.7 |
| 9 | 780709 | 3422673 | 8.6 | 6.0 |
| 13 | 778186 | 3422841 | 8.4 | 5.5 |
| 14 | 778346 | 3422983 | 8.3 | 5.3 |
| 15 | 778677 | 3423495 | 8.7 | 5.8 |
| 17 | 779353 | 3423623 | 8.6 | 5.6 |
| 18 | 779460 | 3423753 | 8.8 | 5.9 |
| 19 | 779584 | 3423863 | 8.9 | 6.1 |
| 20 | 779717 | 3423972 | 8.8 | 6.0 |
| 21 | 777191 | 3423530 | 8.7 | 5.9 |
| 22 | 777373 | 3423644 | 8.6 | 5.8 |
| 23 | 777573 | 3423724 | 8.5 | 5.6 |
| 24 | 777781 | 3423772 | 8.7 | 5.7 |
| 25 | 777988 | 3423819 | 8.7 | 5.7 |
| 26 | 778115 | 3423911 | 8.8 | 5.7 |
| 27 | 778238 | 3424003 | 8.8 | 5.8 |
| 28 | 778327 | 3424176 | 8.9 | 5.9 |
| 29 | 776153 | 3423544 | 8.7 | 6.0 |
| 30 | 776368 | 3423566 | 8.7 | 5.9 |
| 49 | 774014 | 3423693 | 9.4 | 6.9 |
| 50 | 774260 | 3423720 | 9.2 | 6.6 |
| 51 | 774486 | 3423706 | 9.1 | 6.5 |
| 52 | 774790 | 3423693 | 9.0 | 6.4 |
| 53 | 775011 | 3423722 | 8.9 | 6.1 |
| 54 | 775148 | 3423825 | 8.7 | 6.0 |
| 55 | 775284 | 3423927 | 8.7 | 5.9 |
| 56 | 775421 | 3424029 | 8.7 | 5.9 |
| 57 | 775558 | 3424131 | 8.7 | 5.8 |
| 58 | 775719 | 3424237 | 8.8 | 5.8 |
| 59 | 775882 | 3424346 | 8.9 | 6.0 |

Note 1	Wind speed at hub height, not including wake effects.

Note 2        Individual turbine output includes topographic and array effects only.

Proposed turbine layout with individual wind speed and energy output for the Indian Mesa II Wind Farm.

| Turbine Number | Grid Easting [m] | Grid Northing [m] | Mean hub height wind speed1 [m/s] | Energy output2 [GWh/annum] |
| --- | --- | --- | --- | --- |
| 60 | 771501 | 3424273 | 9.2 | 6.5 |
| 61 | 771622 | 3424359 | 9.2 | 6.4 |
| 62 | 771743 | 3424444 | 9.2 | 6.3 |
| 63 | 771864 | 3424530 | 9.2 | 6.4 |
| 64 | 772344 | 3424228 | 9.4 | 6.7 |
| 65 | 772456 | 3424361 | 9.5 | 6.8 |
| 66 | 772701 | 3424390 | 9.4 | 6.6 |
| 67 | 772948 | 3424389 | 9.7 | 6.9 |
| 68 | 773228 | 3424402 | 9.4 | 6.6 |
| 69 | 773614 | 3425211 | 9.0 | 6.0 |
| 70 | 773861 | 3425223 | 9.1 | 6.0 |
| 71 | 774098 | 3425216 | 9.0 | 5.9 |
| 72 | 774441 | 3424945 | 9.2 | 6.2 |
| 73 | 774626 | 3425034 | 9.3 | 6.3 |
| 74 | 774736 | 3425276 | 9.3 | 6.3 |
| 75 | 774839 | 3425469 | 9.6 | 6.6 |
| 76 | 775007 | 3425541 | 9.7 | 6.7 |
| 77 | 775133 | 3425634 | 9.8 | 6.9 |
| 78 | 771406 | 3425056 | 9.3 | 6.2 |
| 79 | 771533 | 3425151 | 9.3 | 6.2 |
| 80 | 771661 | 3425246 | 9.3 | 6.3 |
| 81 | 771788 | 3425342 | 9.3 | 6.4 |
| 82 | 771917 | 3425437 | 9.3 | 6.3 |
| 83 | 772039 | 3425540 | 9.3 | 6.3 |
| 84 | 772179 | 3425616 | 9.4 | 6.4 |
| 85 | 772295 | 3425731 | 9.4 | 6.4 |
| 86 | 772415 | 3425837 | 9.6 | 6.6 |
| 87 | 772565 | 3425914 | 9.6 | 6.6 |
| 88 | 772929 | 3425718 | 9.4 | 6.6 |
| 89 | 772828 | 3426209 | 9.1 | 6.1 |
| 90 | 773093 | 3426203 | 9.2 | 6.2 |
| 91 | 773274 | 3426239 | 9.2 | 6.2 |
| 92 | 773429 | 3426351 | 9.4 | 6.5 |
| 93 | 773630 | 3426443 | 9.4 | 6.5 |
| 96 | 772821 | 3426734 | 8.9 | 5.7 |
| 100 | 771482 | 3426901 | 9.5 | 6.5 |

Note 1	Wind speed at hub height, not including wake effects.

Note 2        Individual turbine output includes topographic and array effects only.

Proposed turbine layout with individual wind speed and energy output for the Indian Mesa II Wind Farm.

| Turbine Number | Grid Easting [m] | Grid Northing [m] | Mean hub height wind speed1 [m/s] | Energy output2 [GWh/annum] |
| --- | --- | --- | --- | --- |
| 102 | 771485 | 3427416 | 9.3 | 6.4 |
| 103 | 771643 | 3427552 | 9.6 | 6.7 |
| 104 | 771674 | 3427815 | 9.6 | 6.6 |
| 105 | 771840 | 3427940 | 9.6 | 6.6 |
| A-106 | 774533 | 3424414 | 9.0 | 5.9 |
| B-107 | 774239 | 3424463 | 9.1 | 6.1 |
| C-108 | 771797 | 3426161 | 9.2 | 5.9 |
| D-109 | 771936 | 3426317 | 9.1 | 5.9 |
| H-113 | 771384 | 3426347 | 8.9 | 5.9 |
| I-114 | 778932 | 3422757 | 8.6 | 5.5 |
| J-115 | 775175 | 3424655 | 9.1 | 5.9 |
| K-116 | 775278 | 3424939 | 9.3 | 6.3 |
| D-117 | 773615 | 3426714 | 9.5 | 6.6 |
| C-118 | 772824 | 3426917 | 9.1 | 5.9 |
| B-119 3 | 772282 | 3426585 | 9.3 | 6.3 |
| A-120 | 772400 | 3426858 | 9.3 | 6.3 |
| E-121 | 774541 | 3425882 | 9.6 | 6.4 |
| F-122 | 774735 | 3426087 | 9.8 | 6.8 |

Note 1	Wind speed at hub height, not including wake effects.

Note 2        Individual turbine output includes topographic and array effects only.

Note 3        Assumed representative location for turbine B-119.

Proposed turbine layout with individual wind speed and energy output for the Indian Mesa II Wind Farm.

| Mast number | Measurement height (m) | Predicted long term mean wind speed (m/s) |
| --- | --- | --- |
| 0641 | 40 | 9.3 |
| 0642 | 40 | 8.7 |
| 0643 | 40 | 9.0 |
| 0651 | 40 | 8.6 |
| 0652 | 65 | 8.8 |
| 0653 | 10 | 8.3 |
| 0654 | 40 | 8.7 |
| 0655 | 40 | 8.6 |
| 0656 | 40 | 8.5 |
| 0657 | 40 | 8.1 |
| 0658 | 40 | 8.0 |

### Predicted long term mean wind speeds at each of the mast locations