# Updated 3/14/02

Using the 1.5 turbine simulator we have verified that the following counters increment during the listed faults or turbine statuses:

| Counter | Fault/status number | Description |
| --- | --- | --- |
| System OK | 1 2 3 6 20 21 87 94 109 110 147 152 153 161 166 181 182 183 184 216 | -program start PLC -no error -manual stop -system OK -cable twisting right -cable twisting left -restart time delay -control call -generator carbon dust filter dirty -speed in tower resonance range -load shutdown -obstruction light error/failure -brush wear generator -over voltage protection triggered* -normal operation -idling position -start up -load operation** -shutdown -obstruction light switch over to auxiliary lamps |
| Down time | 13 14 15 16 17 19 22 23 25 35 45 52 57 59 60 63 64 65 71 75 76 77 81 82 86 88 97 98 99 100 101 102 103 105 106 107 113 114 115 118 124 125 129 134 141 142 144 145 176 177 | -asymmetric generator current -generator over speed -rotor over speed -rotor speed monitor -centrifugal switch -maximum motor power -yaw drive end position -peak value for excessive output -no speed reduction with primary braking (pitch) -emergency stop -hydraulic pump time too long -gearbox oil pressure too low -ratio generator/rotor speed -vibration switch -yaw limit switch activated -safety chain -motor protection -main switch activated -gearbox oil soiled (shutdown) -generator bearing A over temperature -generator bearing B over temperature -gearbox oil over temperature -shaft bearing over temperature -yaw motor over temperature -brake pads worn, secondary brake -multiple over temperature shutdown -generator cooling air over temperature -gearbox bearing over temperature -generator 1 over temperature -generator 2 over temperature -motor protection fuse -motor protection top cabinet -generator 3 over temperature -rotor CCU fault voltage -rotor CCU fault current -rotor CCU fault temperature -line CCU fault voltage -line CCU fault current -line CCU fault temperature -emergency stop top-box -pitch overrun 0° -pitch overrun 90° -generator speed implausible -battery charging voltage not o.k. -rotor CCU collective fault -line CCU collective fault -blade angle asymmetry -blade pitch control deviation -drive train vibration -tower vibration |
| Line out time | 8 116 117 | -over voltage -line fault voltage -line fault frequency |
| Weather out time | 7 78 146 | -storm shutdown -outside temperature too low -turbine stopped due to calm |
| External stop time | 58 172 | -demand to stop by an external device -ice sensor alarm |
| Maintenance time | 47 108 148 155 171 185 186 187 188 189 191 | -hydraulic service switch top cabinet -rotor locking -generator fan service switch -maintenance -service key brake release* -manual operation pitch* -manual operation speed* -manual operation torque* -manual operation, line separation* -manual operation yaw* -manual operation generator fan* |
| Repair time | 156 | -repair |

* - Fault/status 161, 171, 185, 186,187, 188, 189, 191 increment counters that may not be correct

** - Status 183- “load operation” also increments the “operational time” counter

Faults/turbine statuses that cannot be duplicated on the simulator:

| Counter (theoretical) | Fault/status number | Description |
| --- | --- | --- |
| System OK | 4 5 44 89 95 138 162 165 167 169 170 173 193 199 200 204 | -remote stop -remote start -hydraulic filter polluted (warning) -gearbox oil dirty (warning) -PC restart -temperature warning pitch motor -fault battery charge switching -service switch pitch -voltage limitation activated -waiting for gearbox oil pressure -increasing speed with falling blade angle -low-noise operation -marine obstruction light (offshore only) -test fault CCU cooling system -pre-heating CCU cooling system active -FastBus service mode |
| Down time | 24 27 28 31 34 36 38 41 42 43 46 51 53 54 55 56 62 83 112 119 120 121 122 123 130 131 132 133 135 135 136 137 139 140 143 149 150 151 154 157 163 180 190 194 195 196 197 198 201 202 203 205 206 207 208 209 212 213 214 | -primary braking time too long -secondary braking time too long -no speed reduction with secondary braking -timeout yaw counter -brake not released secondary brake -speed with braked turbine -secondary brake test -vibration sensor defect -wrong yaw drive direction -hydraulic filter polluted (switch off) -hydraulic pump (interval) time too short -gearbox oil level too low -wind vane defect -anemometer defect -rotor pulse sensor defect -generator pulse sensor defect -PLC fault collection -gearbox bearing B over temperature (offshore only) -response signal from CCU -pitch controller timeout -communication fault pitch controller -axle disturbance 1 pitch controller -collective fault pitch controller -gearbox oil cooler switch contact -braking time blade 1 too high -braking time blade 2 too high -braking time blade 3 too high -battery charging rotor blade drive -battery charging rotor blade drive -battery test -limit switch rotor blade 0° defect -limit switch rotor blade 90° defect -over temperature pitch motor -motor protection pitch motor -pulse sensor rotor monitor defect -axle 2 fault, pitch controller -axle 3 fault, pitch controller -response circuit breaker generator brush -generator cooling water pressure/level not o.k. -brake does not close -torque deviation -wind deviation -temperature error container -by-pass filter soiling -gearbox pressure loss by-pass filter -pre-heating fault CCU cooling system -over temperature CCU cooling system -pressure fault CCU cooling system -pre-heating CCU cooling system active -PLC module failure -fault temperature measurement -over temperature top box (EW900 only) -gearbox pressure too high (EW900 only) -ground fault LVMD (EW1.5/70.5(60Hz) only) -no activity CAN-Bus CCU -no activity CAN-Bus MFR13 -battery voltage low- axis 1 -battery voltage low- axis 2 -battery voltage low- axis 3 |
| Line out time | 9 | -under voltage |
| Weather out time | 84 | -gearbox oil temperature to low |
| External stop time |  |  |
| Maintenance time | 164 | -maintenance switch pitch |
| Repair time |  |  |

4- remote stop

5- remote start

9- under voltage

24- primary braking time too long

27- secondary braking time too long

28- no speed reduction with secondary braking

31- timeout yaw counter

34- brake not released secondary brake

36- speed with braked turbine

38- secondary brake test

41- vibration sensor defect

42- wrong yaw drive direction

43- hydraulic filter polluted (switch off)

44- hydraulic filter polluted (warning)

46- hydraulic pump (interval) time too short

51- gearbox oil level too low

53- wind vane defect

54- anemometer defect

55- rotor pulse sensor defect

56- generator pulse sensor defect

62- PLC fault collection

83- gearbox bearing B over temperature (only offshore)

84- gearbox oil temperature to low

89- gearbox oil dirty (warning)

95- PC restart

112- response signal from CCU

119- pitch controller timeout

120- communication fault pitch controller

121- axle disturbance 1 pitch controller

122- collective fault pitch controller

123- gearbox oil cooler switch contact

130- braking time blade 1 too high

131- braking time blade 2 too high

132- braking time blade 3 too high

133- battery charging rotor blade drive

135- battery test

136- limit switch rotor blade 0° defect

137- limit switch rotor blade 90° defect

138- temperature warning pitch motor

139- over temperature pitch motor

140- motor protection pitch motor

143- pulse sensor rotor monitor defect

149- axle 2 fault, pitch controller

150- axle 3 fault, pitch controller

151- response circuit breaker generator brush

154- generator cooling water pressure/level not o.k.

157- brake does not close

162- fault battery charge switching

163- torque deviation

164- maintenance switch pitch

165- service switch pitch

167- voltage limitation activated

169- waiting for gearbox oil pressure

170- increasing speed with falling blade angle

173- low-noise operation

174- over temperature transformer warning (offshore only)

175- over temperature transformer disturbance (offshore only)

180- wind deviation

190- temperature error container

192- wrong parameter check sum

193- marine obstruction light

194- by-pass filter soiling

195- gearbox pressure loss by-pass filter

196- pre-heating fault CCU cooling system

197- over temperature CCU cooling system

198- pressure fault CCU cooling system

199- test fault CCU cooling system

200- pre-heating CCU cooling system active

201- PLC fault 24V supply

202- PLC module failure

203- fault temperature measurement

204- FastBus service mode

205- over temperature top box (EW900 only)

206- gearbox pressure too high (EW900 only)

207- ground fault LVMD (EW1.5/70.5(60Hz) only)

208- no activity CAN-Bus CCU

209- no activity CAN-Bus MFR13

212- battery voltage low- axis 1

213- battery voltage low- axis 2

214- battery voltage low- axis 3

215- direction dependent shut-down

217- end of parameter state service

218- frequent cut-ins

219- Ice sensor fault

220- external Stop caused by curtailment

221- external power limitation