East Cost Power

PI Installation

Progress Report and Budget Estimates

Synopsis

The purpose of this project is to provide operations data from the three East Coast Power (ECP) plants in Linden, Bayonne and Camden, New Jersey to Enron's East Power Trading desk in Houston.  In addition, the data will be made available to ECP personnel and other interested parties as required.  The PI-Data Archive (PI) data historian from OSI Software, Inc. will be used to store the data collected from each plant's DCS.  This report covers the work done to date and cost estimates for future work.

PI is a time-series based data historian used widely in the chemical process and electrical industries.  It is currently installed at Enron's peaker plants and has been used successfully to monitor operational and commercial parameters.  PI gets its data through interfaces to the various plant DCS's on a read-only basis and does not affect plant operations.  PI is a client-server based application with a PI server located at each remote site, a central PI server located in Houston and client applications that allow for the visualization and reporting of PI data.  All of the client applications read data from the central server located in Houston.  In order to view the data, client software must be loaded on the user's PC.  A project is currently underway to have PI data available over the Internet through common Web browsers.  This will negate the need to have the client software installed.

In the initial phase of the project, servers were installed at each ECP plant and the PI server software was loaded on each.  In addition, the PI server at each plant was connected to the DCS or an evaluation was made to determine what is necessary to make the connection.  Ben Jordan from Enron's Remote Network Services group traveled to Linden, Bayonne and Camden to install the server hardware in existing server racks at each plant.  Rick Broussard, Alan Chen and Ramesh Swaminathan from Enron - East Power Trading, then went to each plant to install the software and connect to the DCS's.  A detailed discussion of the results follows in later paragraphs.  In a nutshell the PI servers were successfully connected to plant DCS's at Linden and Camden. Current work is underway to configure the PI database to read the values from the Linden and Camden plants.  The Bayonne plant will need additional hardware and software for a connection to be made.

Plant Details

Linden

The Linden plant has a MAX I DCS from Leeds & Northrop.  A turbine monitoring system developed by Enter/GE was originally installed at the plant but never operated successfully.  However, the Enter system came with a custom PI interface and PI server that allowed communications between the DCS and PI.  This system connects to the DCS through a serial communications port on a gateway PC to the MAX1.  Data is collected by a custom software package running on a DOS computer connected by a serial port to the gateway PC.  The PI server and client PC's were connected to the DOS PC via a 10Base2 Ethernet network.  This configuration as installed by Enter would run for approximately two hours at a time before crashing.  It was determined that the probable cause of the crashes was an overload of the 10Base2 network.  The network was re-configured by adding a 10BaseT Hub and isolating the 10Base2 network to the DOS computer and the PI server. Although this system has apparently been made operational, it is recommended that the existing PI server and Enter software be updated to the latest versions if possible.  See figure 1 below.

Since the Enter software included a PI server and interface to the DCS, the new PI installation used this interface to collect PI data for the new server.  The diagram in figure 2 below shows the data flow from the DCS to the PI servers.  As mentioned earlier, all PI data will be read from the Houston PI server via client software.  The client software has not yet been installed at the Linden plant.

Figure 1 Linden DCS-PI Network

Figure 2 Linden Data Flow Diagram

Figure 2 - Linden Data Flow Diagram

Bayonne

The Bayonne plant has a DCS based on a MicroVAX II with a GE Datatronics historian.  This DCS is a legacy system and has no interface to PI nor does GE support it.  During the plant visit, it was determined that it was possible to write a program on the VAX that would allow plant data to be written to a text file.  It may be possible to then write this text file out over a serial port on the VAX to the PI server.  Future work will be needed to write the software on the VAX to read the necessary DCS values and make the serial connection.  The proposed network diagram is shown in Figure 3 and the data flow diagram is shown in Figure 4 below.

Figure 3 - Bayonne DCS - PI Network

Figure 4 - Bayonne Data Flow Diagram

Camden

The Camden plant has a MAX 1000 DCS from Leeds & Northrop.  The existing system has an ODBC interface that stores data in an MS Access database.  A PI-RDBMS interface available from OSI Software was installed to extract the data from the Access database into PI.  At the Camden plant, the PC with the PI database is concurrently connected to the DCS on a 10Base2 network and to the corporate Intranet.  This PC was directly accessible to PI through the corporate net.  The network diagram for the Camden plant is shown in Figure 5 and the data flow diagram is shown in Figure 6 below.

Figure 5 - Camden DCS-PI Network

Figure 6 - Camden Data Flow Diagram

Progress to Date

Since the initial installation, the tag list from Linden has been reviewed and is being configured on the PI server in Houston.  The Camden tag list has been configured on the PI server in Houston and is now collecting values.  As mentioned above, more work is needed on the Bayonne VAX system to get the tag values out of the VAX and into the PI server.  No additional progress has been made at Bayonne.

Costs to Date

PI is sold on a per tag basis. Tags include those for collected data as well as any tags used for calculated data.  Early estimates are that 150 tags will be needed for the three ECP plants.  Enron has an agreement with OSI to purchase tags for $6.00 (Six dollars) each.  In addition to the tags, there is a cost for each interface of $5,000.00.  It will take six interfaces to connect the ECP plants.  OSI charges a 15% annual maintenance fee for all purchased components.  The materials costs including hardware are listed below in Table 1:

| Materials |  |  |  |
| --- | --- | --- | --- |
| Servers | 3 | $ 5,700 | $ 17,100 |
| PI Tags | 150 | $ 6 | $ 900 |
| PI Interfaces | 6 | $ 5,000 | $ 30,000 |
| Shipping | 3 | $ 800 | $ 2,400 |
| Total |  |  | $ 50,400 |
| PI Maintenance/Yr. | 15% | $ 30,900 | $ 4,635 |

Table 1 - ECP Hardware and Server Software Costs

Labor and expenses to date are itemized below in Table 2:

| Labor & Expenses |  |  |  |
| --- | --- | --- | --- |
| Network Support |  |  | $ 1,200 |
| Linden PI Setup |  |  | $ 6,000 |
| Bayonne PI Setup |  |  | $ 1,500 |
| Camden PI Setup |  |  | $ 3,500 |
| Travel Expense |  |  | $ 12,000 |
| Total |  |  | $ 24,200 |

Table 2 - ECP Labor & Expenses to Date

As mentioned above, the ultimate goal of the East Power Trading group is to have all PI data available to users via a Web interface.  However, until the development work is complete, PI client software must be installed at each client workstation to view the data. The client software consists of PI-Data View, an MS Excel Add-in that allows PI data to be viewed and analyzed via Excel, and PI-Process Book, PI client software that allows the creation of text and graphic displays to view the software.  The PI Client Licenses are approximately $1800.00 per license.  One license is needed per PC on which the software is installed.

The PI data from the existing Enron peaking plants is displayed on PI-Process Book screens in a standard text/tabular format.  The data includes a combination of captured values such as MW output, ambient temperature, etc., and calculated values such as heat rate, fuel rate, etc.  It is anticipated that similar screens will be developed for the output of the ECP plants.  Below in Figure 7 is an example of one of the Enron peaker PI displays:

Remaining Work

Figure 7 - Enron Peaking Plant PI Display

The tag list from the Linden plant needs to be finalized and configured in the PI database.  The Camden database is essentially configured and all available tags are being collected.  As mentioned above, the Bayonne plant will require additional programming to get the data from the VAX to the PI system and the physical interface needs to be installed.

Screen development should proceed quickly once the tags have been configured.  There is a possibility that some data points that are not collected in the DCS may have to be either added or inferred from other points.  An example of this is GT rpm.  At the peaker plants, rpm is used as a logic value for some of the calculated points.  For instance, heat rate is not calculated unless the rpm's are greater than 100.  In the GE systems, firing temperature is calculated internally and is not available to the DCS.  This has to be inferred from exhaust temperature.

Below, in Table 3 is a cost estimate for the remaining materials and Table 4 is a cost estimate for remaining labor & expenses:

| Materials |  |  |  |
| --- | --- | --- | --- |
| VAX 56K Modem | 1 | $ 300 | $ 300 |
| VAX Serial Cable & Installation | 1 | $ 500 | $ 500 |
| PI API Node | 2 | $ 500 | $ 1,000 |
| PI Client Software (2 per plant) | 6 | $ 1,800 | $ 10,800 |
| Total |  |  | $ 12,600 |
| PI Maintenance/Yr. | 15% | $ 11,800 | $ 1,770 |

Table 3 - Estimated Remaining Materials

| Labor & Expenses |  |  |  |
| --- | --- | --- | --- |
| Network Support |  |  | $ 400 |
| Complete Linden Configuration |  |  | $ 3,000 |
| Screen Development & Testing |  |  | $ 4,800 |
| Bayonne Programming & Tag Configuration |  |  |  | $ 6,000 |
| Misc. (Additional Tags, configuration, etc.) |  |  |  | $ 3,000 |
| Travel Expense |  |  | $ 3,000 |
| Total |  |  | $ 20,200 |

Table 4 - Estimated Remaining Labor & Expenses

Summary

The PI server installation has been performed at all three plants.  The configuration of the Linden and Camden databases should be completed by the end of August 25.  The development of the PI displays should be completed by the end of September 1.  Concurrently, work will begin on the Bayonne VAX software.  Barring any unforeseen problems, the Bayonne software and database configuration should also be completed by September 1.

There may be some follow up work setting up additional tags not currently being reported to each plant's DCS.  These tags will have to be evaluated on a case by case basis.

To date approximately $50,000 on materials and $24,000 on labor and expenses has been spent.  It is estimated that an additional $33,000 will be needed to complete the project.  An annual fee of approximately $6,500 to OSI Software will cover Maintenance and Support.

Enron proposes that all costs to the ECP plants are deferred until such time as the system has been installed and evaluated.  If ECP wishes to incorporate the system, the costs will be invoiced accordingly.  If ECP chooses not to use the system, Enron will cover all costs, including maintenance fees and access will be limited to Enron personnel only.