Direct FuelCell® Powerplant

Preliminary Specification

1.0	INTRODUCTION

This document summarizes the design specifications for FCE’s 2MW and 2.4MW Direct FuelCell (DFC®) powerplants. The physical configuration of the powerplants are identical, and they differ only in the output capabilities of the installed stack modules.  The powerplant consists of power generation and balance of plant skids arranged to provide sufficient access while taking up a minimum of footprint. The major elements of the powerplant include:

- DC Power Section: Two 4-stack DFC® modules, which generate DC power

- Power Conversion Skid: DC to AC conversion and voltage step-up transformation

- Heat Recovery Unit (HRU) Skid: Fuel preheat, steam generation, and fuel cleanup

- Oxidant Supply:  Air preheat using catalytic oxidation of anode exhaust residual fuel

- Water Treatment and Storage and Instrument Air Skid

- Control System and Interface Panel

The arrangement of the system is shown in Figure 1:

Water Treatment and Storage

Power Conversion and Transformer

Control

Heat Recovery Unit Behind Oxidant Supply Skid

Utility Interconnect & Switchgear

Figure 1

4-stack module

Oxidant Supply Skid

DFC® Powerplant

As shown in Figure 1, the powerplant is configured into a few skids which contain logically grouped subsystems.  The arrangement shown in Figure 1 represents the design developed in detailed design sutdies which have proceeded just short of equipment procurement.  Design refinement due to vendor feedback during the procurement phase may lead to some adjustment of the arrangement as the design is optimized.

The DC Power section is comprised of two fuel cell modules, each of which contains four DFC® stacks, and the associated piping and instrumentation to deliver gases to the stacks.  The modules are cylindrical, truck-transportable units which are internally insulated to maintain the outer skin of the container near ambient temperature.  The modules are fed with a hot fuel/steam mixture from the HRU skid, and with heated air  from the oxidant supply skid.  These inputs are used to produce DC power, and two exhaust streams (fuel and air) which are used for reactant preheat.

The Power Conversion Skid contains the inverter system, which converts the stack DC to AC power, and transformers which step the AC up to 480Volts. The Control System skid contains the plant control hardware, the local user interface panel. and any equipment needed for interfacing with a broader facility supervisory control system.

The Heat Recovery Unit Skid takes treated cold water and fuel and produces a fuel/steam mixture at the appropriate temperature (~1000 oF) for delivery to the fuel cell stacks. This skid also contains the fuel cleanup system, and any other fuel treatment reactors which may be needed (eg deoxidation reactors for peak shaving natural gas).  It also contains several cylinders of nitrogen, which is used during plant start, shutdown, and maintenance.

The Oxidant Supply Skid consists of a packaged catalytic reactor and cold air supply blower (and associated local controls, etc).  It is fed with the spent fuel exhaust from the fuel cell modules.  The residual fuel in this exhaust (typically 20 to 30 percent of the fuel input) is used in the catalytic reactor to heat the cold air up to the desired temperature for delivery to the fuel cell modules.  Cold air is mixed with residual fuel, sent through the catalyst, and the flue gas from the catalyst is sent to the fuel cell modules as the oxidant inlet stream.

The Water Treatment and Storage Skid treats supplied water to provide a quality suitable for use in the steam generator.  The skid includes a storage tank which holds a 12 hour supply of treated water.  An instrument air compressor is also packaged on the water treatment skid.

The powerplant's operating characteristics and performance presented in this document reflect both current and advanced fuel cell technology that FCE expects to achieve into the near future (through 2005).  The operating characteristics listed here are expected values. Guaranteed values for certain performance parameters are identified specifically in the contract.

2.0	PLANT PERFORMANCE AND OPERABILITY CHARACTERISTICS

  - Overall Design Specifications:

The following target specifications have been established for the 2MW and 2.4MW:

### Table 1, Plant Specifications

|  | Initial 7 units, 2MW Maximum Unit Rating |  | Subsequent Units 2.4MW Maximum Unit Rating |  |
| --- | --- | --- | --- | --- |
| # Plot Area |  |  |  |  |
| Height | 25 | feet | 25 | feet |
| Width | 54 | feet | 54 | feet |
| Length | 83 | feet | 83 | feet |
| Power Output |  |  |  |  |
| Power at Plant Rating | 2000 | kW | 2400 | kW |
|  | up to 3300 | kVA | up to 3300 | kVA |
| Voltage | Site dependent |  | Site dependent |  |
| Frequency | 60 | Hz | 60 | Hz |
| Power Quality | Per IEEE 519 |  | Per IEEE 519 |  |
| Efficiency At Rated Output | 50% | LHV | 52% | LHV |
|  | 6,790 | Btu/kWh LHV | 6,600 | Btu/kWh LHV |
| Fuel Use (@933 LHV Btu/scf), scfm | 243 | scfm | 283 | scfm |
| Water Use |  |  |  |  |
| Water Uptake | 300 | gal/h | 310 | gal/h |
| Water Discharge | 125 | gal/h | 130 | gal/h |
| Available Heat |  |  |  |  |
| Exhaust Temperature | 700-750 | deg F | 700-750 | deg F |
| Exhaust Flowrate | 5120 | Scfm | 5810 | scfm |
| Exhaust Absolute Humidity | ~20% | by volume | ~20% | by volume |
| Noise | 60 | dB(A) at 100 feet | 60 | dB(A) at 100 feet |
| Emissions |  |  |  |  |
| CO2 (from typical natural gas) | 1,760 | lbs/h | 2,055 | lbs/h |
| NOx | < 0.1 | ppmv | < 0.1 | ppmv |
| SOx | <0.01 | ppmv | <0.01 | ppmv |
| CO | <10 | ppmv | <10 | ppmv |
| VOC | <10 | ppmv | <10 | ppmv |
| Particulates | <5 | mg/m3 | <5 | mg/m3 |

The electrical system in the plant will take DC power from two Fuel Cell Stack Modules and deliver the plant’s rated AC power output to the grid while supplying all of the plant auxiliaries.  The reactive component (up to 3300 KVA) will be regulated by voltage or a specified VAr setting.   The electrical system will be designed to support plant operation at 50% of rated power output with one Fuel Cell Stack Module (or inverter, or transformer) out of service.  Operation in this mode will require that the defective Fuel Cell Stack Module (or the stack module associated with a defective inverter or transformer) be isolated from the fuel system.

The electrical system is designed so the plant can carry its own auxiliary load when isolated from the grid.  The electrical system configuration is designed to accommodate the optional additional electrical equipment necessary for providing UPS quality power.

Startup power for the plant will normally be obtained from the electric grid.  Black start capability can be provided by bringing a portable diesel generator to the site and connecting it to the 480 VAC Motor Control Center (MCC) to supply the plant’s auxiliary load.

A battery-supported uninterruptible power supply (UPS) will be provided to maintain power for the control system and other critical components during electric grid voltage dips or outages.

Additional electrical equipment that may be necessary at additional cost to the plant buyer include the main step-up transformer and high voltage switchgear. A place has been left for this equipment in the electrical equipment skid and in the plot plan layout.  For facilities with multiple units, it is also possible, if desired, to aggregate power at the 480V level and step up with a equipment outside the unit layout.

2.2 General Operability Characteristics

2.2.1 Plant Control:

The plant is designed for unattended operation with local and remote dispatching/control.  The system has a local control console which is limited to displaying operating mode (see below) and providing inputs for selecting desired power output level or mode transition.  Additional data and controls are provided through local computer hookup or remote computer monitor stations (with security restrictions in each case).

2.2.2  Operating Modes:

Out of Service:			Plant is at ambient temperature.

Heatup:				Plant is heating up to operating temperature

Hot Standby:			Plant is at operating temperature, but not on load

Cool Down:			Plant is slowly being cooled to ambient temperature

Power Output Dispatch Mode:	Plant is delivering power to a set point kW demand

Power Output Regulation Mode:	Plant is meeting changing load of isolated load island

Manual Mode:			Operated with manual override of all or portions of control system

Tripped and Isolated:		Plant is tripped, with slow nitrogen purge

Power Output Regulation Mode is not applicable to grid-connected units, and cannot be done at the normal plant efficiencies.  The baseline plant is not capable of black start from out of service, however this can be done by using a generator to power plant auxiliaries during heatup.

2.2.3 Operating Mode Transition Times and Ramp Rate:

Out of Service to Hot Standby :	70 hours or less for initial units

20 hours commercial unit target

Hot Standby to Rated Load:	10 minutes or less

2.3 Plant and Subsystem Life

The design life target for the overall plant is 30 years, assuming appropriate maintenance and component replacement.  The fuel cell stacks in the 4-stack modules have a replacement schedule of 25,000 hours for early production units, with a target of at least 40,000 hours for mature units (year 2004 or later).  “Hours” here refers to hours of operation at a stack temperature above 900 oF.  During operation of these stacks over their lifetimes, their performance gradually decreases.  This results in a drop of power output and efficiency of about 10% over the replacement schedule period.  Operation of the stacks beyond this time may be possible, but at restricted power output and efficiency.

The 2MW and 2.4MW market entry powerplants are designed so that advanced mature stacks (2004 timeframe) can be installed and used to their full capacity without a resize of the BOP components.  This means that the equipment in the process skid is sized to provide the flows (e.g. fuel and steam) needed to support operation of Mature stacks at 3000kW net AC.  The electrical skid is also capable of supporting power conversion to 3000kW net AC.

2.4 Operation and Maintenance Requirements

The powerplants will require periodic replacement of the following equipment and consumables:

- Fuel cell stacks, as discussed above (also see section 2.5.1).

- Water treatment skid chemicals and components (salt, activated carbon, softener resin, RO membranes, and filters).

- Fuel cleanup Sulfur sorbent

- Bottled nitrogen (used as a blanket and/or purging gas for the system during startup, shutdown, and emergency shutdown of the plant) and bottled carbon dioxide.   For startup from cold, a small amount of hydrogen may be needed, but it need not be stored on site routinely.

- Catalysts (higher hydrocarbon preconversion and peak shaving de-oxidizer (if included)).

- Miscellaneous materials for normal operation and maintenance (O&M) of the plant (including filters, lube oil, etc).

The estimated initial quantities and service life of major catalysts and chemicals for the powerplant are listed in Table 2.

Table 2

Catalysts and Chemicals Summary

| ITEM | INITIAL AMOUNT | SERVICE LIFE |
| --- | --- | --- |
| ### Fuel Preparation Sulfur Sorbent Preconverter Catalyst De-Oxidizer Catalyst (1) | 4000 lbs 7.5 ft3 1.5 ft3 | 6 mnths – 2 years(2) 3 years 5 years |
| ### Oxidant Supply Anode Exhaust Catalyst | 7.5 ft3 | 5 years |
| ### Water Treatment Salt | 80 gallon | 1 to 3 months |

Notes:

(1) Required for Peak Shave Gas Option Only

(2) At 100% capacity, dependent on type of odorant in natural gas

Labor requirements for O&M are expected to be limited to labor to replace these consumables, routine maintenance, and periodic checks of the plant.  The unit normally runs unattended.

2.5  Installation and Site Issues

The powerplant is designed to be installed in a wide variety of sites, with a range of conditions, however bounds have been placed on the site conditions to be used as a design basis.  The powerplants will be shipped to these sites and installed with a minimum of field work.  The following subsections discuss the modularization, transportation, and site issues.

2.5.1 Modularization and Transportation

The DFC Powerplant is highly modularized, consisting of two Fuel Cell Stack Modules and mechanical equipment and electrical equipment skids.  All components are designed for installation outdoor, and to be transportable by truck to the plant site.  Standard or customized trailers will be used for ground transportation.

The Fuel Cell Stack Modules and balance of plant (BOP) equipment skids will be preassembled and tested in the shop before shipment to the site.  Each cylindrical Fuel Cell Stack Module, containing four fuel cell stacks and internal distribution piping/ducting, will be assembled and conditioned in the factory. All mechanical and electrical equipment, piping, and valves will be shop installed on the equipment skids prior to delivery.  Interconnecting piping between skids has been minimized in the plant design.  All instrumentation and electrical components on the skids will be prewired, with all connections to other skids terminating at junction boxes.

The design of the Fuel Cell Stack Modules and equipment skids facilitates rapid installation and interconnection at the plant site, while providing access to critical plant components for inspection and maintenance work (such as Fuel Cell Stack Module replacement, catalyst / absorbent replacement, valve maintenance, air filter changeout, etc.)   The Fuel Cell Stack Modules and equipment skids are designed to be truck transportable.  The Fuel Cell Stack Module is about 13 feet in diameter, and weighs ~95,000 lbs.  The shipping weight of the other BOP skids is summarized in Table 3:

### Table 3, BOP Skid Shipping Weights

| DFC powerplant Weights | Estimated Shipping Weight, lbs |
| --- | --- |
| HRU Skid | 116,000 |
| Oxidant Supply Skid | 82,000 |
| Water Treatment/Instrument Air | 53,000 |
| Electrical Skid #1 | 72,000 |
| Electrical Skid #2 | 72,000 |
| Electrical / Control Center Skid | 16,000 |

Shipping of the Fuel Cell Stack Modules and equipment skids will be in accordance with Department of Transportation (DOT) regulations.  Special permitting may be required for transporting the Fuel Cell Stack Modules and equipment skids which weigh more than 50,000 lbs.  Also, special routing with escort and special permitting may be required for the Fuel Cell Stack Modules, particularly in metropolitan areas.  These additional requirements are not extreme, and do not pose a significant restriction on the areas which modules can be delivered to.

On arrival at the plant site, the Fuel Cell Stack Modules and equipment skids will be positioned onto their foundations and aligned using a crane or by jacking and rolling.  Installation of interconnecting piping and of interconnecting electrical and instrumentation wiring will be completed thereafter.  Approximately four weeks will be required after arrival of the stack modules/skids at the site to install the stack modules/skids and complete powerplant commissioning.

As noted above, the fuel cell stacks have to be replaced every three (market entry) to five (mature) years.  This will be done by delivering two new or reconditioned modules to the site and swapping out the old modules with a minimum of field work and down time.  The used modules will be returned for materials recycling or reconditioning.

The plant requires a rectangular plot area of less than 4500 square feet.  Maintenance access is provided within the plant's boundaries for vehicles required to service plant equipment.  An access zone capable of supporting the module transporter and the crane used to lift and replace the Fuel Cell Stack Modules is required at the front of the site.  The zone is 18 feet wide and runs the 83 foot length of the plant.  A laydown area of about 4500 square feet should be available adjacent to the plant during construction.  Additional construction costs may be incurred if the laydown area cannot be provided.

The design basis assumptions for site interfaces and site conditions are described in the next sections.

2.5.2 Site Conditions

Generic site and climatic design conditions for the plant are listed in Table 4.  This design range should allow the plant to be installed at most sites around the world.  The “design conditions” data refer to the range of conditions that the standard plant must operate under.  Conditions outside of this range will require plant modifications at extra cost.  The “performance point” data refer to the conditions at which the plant will provide its rated output and efficiency.

Additional general site conditions assumed in the baseline design are:

- The site is clear and level, free of hazardous materials, and graded to ensure drainage of surface water.

- The site soils are capable of a bearing pressure of 4000 pounds/square foot (PSF).

- All-weather road access at the front of the site is available.  The road will have sufficient load bearing capacity for the heaviest single equipment skid (120,000 lb), plus its transport and/or crane.

As evident from this discussion, the plant design has been done assuming an outdoor installation.  This does not preclude the installation of the powerplant inside a building, as long as the proper floor loadings and access allowances are provided.

TABLE 4

GENERIC SITE DESIGN CONDITIONS(1)

| CATEGORY | DESIGN CONDITIONS | PERFORMANCE POINT(2) |
| --- | --- | --- |
| Elevation above Sea Level | 0 to 2500 ft | 0 ft |
| Ambient Temperature | -20 to 104 F | 59 F |
| Relative Humidity | 0 to 100 % | 60 % |
| Wind Loading @ 33 ft | 24 PSF (3) |  |
| Snow Load | 30 PSF (4) |  |
| Precipitation | 2.5 inches/hour |  |
| Seismic | UBC Zone 2 |  |
| Ambient Dust Loading, Ave./yr | 27 micro-gram/m3 |  |
| Ambient Gaseous Halide Concentration, Ave./yr | 20 ppbw |  |
| Ambient Gaseous Sulfur Dioxide Concentration in Air | < 10 ppb |  |

Notes:

(1)	Highway access is required.  Rail siding is not required.

(2)   Basis for powerplant performance calculations.

(3)  This wind load of 30 PSF is based on a wind speed of less than 90 mph and Exposure C.  Exposure C is defined as “Open terrain with scattered obstructions having height generally less than 30 feet” (American Society of Civil Engineers standard ASCE 7-95).

(4)  This snow load is equivalent to a ground snow load of 40 PSF and a snow exposure factor of 0.7 per Uniform Building Code UBC-97.

2.5.3  Plant / Site Interfaces

The plant is designed for the following interconnections at the plant boundary limit:

- Pipeline natural gas supply

- Municipal quality potable water supply

- Firewater supply (depending on local regulations)

- Waste water discharge

- Flue Gas discharge to safe location (if indoors)

- Safety relief valve discharge to safe location (if indoors)

- Discharge of ventilation gases (if indoors)

The plant also includes connections within the plant boundaries to tie into a telephone line and / or data highway (e.g. to connect the controller and Fire Alarm Control Panel with the Plant Buyer's control center and / or dispatch facility, local fire department, FuelCell Energy, Inc., etc.).

A connection to an electric grid is also required.  Whenever the powerplant will not be generating power (such as during plant startup and shutdown), electric power for the plant auxiliaries will have to be backfed from the electric grid. Optionally, a small generator could be provided for this purpose.  The plant auxiliaries typically consume up to 60kW.

Two of the most important interfaces to the plant are the fuel and water supply.  The   design includes fuel cleanup and water treatment systems which have minimum requirements for the quality of the gas and water entering the plant.  These requirements are described in the next sections.

2.5.3.1  Fuel Quality Requirements

The main plant feedstock is pipeline natural gas.  The plant is designed to operate with natural gas that meets the "range/limits" criteria listed in Table 5.  A small addition to the standard plant provides the capability to generate power on peak shave gas (natural gas mixed with propane or butane and a small amount of air, with up 4% oxygen content), as defined in Table 6, by incorporating an optional reactor.

A natural gas with the "performance fuel" characteristics listed in Table 5 was used as the basis for estimating the plant's rated performance.  Use of natural gas with a different composition or heating value, or use of a peak shave gas (propane or butane), may impact plant performance.  Estimations of the type of impact can be made once a unique gas is specified.

The plant is designed to desulfurize pipeline natural gas containing one of the three natural gas odorant blends listed in Table 7.  Each of the blends shown represents one of the three classes of natural gas odorants typically added by natural gas pipeline and/or local distribution companies. Three standardized natural gas desulfurization systems are offered, each optimized for pipeline natural gases containing one of these odorant blends.  The pipeline gas odorant composition listed for the base plant design (all mercaptan odorant blend) in Table 7 is the basis used for the standard plant.  Depending on the type and level of the odorants, desulfurizing absorber beds will need to be replaced every one to two years.  Since the absorbent is run cold, it is possible to shut the plant down, replace the absorbent, and restart the plant before the stack and hot components have cooled significantly.

Table 5

Pipeline Natural Gas Requirements (Delivered To Site)

| PROPERTY | RANGE/LIMITS |  |  | PERFORMANCE FUEL |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Composition Methane, vol % Ethane, vol % Propane vol % Butanes, vol % Pentanes+, vol % Unsaturated Hydrocarbons Inert Gases - Nitrogen, vol % - Carbon Dioxide, vol % Oxygen, vol % | 80 - 100 0 - 10 0 - 3 0 – 1.25 0 - 0.5 None 0 - 5 0 - 3 0 - 3 0 - 0.2 | (2) | (1) 93.8 1.9 1.6 0.5 0.0 None 2.2 1.1 1.1 0.00 |  |
| Impurities Total Sulfur, ppmv grains/100 SCF - H2S, ppmv - COS, ppmv - Odorants, ppmv Halogens (Cl, etc) Dust/Gum/Solid Matter Water, lb/MMscf | 0 - 12 0 - 0.7 0 - 0.8 0 - 2 0 - 12 None None 0 - 7 | (3) | 6 0.36 0 0 6 None None Dry | (4) |
| Physical Properties Heating Value, Range - LHV, Btu/scf - HHV, Btu/scf Pressure, psig | 870 – 1000 970 – 1100 15 |  | (1) 933 1035 15 | (5) |

Notes for Table 5

(1)   The composition and heating value of the performance natural gas are the mean values from a survey of natural gas in 26 major metropolitan areas of the U.S. (from GRI report GRI-92/0123, March 1992).  Deviations from this specification will impact plant performance.

(2)   If the natural gas has a higher oxygen content, such as when propane-air peakshaving gas is present, the plant must be maintained in standby mode, unless the peak shaving option is installed, in which case the plant performance will be down-rated.

(3)   Nearly all pipeline natural gases will meet this specification, based on the sulfur impurity levels reported in GRI-92/0123.

(4)   Basis is the average total sulfur content in pipeline natural gas from a survey in GRI-92/0123.

(5)   Basis for the 2MW Powerplant performance estimate and the sulfur adsorption capacity of the sorbent in the natural gas desulfurization system.

Table 6

Peak Shave Gas Compositions (Delivered To Site)

| PROPERTY | PROPANE/AIR (1) |  |  | BUTANE/AIR (1) |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Composition Hydrogen, vol % Methane, vol % Ethane, vol % Propane vol % Butanes, vol % Pentanes+, vol % Oxygen, vol % Inert Gases - Nitrogen, vol % - Carbon Dioxide, vol % Unsaturated Hydrocarbons | 0.5 44.0 2.0 31.0 0.5 0.0 4.0 18.0 17.0 1.0 0.0 |  | 0.5 53.5 2.0 1.0 21.0 0.0 4.0 18.0 17.0 1.0 0.0 |  |
| ###### Impurities | Similar to Natural Gas Data |  | Similar to Natural Gas Data |  |
| Physical Properties Heating Value, Range - LHV, Btu/scf - Wobbe No. Pressure, psig | 1163.8 1183.2 15 |  | 1172.9 1187.9 15 |  |

Notes for Table 6

(1)   Gas compositions estimated from values provided for European peak shave gas compositions.  Compositions based on maximum oxygen and propane/butane concentrations, assumed to be worst case scenario for process design; other values fall within ranges for peak shave gas compositions, and chosen to provide comparable Wobbe Nos.

Table 7

Odorant Composition in Pipeline Natural Gas

| Fuel Treatment System Design Basis | Base Plant Design (1) | Option 1 (2) | Option 2 (2) |  |  |
| --- | --- | --- | --- | --- | --- |
| Natural Gas Odorant Blend | All Mercaptan Blend | Mercaptan/ Alkyl Sulfide Blend | Thiophane/ Mercaptan Blend | Thiophane (99.9%) |
| Organic Sulfur Components, mol % Mercaptans Alkyl Sulfides Thiophane Total | 100 -- -- 100 | 50 50 -- 100 | 50 -- 50 100 | -- -- 100 100 |

Notes for Table 7

(1)	Basis used for capital and O&M cost projections.

(2)	Requires upgraded fuel gas treatment system with higher capital and O&M costs.

2.5.3.2  Water Quality Requirements

The plant is designed to operate with municipal potable water makeup that meets the criteria listed in Table 8.  These criteria were used in estimating specifications for the water treatment system.  The performance water criteria listed in the table is the basis used for estimating the plant's water treatment requirement.  Water quality outside this range will typically require more frequent maintenance intervals or additional treatment equipment.

Table 8

Water Requirements (Delivered to Site)

| ITEM | RANGE / LIMITS | PERFORMANCE WATER (1) |
| --- | --- | --- |
| Quality Calcium (Ca), mg/l as CaCO3 Magnesium (Mg), mg/l as CaCO3 Sodium (Na), mg/l Bicarbonate (HCO3), mg/l as CaCO3 Chloride (Cl), mg/l Sulfate (SO4), mg/l Total Dissolved Solids, mg/l Total Hardness as CaCO3, mg/l Silica (SiO2), mg/l Iron (Fe), mg/l Copper (Cu), mg/l Silt Density Index Specific Conductance, micromho/cm pH Properties Temperature, F Pressure, psig | 0 - 120 0 - 30 N/A 0 - 90 0 - 50 0 - 90 0 - 350 0 - 150 0 - 10 0 - 0.1 0 - 0.05 0 - 5 0 - 580 7 - 8.5 40 - 90 50 - 65 | 44 16 16 50 17 20 135 60 3 0.03 0.01 2 205 7.6 59 60 |

Note:

(1)   Basis used for estimating the powerplant water treatment requirements