COBERRA 6562 DLE

## Gas Turbine Site Performance

#### CASE 1: 	5700 Ft. ASL

| Point Number | 1 | 2 | 3 | 4 | 5 |
| --- | --- | --- | --- | --- | --- |
| Ambient Temperature (°F) | 59 | 68 | 77 | 86 | 95 |
| Elevation (ft ASL) | 5700 | 5700 | 5700 | 5700 | 5700 |
| Relative Humidity (%) | 60 | 60 | 60 | 60 | 60 |
| Combustor | DLE | DLE | DLE | DLE | DLE |
| Fuel | Nat Gas | Nat Gas | Nat Gas | Nat Gas | Nat Gas |
| Lower Heating Value (Btu/lb) | 21114 | 21114 | 21114 | 21114 | 21114 |
| Inlet Loss (in H2O) | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 |
| Exhaust Loss (in H2O) | 4 | 4 | 4 | 4 | 4 |
| Shaft Power (HP) | 30271* | 28942 | 27635 | 26343 | 25073 |
| Heat Rate (BTU/HP.Hr) | 6904** | 6986 | 7077 | 7179 | 7294 |
| PT Speed (RPM) | 4800 | 4800 | 4800 | 4800 | 4800 |
| Fuel Flow (lb/Hr) | 9899 | 9575 | 9262 | 8957 | 8662 |
| PT Exit Flow (lb/s) | 162.5 | 157.8 | 153 | 148.3 | 143.4 |
| NOx (vppm) | 25 | 25 | 25 | 25 | 25 |
| NOx (tons/yr) | 102 | 99 | 96 | 93 | 90 |
| CO (vppm) | 5 | 5 | 5 | 5 | 5 |
| CO (tons/yr) | 12 | 12 | 12 | 11 | 11 |

Guarantee Tolerances:

### *Output Power (HP)		0%

**Fuel Rate (BTU/HP-Hr)		+3%

Guarantees are based on a clean and new engine.  All other data is expected, not guaranteed.

Note:

1)	Tons/yr based upon 8760 hours per year and 1 ton = 2000 lb.

COBERRA 6562 DLE

## Gas Turbine Site Performance

#### CASE 2: 	6000 Ft. ASL

|  | 1 | 2 | 3 | 4 | 5 |
| --- | --- | --- | --- | --- | --- |
| Ambient Temperature (°F) | 59 | 68 | 77 | 86 | 95 |
| Elevation (ft ASL) | 6000 | 6000 | 6000 | 6000 | 6000 |
| Relative Humidity (%) | 60 | 60 | 60 | 60 | 60 |
| Combustor | DLE | DLE | DLE | DLE | DLE |
| Fuel | Nat Gas | Nat Gas | Nat Gas | Nat Gas | Nat Gas |
| Lower Heating Value (Btu/lb) | 21114 | 21114 | 21114 | 21114 | 21114 |
| Inlet Loss (in H2O) | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 |
| Exhaust Loss (in H2O) | 4 | 4 | 4 | 4 | 4 |
| Shaft Power (HP) | 29930* | 28614 | 27326 | 26049 | 24811 |
| Heat Rate (BTU/HP.Hr) | 6905** | 6986 | 7077 | 7180 | 7293 |
| Fuel Flow (lb/Hr) | 9788 | 9467 | 9159 | 8858 | 8571 |
| PT Exit Flow (lb/s) | 160.7 | 156 | 151.3 | 146.6 | 141.9 |
| NOx (vppm) | 25 | 25 | 25 | 25 | 25 |
| NOx (tons/yr) | 100 | 98 | 95 | 92 | 89 |
| CO (vppm) | 5 | 5 | 5 | 5 | 5 |
| CO (tons/yr) | 12 | 12 | 12 | 11 | 11 |

Guarantee Tolerances:

### *Output Power (HP)		0%

**Fuel Rate (BTU/HP-Hr)		+3%

Guarantees are based on a clean and new engine.  All other data is expected, not guaranteed.

Note:

- Tons/yr based upon 8760 hours per year and 1 ton = 2000 lb.

COBERRA 6562 DLE

## Gas Turbine Site Performance

#### CASE 3 : 	6800 Ft. ASL

|  | 1 | 2 | 3 | 4 | 5 |
| --- | --- | --- | --- | --- | --- |
| Ambient Temperature (°F) | 59 | 68 | 77 | 86 | 95 |
| Elevation (ft ASL) | 6800 | 6800 | 6800 | 6800 | 6800 |
| Relative Humidity (%) | 60 | 60 | 60 | 60 | 60 |
| Combustor | DLE | DLE | DLE | DLE | DLE |
| Fuel | Nat Gas | Nat Gas | Nat Gas | Nat Gas | Nat Gas |
| Lower Heating Value (Btu/lb) | 21114 | 21114 | 21114 | 21114 | 21114 |
| Inlet Loss (in H2O) | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 |
| Exhaust Loss (in H2O) | 4 | 4 | 4 | 4 | 4 |
| Shaft Power (HP) | 29034* | 27775 | 26509 | 25286 | 24095 |
| Heat Rate (BTU/HP.Hr) | 6906** | 6986 | 7078 | 7180 | 7294 |
| Fuel Flow (lb/Hr) | 9496 | 9190 | 8886 | 8599 | 8324 |
| PT Exit Flow (lb/s) | 155.9 | 151.4 | 146.8 | 142.2 | 137.7 |
| NOx (vppm) | 25 | 25 | 25 | 25 | 25 |
| NOx (tons/yr) | 97 | 95 | 92 | 89 | 86 |
| CO (vppm) | 5 | 5 | 5 | 5 | 5 |
| CO (tons/yr) | 12 | 12 | 11 | 11 | 10 |

Guarantee Tolerances:

### *Output Power (HP)		0%

**Fuel Rate (BTU/HP-Hr)		+3%

Guarantees are based on a clean and new engine.  All other data is expected, not guaranteed.

Note:

1)	Tons/yr based upon 8760 hours per year and 1 ton = 2000 lb.

COBERRA 6562 DLE

## Gas Turbine Site Performance

#### CASE 4: 	7400 Ft. ASL

|  | 1 | 2 | 3 | 4 | 5 |
| --- | --- | --- | --- | --- | --- |
| Ambient Temperature (°F) | 59 | 68 | 77 | 86 | 95 |
| Elevation (ft ASL) | 7400 | 7400 | 7400 | 7400 | 7400 |
| Relative Humidity (%) | 60 | 60 | 60 | 60 | 60 |
| Combustor | DLE | DLE | DLE | DLE | DLE |
| Fuel | Nat Gas | Nat Gas | Nat Gas | Nat Gas | Nat Gas |
| Lower Heating Value (Btu/lb) | 21114 | 21114 | 21114 | 21114 | 21114 |
| Inlet Loss (in H2O) | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 |
| Exhaust Loss (in H2O) | 4 | 4 | 4 | 4 | 4 |
| Shaft Power (HP) | 28386* | 27155 | 25926 | 24720 | 23525 |
| Heat Rate (BTU/HP.Hr) | 6906** | 6985 | 7078 | 7181 | 7298 |
| PT Speed (RPM) | 4800 | 4800 | 4800 | 4800 | 4800 |
| PT Exit Flow (lb/s) | 152.4 | 147.9 | 143.5 | 139 | 134.4 |
| NOx (vppm) | 25 | 25 | 25 | 25 | 25 |
| NOx (tons/yr) | 95 | 92 | 90 | 87 | 84 |
| CO (vppm) | 5 | 5 | 5 | 5 | 5 |
| CO (tons/yr) | 12 | 11 | 11 | 11 | 10 |

Guarantee Tolerances:

### *Output Power (HP)		0%

**Fuel Rate (BTU/HP-Hr)		+3%

Guarantees are based on a clean and new engine.  All other data is expected, not guaranteed.

Note:

1)	Tons/yr based upon 8760 hours per year and 1 ton = 2000 lb.