SCOPE OF WORK

##### Affiliate shall provide the following materials:

Four (4) yagi antennas

One (1) yagi cellular antenna

Two (2) omnidirectional (omni) antennas

Four (4) 25' sections of LDF-4 grade foam coaxial cable with male-male N-connectors

One (1) 50' section of LDF-4 grade foam coaxial cable with male-male N-connectors

One (1) 250' section of LDF-5 grade foam coaxial cable with male-female N-connectors

Six (6) connector kits for foam cable

Seven (7) MDS-9810 radios

Two (2) Starcomm modems 3342E-003-2

Two (2) Rockwell UDS-2440 modems

Six (6) Fisher ROC 364 Remote Terminal Units (installed)

Two (2) PEX-5000 5 port multiplexers

One (1) Citel lightning surge protector

One (1) cellular modem

One (1) Xyplex

One (1) hub

One (1) router

##### At the Lysite Production office, 2700 Badwater Road, Lysite, WY, one omni antenna on the Burlington Resources tower located at the same site, using the 250' section of LDF-5 foam cable.  The antenna is to be connected, through the Citel lightning protector, to one of the MDS-9810 radios, set to master mode.  This MDS-9810 radio is also for Contractor to install configure and test.  Contractor shall also install, configure and test one of the PEX-5000 multiplexers. The PEX-5000 is to be configured with one of the Rockwell UDS-2440 modems (or the Starcomm should the Rockwell not be available) on a slave port.  The master port is to be reserved for connection to either a VSAT or a CDPD modem later.  The PEX-5000 will be used to route polling messages from Houston through the MDS-9810 master radio.

##### At the Madden West meter site, Contractor shall install, configure and test a yagi antenna and a slave MDS-9810 radio tied to the Lysite master radio.  Contractor shall be responsible for the installation of a mast on which to mount the antenna.  12V DC power is available for power to devices at the site.

##### At the Fred Novotny meter site, Contractor shall install, configure and test a yagi antenna and a slave MDS-9810 radio tied to the Lysite master radio.  Contractor shall be responsible for the installation of a mast on which to mount the antenna.  12 volt DC power is available for power to devices at the site.

##### At the Keith Baker meter site, Contractor shall install, configure and test a yagi antenna and a slave MDS-9810 radio tied to the Lysite master radio.  Contractor shall be responsible for the installation of a mast on which to mount the antenna.  12 volt DC power is available for power to devices at the site.

##### At the Sand Draw meter site, Contractor shall install, configure and test a yagi cellular antenna and a cellular modem.  Contractor shall be responsible for the installation of a mast on which to mount the antenna.  12 volt DC power is available for power to devices at the site.

##### At the Lost Creek Plant site, 55 East Carlton Road, Wamsutter, Wyoming, the installation shall be performed in stages.  For immediate service, Contractor shall connect a telephone line (to be provided at the analyzer building by Affiliate) to the Fisher modem already installed in the Fisher ROC RTU that monitors the plant inlet meters.  Longer term, Contractor shall install, configure and test a PEX-5000, an MDS-9810 master radio, an omni antenna, and a Rockwell modem (or one of the Starcomms, should the Rockwell not be available).  An RS-232 port will replace the Fisher modem at that point, and Contractor shall install an RS-232 cable from the RTU to the communications room in the control building at the plant site.  The final location for the omni antenna and the MDS-9810 master radio must be approved by Affiliate.  Preliminary research indicates that the radio and antenna should be installed on or near the light pole just east of the inlet meter analyzer building.  The MDS radio may be installed in the analyzer building.  The MDS-9810 master radio must be connected back to the PEX-5000.  Contractor shall purchase and install the necessary cabling and connectors to complete this installation.  Affiliate will provide a 56K line terminating in the communications room in the control building at the plant site.  Contractor shall install and test the hub, router, and Xyplex, which will be used to poll the end devices thorough the master port on the PEX-5000.  The Rockwell modem (or Starcomm equivalent) shall be installed, configured and tested, and shall poll the end devices through a slave port on the PEX-5000.  Finally, Contractor shall work with Affiliate to successfully poll data from the Rosemont Delta V plant control system through the PEX-5000 or by other means approved by Affiliate.

##### At the CIG/WIC meter site, Contractor shall install, configure and test a yagi antenna and a slave MDS-9810 radio tied to the Lost Creek Plant master radio.  Contractor shall be responsible for the installation of a mast on which to mount the antenna.  12 volt DC power is available for power to devices at the site.

##### Contractor shall work with Affiliate personnel to establish successful communications between each of the above sites and the SCADA server located in Houston, Texas.

##### One MDS-9810 radio is to be used as a spare in case of an electronic failure in any of the other MDS radios.