SPILL PREVENTION CONTROL AND

COUNTERMEASURE PLAN (SPCC)

FOR

Brownsville Power I, L.L.C.

948 Beechgrove Rd

Brownsville, TN 38012

Designated Person Accountable for Spill Prevention:

Mitchell Hurt

Plant Manager

CERTIFICATION

I hereby certify that I have examined the facility, and being familiar with the provisions

of 40 CFR part 112, attest that this SPCC Plan has been prepared in accordance

with good engineering practices.

Engineer:	Gus Eghneim, Ph. D.,  P.E.

Registration Number: 				Signature:

State: 						Date:

SPILL PREVENTION CONTROL AND COUNTERMEASURE

COMPLIANCE INSPECTION PLAN

# REVIEW PAGE

In accordance with 40 CFR 112.5(b), a review and evaluation of this SPCC Plan is conducted at least once every three years. The SPCC Plan should be amended within six months of the review to include more effective prevention and control technology if: (1) such technology will significantly reduce the likelihood of a spill event from the facility, and (2) if such technology has been field-proven at the time of review. Any amendment to the SPCC Plan shall be certified by a Professional Engineer within six months after a change in the facility design, construction, operation, or maintenance occurs which materially affects the facility’s potential for the discharge of oil into or upon the navigable waters of the United States or adjoining shorelines.

Review Dates		Amendment 		Signature

Date

October 15, 2000		Original

MANAGEMENT APPROVAL

Brownsville Power I is committed to the prevention of discharges of oil to navigable waters and the environment, and maintains the highest standards for spill prevention control and countermeasures through regular review, updating, and implementation of this Spill Prevention Control and Countermeasure Plan for the facility.

Mitchell Hurt

# Authorized Facility Representative		Signature

Plant Manager

Title

TABLE OF CONTENTS								Page

- Introduction

2.	Facility Owner and Operator

A. 	Facility Owner, Address, and Telephone

B. 	Facility Operator, Address, and Telephone

3. 	Facility Contact(S)

4. 	Facility Description

A. 	Facility Operations

B. 	Facility Storage

C. 	Drainage Pathway and Distance to Navigable Waters

5. 	Spill History

6. 	Potential Spill Predictions, Volumes, Rates, And Control

7. 	Prevention Measures Provided

A. 	Drainage Control

B. 	Bulk Storage Tanks/Secondary Containment

C. 	Facility Transfer Operations

D. 	Facility Tank Car and Truck Loading/Unloading Operations

E. 	Inspections/Record Keeping

F. 	Site Security

G. 	Personnel Training and Spill Prevention Procedures

H. 	Spill Control Equipment

- Emergency Contacts

APPENDICES

Appendix 1	Facility Layout And Surface Drainage Diagram

Appendix 2 	Secondary Containment Calculations for Diked Storage Areas

Appendix 3 	Facility Inspection Report and Checklist

Appendix 4 	Certification of the Applicability of the Substantial

Harm Criteria Checklist

Appendix 5 	SPCC Plan Training Records

Appendix 6	Drainage Discharge Report Form

Appendix 7 	SPCC Plan Checklist

- INTRODUCTION

EPA’s Oil Pollution Prevention regulations (40 CFR 112.1 through 112.7) establish requirements for facilities to prevent oil spills from reaching the navigable waters of the U.S. or adjoining shorelines.  The regulations apply to non-transportation-related facilities with a total aboveground (i.e., not completely buried) oil storage capacity of greater than 1,320 gallons (or greater than 660 gallons capacity in a single aboveground container), or total underground (i.e., buried) oil storage capacity greater than 42,000 gallons. The regulations apply specifically to a facility's storage capacity, regardless of whether the tank(s) is completely filled. In addition to the storage capacity criteria, facilities are regulated if due to their location the facility could reasonably be expected to discharge oil into navigable waters of the U.S. or adjoining shorelines.  The term navigable water is defined in the above regulations and for the most part covers all surface waters, including any waterway within the U. S.  Also included are normally dry arroyos, creeks or like through which water may flow and ultimately end up in public waters such as rivers, lakes, bays, streams and wetlands.

Applicability to the facility

EPA has made the determination that facilities that use equipment (i.e., transformers) which contain dielectric fluid (i.e., mineral oil), in quantities over the above thresholds, are subject to the Oil Pollution Prevention regulations.   As a result, the facility is required to prepare and implement an Spill Prevention Control and Countermeasure (SPCC) Plan.  The SPCC plan must describe all procedures, equipment and preventive measures adopted to prevent oil spills.  The SPCC Plan must:

- be kept on site;

- have the full understanding of all employees involved in the facility operation;

- be certified by a registered professional engineer.

- have full management approval;

- conform with all SPCC requirements in 40 CFR 112;

- discuss spill history;

- discuss spill predictions (i.e., direction of flow);

- be reviewed every three years by management;

- be amended and certified by a P. E. for modifications.

The following is a partial list of facility operations and associated equipment subject to the SPCC requirements:

- storage and transfer of lube oil for maintenance activities;

- storage of fuel oil or diesel for powering emergency or backup equipment; and

- storage of insulation (dielectric) oil in electrical equipment (e.g.,  transformers).

- FACILITY OWNER and OPERATOR:

A. 	Facility Owner, Address, and Telephone:

Enron Corporation

333 Clay Street

Houston, Texas 77002

(713) 345-5216

- Facility Operator, Address and Telephone:

Operational Energy Corporation

948 Beechgrove Rd

Brownsville, TN 38012

(901) 772-9003

- FACILITY CONTACT(s):

Name 			Title 			Telephone

Mitchell Hurt 		Plant Manager 	(901) 772-9003

Dean Frederick	Plant Supervisor 	(901) 772-9003

- FACILITY DESCRIPTION:

In this section describe the facility’s day-to-day operations, including hours of operation, personnel, and operational history. In your description include a discussion of the modes of transportation used for receiving products and raw materials (e.g., pipeline, railcar, tanker truck).

- Facility Operations:

The facility is a merchant power, electric generating plant that operates when electric power is needed to meet the peak demand of consumers.  It normally operates during the months of June through September of each year.   The typical hours of operation are from 8:00 am to 11:00 pm.   Personnel at the facility includes a plant manager, a plant supervisor,  five (5) plant operators, and an administrative assistant.  The facility began operation in May of  1999.

Normal operations during the peaking season include the preparation and start up of the turbines around 8:00 am and concluding with plant shut down around 11:00 pm.  While the facility is operating or in stand-by, operators make rounds, record equipment data, and perform preventative maintenance duties. Equipment maintenance performed includes, but is not limited to, repairing or replacing faulty equipment, calibrating instrument, controls & monitoring equipment. During the non-peaking season, the operations staff performs predictive, and preventative maintenance. They supervise contractors that are performing major maintenance such as turbine inspection/repairs and plant improvements.

The power plant is located on approximately 134 acres of land. A general site layout for the facility is shown in Appendix 1 (Facility Layout and Surface Drainage Diagram – need to include).  As shown, there are four (4) identical Westinghouse simple cycle, natural gas fired turbines at the facility (two Model 501D5 and two Model 501D5A).  Additionally, the facility has two oil-filled (22,570 gallons each) step up transformers located east of the turbines. There are also four (4) step-down transformers located east of the turbines. Two of these transformers hold 402 gallons of oil each, and the other two hold 1260 gallons each.  All transformers are located over containment basins.

Lubricating oil for the gas turbine generator is stored in a 2,500 gallons lube oil reservoir located just forward of the gas turbine compartment.  The total oil capacity for all turbines is 10,000 gallons.  The facility has a 3,500 gallons used oil tank.

The Facility has a water wash drain for each turbine that empties into a collection tank.  The capacity of the collection tank is 2000 gallons.  This wash water is periodically picked up by    **** and transported to ****  for disposal.

Any other tanks that store oil or petroleum products (i.e., diesel, lube oil, kerosene )  ????

Please describe here procedures for all OIL loading and unloading activities at the facility including frequency, duration of each loading/unloading event, where the loading/unloading occurs, and spill preventive measures taken.

- Facility Storage

In this section describe all types of oil product storage at your facility including oil products stored in aboveground storage tanks (ASTs), underground storage tanks (USTs), oil-filled electrical equipment (e.g., circuit breakers, transformers), spill tanks, oil/water separators, vapor recovery units portable tanks, drum storage, and trucks which hold oil product and are parked on site.

Tank ID 					Volume 				Contents

### Aboveground Storage Tanks

Three (3) Step Up Transformers		22,570 gallons	 (each)			 Mineral Oil

Two (2) Step Down Transformers	1,260 gallons	(each)			 Mineral Oil

Two (2) Step Down Transformers	402 gallons	(each)			 Mineral Oil

One (1) Wash water tank			2,000	 				Oil and Water

Four (4) Turbine Lube Oil Reservoirs	2,500 gallons (each)			Lube Oil

One (1) Used Lube Oil Tank		3,500 gallons (each)			Used Lube Oil

Other Equipment/Storage

Three (3) Lube Oil Drums	 ?		55 gallons				Lube Oil

Diesel tank  ?					---				Diesel Fuel

- Drainage Pathway and Distance to Navigable Waters

#### This section should describe the facility’s proximity to bays, rivers, streams (perennial or intermittent), creeks, ditches, flood control channels, storm drains, and other waterways.

#### Additionally, a facility layout and surface drainage diagram must be included in this section.  The diagram should include location of all OIL storage areas, direction of flow in case of a spill, and location of spill control equipment.

4.	SPILL HISTORY [112.7(a)]:

112.7(a) A facility which has experienced one or more spill events within twelve months prior to the effective date of this part should include a written description of each such spill, corrective action taken and plans for preventing recurrence.

If any, please complete the following Table for each spill.

The following spills have occurred at the facility through October 15, 2000.

| Description of Spill | Corrective Actions | Preventive Measures |
| --- | --- | --- |

Information on oil spills and/or leaks that occur after October 15, 2000 at the Facility will be added to this section.  This section will be reviewed annually and updated if necessary.

A.	Oil Spill Prevention

In addition to the preventive measures outlined in this SPCC plan, the facility has developed guidelines that establish specific requirements to ensure that reasonable measures are taken to prevent oil spills.   Some of these preventive measures or best management practices include:

- Annual training of personnel to ensure that all employees are familiar with the SPCC plan including preventive measures and response actions in the event of a spill.

- Unloading or loading of oil must be monitored for leaks, spills and proper hose connections or disconnections.

- Required repairs or replacement shall occur in a timely manner and shall be documented in the preventative maintenance program.

- Container storage buildings and secondary containment systems including the immediate area around such structures must be kept clean and free of trash, junk and debris.

- All storage containers must be kept securely closed except when adding or removing contents.

- Funnels must be removed from containers or covered when not in use.

- The valves for all dike and sump drains must always be closed except during drainage periods. Before releasing accumulated precipitation, inspect for any visible sheen or other signs of contamination. If any sheen is detected, it must be removed prior to discharge.

- Equipment leaks shall be repaired as soon as possible.

- Where appropriate, each loading or unloading installation shall have adequate containment equipment or systems.

- Containment systems shall have provisions to drain or otherwise remove rainwater.  Drainage valves shall remain closed at all times except when actively draining accumulated rainwater.

B.	Oil Spill Response Actions

The facility has developed an Emergency Action Plan that includes specific instructions to be followed in the event of an oil spill.

For each spill, at a minimum, the following information will be recorded:

- Location, Date, and Time of Spill;

- Type and Amount Spilled;

- Cause of Spill;

- Waterbody affected;

- Description of Physical Damage;

- Cost of Damage;

- Cost of Cleanup; and

- Corrective Action Taken and Plan to Prevent Recurrence.

5.	POTENTIAL SPILL PREDICTIONS, VOLUMES, RATES, AND CONTROL [112.7(b)]:

112.7(b) Where experience indicates a reasonable potential for equipment failure (such as tank overflow, rupture, or leakage), the plan should include a prediction of the direction, rate of flow, and total quantity of oil which could be discharged from the facility as a result of each major type of failure.

Types of failures to consider include tank (aboveground and underground) overflow, tank rupture or leakage, and spills during tank loading/unloading operations.  Please note that rate calculations assume worst case conditions.

| Source | Type of Failure | Volume | Rate (gallon/hr) | Direction of Flow | Containment |
| --- | --- | --- | --- | --- | --- |
| Aboveground Storage Tanks |  |  |  |  |  |
| Step Up Transformers | Rupture/ Leakage | 22,570 | 22,570 |  |  |
| Step Down Transformers | Rupture/ Leakage | 1,260 | 1,260 |  |  |
| Step Down Transformers | Rupture/ Leakage | 402 | 402 |  |  |
| Diesel Tank | Rupture/ Leakage | ---- | ---- |  |  |
| Wash water Tank | Rupture/ Leakage | 2000 | 2000 |  |  |
| Used Oil Tank | Rupture/ Leakage | 3,500 | 3,500 |  |  |
| Other Equipment/Storage |  |  |  |  |  |
| Lube Oil Drums | Drum Rupture | 55 | 55 |  |  |
| Lube Oil Reservoirs | Rupture/ Leakage | 2,500 | 2,500 |  |  |

6. 	PREVENTION MEASURES PROVIDED:

### Drainage Control Diversionary Structures and Containment [112.7(c)]

112.7(c) Appropriate containment and/or diversionary structures or equipment to prevent discharged oil from reaching a navigable water course should be provided. One of the following preventive systems or its equivalent should be used as a minimum:

(i) Dikes, berms or retaining walls sufficiently impervious to contain spilled oil;

(ii) Curbing;

(iii) Culverting, gutters or other drainage systems;

(iv) Weirs, booms or other barriers;

(v) Spill diversion ponds;

(vi) Retention ponds;

(vii) Sorbent materials.

At Brownsville Power I, all tanks that contain oil have secondary  containment, including dikes, berms, walls, curbing, and containment basins.

- Drainage Control [112.7(e)(1)(i-v)]:

- Drainage from diked storage areas:

112.7(e) (1) Facility drainage (onshore); (excluding production facilities). (i) Drainage from diked storage areas should be restrained by valves or other positive means to prevent a spill or other excessive leakage of oil into the drainage system or in plant effluent treatment system, except where plant systems are designed to handle such leakage. Diked areas may be emptied by pumps or ejectors; however, these should be manually activated and the condition of the accumulation should be examined before starting to be sure no oil will be discharged into the water.

After a careful examination and assurance that no oil is present in the water, the rainwater accumulated in all diked areas is drained using portable pumps.

(ii)  Valves used on diked area storage:

112.7(e) (1) Facility drainage (onshore); (excluding production facilities). (ii) Flapper-type drain valves should not be used to drain diked areas. Valves used for the drainage of diked areas should, as far as practical, be of manual, open-and-closed design. When plant drainage drains directly into water courses and not into wastewater treatment plants, retained storm water should be inspected as provided in paragraphs (e)(2)(iii) (B), (C) and (D) of this section before drainage.

There are no valves on the secondary containment structures at the facility. Storm water is removed using a portable pump.

(iii)	Plant drainage systems from undiked areas:

112.7(e) (1) Facility drainage (onshore); (excluding production facilities). (iii) Plant drainage systems from undiked areas should, if possible, flow into ponds, lagoons or catchment basins, designed to retain oil or return it to the facility. Catchment basins should not be located in areas subject to periodic flooding.

If any, this section should describe drainage in areas of the facility that do not have localized containment (e.g., area drains to a catch basin or retention pond).

Please complete this section ….

Example for Lincoln:    All plant storm drains are routed into a storm drain pond, located in the southwest corner of the facility. The storm drain pond has a twelve (12) inch drain pipe with a ten (10) inch restrictor pipe for one hundred-year storm. This drains to a “wet lands”.  Note: Water from off site drains into the facilities storm drain system.

(iv) Final discharge of drainage:

112.7(e) (1) Facility drainage (onshore); (excluding production facilities). (iv) If plant drainage  is not engineered as above, the final discharge of all in plant ditches should be equipped with  a diversion system that could, in the event of an uncontrolled spill, return the oil to the plant.

This section is not applicable to this facility because all tank areas at the facility have containment. All tanks, transformers and drums that contain oil have secondary containment to prevent oil spills from reaching the navigable waters of the U.S.

(v) 	Facility Drainage Systems and Equipment:

112.7(e) (1) Facility drainage (onshore); (excluding production facilities). (v) Where drainage waters are treated in more than one treatment unit, natural hydraulic flow should be used. If pump transfer is needed, two ‘‘lift’’  pumps  should be  provided, and at least one of the pumps should be permanently installed when such  treatment is continuous. In any event, whatever techniques are used facility drainage systems should be adequately engineered to prevent oil from reaching navigable waters in the event of equipment failure or human error at the facility.

There is no wastewater treatment at this facility; therefore, this section is not applicable

- Bulk Storage Tanks/Secondary Containment [112.7(e)(2)(i-xi)]:

- Tank compatibility with its contents:

112.7(e) (2) Bulk storage tanks (onshore); (excluding production facilities). (i) No tank should be used for the storage of oil unless its material and construction are compatible with the material stored and conditions of storage such as pressure and temperature, etc.

All tanks at the facility were constructed of welded steel in accordance with API standards 650 and 651, and are compatible with the contents that they hold.

- Diked area construction and containment volume for storage tanks:

112.7(e) (2) Bulk storage tanks (onshore); (excluding production facilities). (ii) All bulk storage tank installations should be constructed so that a secondary means of containment is provided for the entire contents of the largest single tank plus sufficient freeboard to allow for precipitation. Diked areas should be sufficiently impervious to contain spilled oil. Dikes, containment curbs, and pits are commonly employed for this purpose, but they may not always be appropriate. An alternative system could consist of a complete drainage trench enclosure arranged so that a spill could terminate and be safely confined in an in plant catchment basin or holding pond.

Precipitation freeboard should be based on regional rainfall patterns.

The oil storage tank areas have concrete slabs, surrounded by rebar steel reinforced, concrete walls for containment. The concrete containment area has been designed to be sufficiently impervious to hold the entire contents of the largest tank plus sufficient freeboard to allow for precipitation.

Appendix 2 provides secondary containment calculations for each tank area.

Note … for containment calculations, please provide the dimensions of the largest tank for each containment area.   For the freeboard calculation, we will use a 10 % factor.

- Diked area, inspection and drainage of rainwater:

112.7(e) (2) Bulk storage tanks (onshore); (excluding production facilities). (iii) Drainage of rainwater from the diked area into a storm drain or an effluent discharge that empties into an open water course, lake, or pond, and bypassing the in plant treatment system may be acceptable if:

(A) The bypass valve is normally sealed closed.

(B) Inspection of the run off rain water ensures compliance with applicable water quality standards and

will not cause a harmful discharge as defined in 40 CFR part 110.

(C) The bypass valve is opened and resealed following drainage under responsible supervision.

(D) Adequate records are kept of such events.

After a careful examination for oil has been conducted and documented by the plant operator, the rainwater accumulated in all diked areas is drained using portable pumps.  The plant operator notes the appearance of the water (checks water for pH and conductivity, prior to pumping), the time when water extraction is initiated and monitors the drainage closely.  After drainage is completed, the plant operator removes the pump and notes the time when water extraction concluded.  All information is recorded in drainage discharge report form shown in Appendix 6.  If an oil sheen or oil accumulation is observed, the oil-contaminated water will be transported to an appropriate waste-handling facility for disposal.   If not the case, please describe here the alternate method of drainage to be employed..

- Corrosion protection of buried metallic storage tanks:

112.7(e) (2) Bulk storage tanks (onshore); (excluding production facilities). (iv) Buried metallic storage tanks represent a potential for undetected spills. A new buried installation should be protected from corrosion by coatings, cathodic protection or other effective methods compatible with local soil conditions. Such buried tanks should at least be subjected to regular pressure testing.

Note: Underground storage tanks for purposes of SPCC must be completely buried, unlike “underground storage tanks” in EPA’s UST program, which may be partially buried.

There are no buried metallic oil storage tanks at the facility; therefore, the requirements of this section do not apply.

- Corrosion protection of partially buried metallic tanks:

112.7(e) (2) Bulk storage tanks (onshore); (excluding production facilities). (v) Partially buried metallic tanks for the storage of oil should be avoided, unless the buried section of the shell is adequately coated, since partial burial in damp earth can cause rapid corrosion of metallic surfaces, especially at the earth/air interface.

There are no partially buried metallic oil storage tanks at the facility; therefore, the requirements of this section do not apply.

(vi) Aboveground tank periodic integrity testing:

112.7(e) (2) Bulk storage tanks (onshore); (excluding production facilities). (vi) Aboveground tanks should be subject to periodic integrity testing, taking into account tank design (floating roof, etc.)  and using such techniques as hydrostatic testing, visual inspection or a system of nondestructive shell thickness testing. Comparison records should be kept where appropriate, and tank supports and foundations should be included in these inspections. In addition, the outside of the tank should frequently be observed by operating personnel for signs of deterioration, leaks which might cause  a spill, or accumulation of oil inside diked areas.

Tanks are constantly observed by facility personnel during operating hours. Formal inspections are conducted weekly to examine the exterior of the tanks and the containment areas. These inspections are documented using the report form that can be found in Appendix 3. In accordance with API 653, every ten years, or more often when necessary based on visual inspection or monitoring results, the ASTs are drained, cleaned, inspected, repaired, if necessary, and painted.

- Control of leakage through internal heating coils:

112.7(e) (2) Bulk storage tanks (onshore); (excluding production facilities). (vii) To control leakage through defective internal heating coils, the following factors should be considered and applied, as appropriate.

(A) The steam return or exhaust lines from internal heating coils which discharge into an open water course should be monitored for contamination, or passed through a settling tank, skimmer, or other separation or retention system.

(B) The feasibility of installing an external heating system should also be considered.

Not applicable.  Electric heating coils are used at the facility.

- Tank installation fail-safe engineered:

112.7(e) (2) Bulk storage tanks (onshore). (viii) New and old tank installations should, as far as practical, be fail-safe engineered or updated into a fail-safe engineered installation to avoid spills.  Consideration should be given to providing one or more of the following devices:

- High liquid level alarms with an audible or visual signal at a constantly manned operation or surveillance station; in smaller plants an audible air vent may suffice.

(B) Considering size and complexity of the facility, high liquid level pump cutoff devices set to stop flow at a predetermined tank content level.

(C) Direct audible or code signal communication between the tank gauger and the pumping station.

(D) A fast response system for determining the liquid level of each bulk storage tank such as digital       computers, telepulse, or direct vision gauges or their equivalent.

(E) Liquid level sensing devices should be regularly tested to insure proper operation.

Note: In order to provide adequate fail-safe engineering, redundancy should be employed. Inventory       control and “sticking” are not adequate methods unless a second form of overfill prevention is utilized.

All tanks at the facility are equipped with visual gauges that operate on a float system. Filling procedures allow tanks to be filled to a safe height which is designated to be 90% of the tank capacity. All tanks are equipped with high-level alarms. These alarms, which include high-level alarms at 90% and high-high level alarms at 95%, are inspected once every four weeks during the weekly facility inspection.  At that time, the float gauges are calibrated by manually taping the tanks.

- Observation of disposal facilities for effluent discharge:

112.7(e) (2) Bulk storage tanks (onshore); (excluding production facilities). (ix) Plant effluents which are discharged into navigable waters should have disposal facilities observed frequently enough to detect possible system upsets that could cause an oil spill event.

The facility does not discharge industrial wastewater directly into navigable waters.  The wash water generated at the facility is stored in a tank and then transported for proper disposal at  ..where ?

(x) Visible oil leak corrections from tank seams and gaskets:

112.7(e) (2) Bulk storage tanks (onshore); (excluding production facilities). (x) Visible oil leaks which result in a loss of oil from tank seams, gaskets, rivets and bolts sufficiently large to cause  the accumulation of oil in diked areas should be promptly corrected.

Visible oil leaks are reported to the maintenance department through a work order system, so that they can be fixed immediately. The maintenance department informs the plant operator when the repair has been completed or if additional time is needed to obtain parts and remedy the leak. Measures will be taken to minimize and mitigate the leak, while awaiting repair. Any spilled oil is cleaned up immediately by the operations personnel. Oil spill cleanup supplies are located  … where ?

(xi) Appropriate position of mobile or portable oil storage tanks:

112.7(e) (2) Bulk storage tanks (onshore); (excluding production facilities). (xi) Mobile or portable oil storage tanks (onshore) should be positioned or located so as to prevent spilled oil from reaching navigable waters. A secondary means of containment, such as dikes or catchment basins, should be furnished for the largest single compartment or tank. These facilities should be located where they will not be subject to periodic flooding or washout.

Please describe location and means of containment for all portable or mobile oil storage tanks/containers.   For example, if any,  for the lube oil drums and diesel tank … are they portable or mobile … any other tanks ?

- Inspections/Record Keeping [112.7(e)(8)]:

112.7(e) (8) Inspections and records. Inspections required by this part should be in accordance with written procedures developed for the facility by the owner or operator. These written procedures and a record of the inspections, signed by the appropriate supervisor or inspector, should be made part of the SPCC Plan and maintained for a period of three years.

Note: Written inspection procedures (e.g., checklist) should be included in the SPCC Plan. Documentation of the inspections can be maintained in a separate location other than the SPCC Plan as long as their location is referenced as a part of the SPCC Plan for three years. All other records pertaining to SPCC (e.g., drainage discharges, tank integrity testing, training records, etc.) must also be maintained for three years.

Facility inspections are conducted weekly and records of these inspections are documented and signed by the inspector or plant manager.  During the inspections, all tanks, containment structures, valves, and other equipment are inspected.  Results of  inspections are documented using the report form that can be found in Appendix 3.

All records of facility inspection, drainage discharges and personnel training are retained for at least three years.

- Site Security [112.7(e)(9)(i-v)]:

- Fencing:

112.7(e) (9) Security (i) All plants handling, processing, and storing oil should be fully fenced, and entrance gates should be locked and/or guarded when the plant is not in production or is unattended.

The entire facility is fenced and guarded 24 hours a day.

- Flow valves locked:

112.7(e) (9) Security (ii) The master flow and drain valves and any other valves that will permit direct outward flow of the tank’s content to the surface should be securely locked in the closed position when in nonoperating or nonstandby status.

All tank valves are securely locked in the closed position when in nonoperating or nonstandby status.

- Lighting adequate to detect spills:

112.7(e) (9) Security (v) Facility lighting should be commensurate with the type and location of the facility. Consideration should be given to:

- Discovery of spills occurring during hours of darkness, both by operating personnel, if present, and by nonoperating personnel (the general public, local police, etc.) and

(B) prevention of spills occurring through acts of vandalism.

Lighting at the facility is adequate to detect spills during nighttime hours and prevent vandalism.

- Personnel Training and Spill Prevention Procedures [112.7(e)(10)(i-iii)]:

- Personnel instructions:

112.7(e) (10) Personnel, training and spill prevention procedures. (i) Owners or operators  are responsible for properly instructing their personnel in the operation and maintenance of  equipment to prevent the discharges of oil and applicable pollution control laws, rules and regulations.

Describe spill prevention and operation’s training for new hires and refresher training for all Personnel.

All new hires are required to have a spill prevention training, which includes a complete review of facility’s SPCC Plan. Employees are also instructed and tested on the job.  Once a year, refresher training and deployment exercises for spill response are conducted.  Training records are found in Appendix 5. The plant manager or his designee will conduct the training.

(ii) Designated person accountable for spill prevention:

112.7(e) (10) Personnel, training and spill prevention procedures.(ii) Each applicable facility should have a designated person who is accountable for oil spill prevention and who reports to  line management.

Mr. Mitchell Hurt is the designated person accountable for spill prevention at the facility.

- Spill prevention briefings:

112.7(e) (10) Personnel, training and spill prevention procedures. (iii) Owners or operators should schedule and conduct spill prevention briefings for their operating personnel at intervals frequent enough to assure adequate understanding of the SPCC Plan for that facility. Such briefings should highlight and describe known spill events or failures, malfunctioning components, and recently developed precautionary measures.

Periodically, during weekly safety briefings, spill prevention is discussed.  Any near misses or incidents are discussed in these briefings in order to prevent them from recurring. Employee feedback and recommendations are encouraged in spill prevention and operation. Sign-in sheets, which include the topics of discussion at each meeting, are maintained for documentation.

- Spill Control Equipment:

List all spill control equipment stored at your facility (e.g., granular absorbent, empty drums, shovels, brooms, absorbent pads and  booms, vacuum truck)  for the purposes of  meeting  the requirements of 112.7(c).

Spill control equipment on site includes absorbent pads and booms, granular absorbent, empty drums, brooms, and shovels.  As noted in Appendix 1, oil spill clean up supplies and equipment is stored …where ?

- Emergency Contacts

Part 110-Discharge of Oil: 110.10 Notice. Any person in charge of a vessel or of an onshore  or Offshore facility  shall, as soon as he or  she has  knowledge of  any  discharge  of oil  from  such Vessel or facility in violation of §110.6, immediately notify the National Response Center (NRC) (800-424-8802). If direct reporting to the NRC is not practicable, reports may be made to the Coast Guard or EPA predesignated On-Scene Coordinator (OSC) for the geographic area where the discharge occurs. All such reports shall be promptly relayed to the  NRC. If it is not possible to notify the NRC or the predesignated OCS immediately, reports may  be made immediately to the nearest Coast Guard unit, provided that the person in charge of the vessel or Onshore  or offshore facility notifies the NRC as soon as possible. The reports shall be made in accordance with such procedures as the Secretary of Transportation may prescribe. The procedures for such  notice are  set forth in U.S. Coast Guard regulations, 33 CFR part 153, subpart B and in the NationalOil and Hazardous Substances Pollution Contingency Plan, 40 CFR part 300, subpart E. (Approved  by the Office of Management and Budget under the control number 2050-0046).

##### Facility Personnel

Dean Frederick, Plant Supervisor			Work:	(901) 772-9003

825 W Thomas St					Home:	(901) 772-2559

Brownsville, TN 38012				Cell:	(901) 780-7000

Mitchell Hurt, Plant Manager			Work:	(901) 772-9003

2711 Cedar Grove Cove				Home:	(901) 380-1028

Cordova, TN 38018				Cell:	(901) 780-9064

Greg Myers, Technician				Work:	(901) 772-9003

16 Rachel Drive Apt #1				Home:	(901) 660-3387

Jackson, TN 38305

##### Agencies

- State of Tennessee				Day Phone:	(901) 661-6200

Environmental Field Office

362 Carriage House Drive

Jackson TN, 38305

Water Pollution Division			Day Phone:	(901) 661-6201

Pat Patrick

2.	National Response Center (NRC)		24 Hour:	(800) 424-8802

- U. S.  EPA Region 4				Day Phone	(404) 562-9900

Atlanta Federal Center					(800) 241-1754
61 Forsyth Street, SW
Atlanta, GA 30303-3104

- Brownsville Fire Department			24 Hour:	911 or

19 Franklin Street West					(901) 772-1215

Brownsville, TN 38012

Chief:	Chris Lee				Business:	(901) 772-1369

5.	Haywood County Sheriff Department		24 Hour	911 or

1 Washington Ave North					(901) 772-1215

Brownsville, TN 38012

Sheriff:   Lemuel Marler			Business:	(901) 772-2412

6.	Haywood County Emergency 		24 Hour:	911 or

Management / Rescue					(901) 772-1215

111 Washington Ave. North

Brownsville, TN 38012

Acting Head:	Ed Ellington			Business	(901) 772-1227

Cleanup Contractors

- Advanced Response Corporation		24 Hour:	(877) 343-9272

Kenneth Knibbs				Business:	(901) 344-9272

Fax:		(901) 344-9238

- CB Specialty Services			24 Hour:	(877) 624-6555

Clayton Chaney				Business:	(901) 624-6555

Fax:		(901) 624-6556

- Four Seasons					24 Hour:	(800) 868-2718

Jim Whitehead				Business:	(901) 745-3800

Fax:		(901) 745-3876

##### Appendix 1

Facility Layout and Surface Drainage Diagram

Need to include Facility Layout and Surface Drainage Diagram

##### Appendix 2

##### Secondary Containment Calculations for Diked Storage Areas

Need to include containment calculations here

##### Appendix 3

##### Facility Inspection Report and Checklist

Facility Inspection Report and Checklist

| Date: __________________________________________ Time: _________________________________________ Inspector: ______________________________________ | # X=Satisfactory NA=Not Applicable O=Repair or Adjustment Required C=See comment under Remarks/Recommendations |
| --- | --- |

| # Drainage ____Any noticeable oil sheen on runoff. ____Containment area drainage valves are closed and locked. ____Oil/water separator systems working properly. ____Effluent from oil/water separator inspected. ____No visible oil sheen in containment area. ____No standing water in containment area. | ## ASTs _____ Tank surfaces checked for sings of leakage. _____ Tank condition good (no rusting, corrosion, pitting). _____ Bolts, rivets, or seams are not damaged. _____ Tank foundation intact. _____ Level gauges and alarms working properly. _____ Vents are not obstructed. _____ Valves , flanges, and gaskets are free from leaks. _____ Containment walls are intact. |
| --- | --- |
| ### Truck Loading/Unloading Area ____ No standing water in rack area. ____ Warning signs posted. ____ No leaks in hoses. ____ Drip pans not overflowing. ____ Catch basins free of contamination. ____ Containment curbing or trenches intact. ____ Connections are capped or blank-flanged. | ### Security ____ Fence and gates intact. ____ Gates have locks. ____ ASTs locked when not in use. ____ Starter controls for pumps locked when not in use. ____ Lighting is working properly. |
| ## Training ____ Spill prevention briefing held. ____ Training records are in order. |  |

REMARKS/RECOMMENDATIONS:

Appendix 4

##### Certification of the Applicability of the

###### Substantial Harm Criteria Checklist

Section 112.20(e) of the facility response plan regulation requires that all facilities regulated by the Oil Pollution Prevention Regulation (40 CFR part 112) conduct an initial screening to determine whether they are required to develop a facility response plan. The criteria in this checklist can be found in 40 CFR 112.20(f)(1). Facilities should include this form with their SPCC Plan.

###### Certification of the Applicability

of the Substantial Harm Criteria Checklist

FACILITY NAME: 		Brownsville Power I, L.L.C.

FACILITY ADDRESS: 	948 Beechgrove Rd., Brownsville, TN 38012

1. 	Does the facility transfer oil over water to or from vessels and does the facility have a total oil storage capacity greater than or equal to 42,000 gallons?

Yes  					No    	x

2. 	Does the facility have a total oil storage capacity greater than or equal to 1 million gallons and does the facility lack secondary containment that is sufficiently large to contain the capacity of the largest aboveground oil storage tank plus sufficient freeboard to allow for precipitation within any aboveground oil storage tank area?

Yes 					No  	x

3. 	Does the facility have a total oil storage capacity greater than or equal to 1 million gallons and is the facility located at a distance (as calculated using the formula in Attachment C-III, Appendix C, 40 CFR 112 or a comparable formula1) such that a discharge from the facility could cause injury to fish and wildlife and sensitive environments? For further description of fish and wildlife and sensitive environments, see Appendices I, II, and III to DOC/NOAA's "Guidance for Facility and Vessel Response Environments" (Section 10, Appendix E, 40 CFR 112 for availability) and the applicable Area Contingency Plan.

Yes 		 			No 	x

4. 	Does the facility have a total oil storage capacity greater than or equal to 1 million gallons and is the facility located at a distance (as calculated using the appropriate formula (Attachment C-III, Appendix C, 40 CFR 112 or a comparable formula 1 ) such that a discharge from the facility would shut down a public drinking water intake2  ?

Yes 		 			No 	x

Notes

1   If a comparable formula is used, documentation of the reliability and analytical soundness

of the comparable formula must be attached to this form.

2  For the purposes of 40 CFR part 112, public drinking water intakes are analogous to public

water systems as described at 40 CFR 143.2(c).

- Does the facility have a total oil storage capacity greater than or equal to 1 million gallons and has the  facility experienced a reportable oil spill in an amount greater than or equal to 10,000 gallons within the last 5 years?

Yes  				No  	x

CERTIFICATION

I, Mitchell Hurt, certify under penalty of law that I have personally examined and am familiar with the information submitted in this document, and that based on my inquiry of those individuals responsible for obtaining this information, I believe that the submitted information is true, accurate, and complete.

Mitchell Hurt

Name					Signature

Plant Manager	 			October 15, 2000

Title					Date

##### Appendix 5

SPCC Plan Training Record

SPCC Plan Training Record

| Date | Training Topic | Name | Signature |
| --- | --- | --- | --- |

## Appendix 6

##### Drainage Discharge Report Form

##### Drainage Discharge Report Form

## SPCC Plan Checklist

SPCC Plan Checklist

- Operator and Owner Addresses and Phone Nos.

II. 	Day-to-day Operations and Facility Background

III. 	Receiving Water/Probable Flow Paths (e.g., facility storm drain, street storm drain, WWTP outfall, overland to river or stream, flood control pond)

IV. 	Copy of SPCC Plan/Site Diagrams

____Certification of engineer: 112.3 (d).

____Reviewed within past three years: 112.5(b).

____Full approval of appropriate level management: 112.7.

____Spill history: 112.7(a)

____Spill predictions: 112.7(b)

____Diversionary structures and containment: 112.7(c)

V. SPCC Measures

112.7(e)(1) Facility drainage:

____i) Dike drainage via valves or manually controlled pumps.

____ii) No flapper-type drain valves on diked areas. Dike drain valves manual control.

____iii) Undiked area drains to catch basin.

____iv) If no drain prep as above. Diversion system to return oil.

____v) If drainage water not moved by gravity flow, then redundant lift pump setup.

112.7(e)(2) Bulk storage tanks:

____i) Material and construction compatible with contents.

____ii) Secondary containment for largest tank + precipitation, and

____ dikes sufficiently impervious to spilled oil.

____ or trench enclosure draining to catch basin.

____iii) Rainwater drainage (into a storm drain or water course) okay if:

____bypass valve normally sealed closed, and

____inspection and compliance with water quality standards, and

____valve opened under responsible supervision, and

____records kept of drainage events.

____iv) Buried tanks protected against corrosion/regular pressure testing.

____v) Partially buried tanks protected against corrosion.

____vi) Surface tanks integrity tested via hydrostatic, visual inspection, or nondestructive shell thickness methods. Construction of tanks base adequate.

____vii) Internal heating coils are closed loop or treated and monitored.

____viii) Fail-safe engineering on all tanks, new and old, via high liquid level alarms or high liquid level pump cutoff devices, or audible/code warning, and

____regular testing of liquid level sensors.

____ix) Water discharge facilities inspected regularly (NPDES).

____x) Visible leaks on tanks and piping corrected (Protocol).

____xi) Secondary containment for largest portable storage tank.

____ Portable tank area free from periodic flooding or washout.

112.7(e)(3) Facility transfer operations:

____i) Buried piping protected against corrosion.

____ii) Out-of-service pipes capped with origin marked.

____iii) Pipe supports minimize abrasion, corrosion, sagging.

____iv) Regular inspection of surface pipe and valves.

____ Regular pressure testing for pipes with no secondary containment.

____v) Signs to warn vehicles about piping.

112.7(e)(4) Facility loading/unloading rack:

____i) Follow DOT procedures for loading/unloading tank cars and tank trucks.

____ii) Secondary containment for largest vehicle compartment (or quick drainage system).

____iii) Prevention of early vehicle departure via warning signs, physical barriers, or interlocked warning light.

____iv) Vehicles examined for leakage at all outlets prior to departure.

112.7(e)(8) Inspections and records:

____ Written procedures records kept for three years of inspections and,

____ Records (inspections, discharges, training, briefings) kept for three years.

112.7(e)(9) Security:

____(i) Fully fenced.

____ Gates locked when plant unattended.

____(ii) Master flow and drain valves of tanks locked closed.

____(iii) Starter control locked “off” or located where only the authorized have access.

____(iv) Out-of-service pipelines capped or blank-flanged.

____(v) Lighting adequate for night spill detection and deterring vandals.

112.7(e)(10) Personnel, training and spill prevention procedures:

____(i) Personnel instructed in equipment operation and oil regulations.

____(ii) One person accountable for spill prevention.

____(iii) Owner/operator schedules regular briefings.

____ 112.20(e) Applicability of Substantial Harm Criteria Checklist Completed.