ISO 9001 CERTIFIED

TECHNICAL PROPOSAL INFORMATION

| Customer: | S & S Energy Products |  | Date: | 10/02/00 |
| --- | --- | --- | --- | --- |

| Proposal No: | - |  | Spec No: | - |  | Item No: | Q793001/A |
| --- | --- | --- | --- | --- | --- | --- | --- |

| RATING |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Type | Transformer | Class | H Winding |  | X Winding |  | Y Winding |  |
| Phase | 3 | - | 60 Wye | kV | 13.8 Delta | kV | - | kV |
| Hertz | 60 | OA | 36,000 | KVA | 36,000 | KVA | - | KVA |
| Temp Rise | 65 °C | FA | 48,000 | KVA | 48,000 | KVA | - | KVA |
| Insul Liquid | NON PCB OIL TYPE I | FA | 60,000 | KVA | 60,000 | KVA | - | KVA |
|  | - | - | - | KVA | - | KVA | - | KVA |

| ADDITIONAL TAP VOLTAGES |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| H Winding (Kv) | ± 2 of 2.5 % |  | NLTC |  |  |  |  |  |
| X Winding (Kv) | - |  |  |  |  |  |  |  |
| CONNECTIONS FOR OPERATION |  |  |  |  |  |  |  |  |
| Transformers in Bank |  | To Transformer From |  | Phase | Connected | To Transformer To | Phase | Connected |
| - |  | - |  | - | - | - | - | - |

| PERFORMANCE BASED ON A LOADING OF |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| H Winding |  | 60.0 |  | kV |  | 36.0 |  | MVA |  |
| X Winding |  | 13.8 |  | kV |  | 36.0 |  | MVA |  |
| Y Winding |  | - |  | kV |  | - |  | MVA |  |
| - |  | - |  | - |  | - |  | - |  |
| - |  | - |  | - |  | - |  | - |  |
| DIELECTRIC TESTS |  |  |  |  |  |  |  |  |  |
| Applied Voltage |  |  | H Winding |  |  |  | 34 | kV |  |
| (To other wind- |  |  | X Winding |  |  |  | 34 | kV |  |
| ing and ground) |  |  | Y Winding |  |  |  | - | kV |  |
| Induced |  |  | 7200 cycles |  |  |  | 120 | kV |  |
| Voltage |  |  |  |  |  |  | - | kV |  |
| INSULATION LEVELS |  |  |  |  |  |  |  |  |  |
|  | Basic Lightning |  |  |  | Low Frequency |  |  |  |  |
| ITEMS | Impulse Insula- |  |  |  | Voltage |  |  |  |  |
|  | tion Level |  |  |  | Insulation Level |  |  |  |  |
| H Line | 350 |  |  |  | 140 |  |  |  |  |
| H neutral | 110 |  |  |  | 34 |  |  |  |  |
| X line | 110 |  |  |  | 34 |  |  |  |  |
| X neutral | - |  |  |  | - |  |  |  |  |
| Y line | - |  |  |  | - |  |  |  |  |

| PERFORMANCE DATA, Based on |  | 85 |  | C Reference Temperature, |  |  | 36 | MVA Altitude: 1000 Mts. |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Losses and Exciting Current |  |  |  |  |  |  | Regulation |  |  |
| Excitation | % Ex |  | No Load Kw (20°C) |  | Total Loss Kw |  | Power Factor |  | % Regulation |
| 100% | 0.5 |  | 28 |  | 155 |  | 0.80 |  | 5.280 |
| 110% | 2.208 |  | 39 * |  | 166 * |  | 1.0 |  | 0.671 |
| - | - |  | * Not Guaranteed |  |  |  | - |  | - |

| AUXILIARY LOSSES |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Transformer KVA |  | Class |  | KWatts Aux Loss |  |
| 36,000 | - | OA |  | 0 |  |
| 48,000 | - | FA |  | 4 |  |
| 60,000 | - | FA |  | 5.5 |  |
| - | - | - |  | - |  |
| - | - | - |  | - |  |
| Average Sound Level |  |  | 74/76/77 |  | dB OA/FA/FA |

| PERCENT IMPEDANCE VOLTS |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Between | At | % IZ | Between | At |
| % IZ | Windings | kVA | Zero | Windings | kVA |
| 8 | H-X | 36,000 | 6.8 | H-X | 36,000 |
| - | - | - | - | - | - |
| - | - | - | - | - | - |

| EFFICIENCIES ( p.f = 1 ) AT 36 MVA |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Load | Full Load | 3/4 Load | 1/2 Load | 1/4 Load |  |  |  |
| % | 99.576 | 99.638 | 99.675 | 99.612 |  |  |  |

| MECHANICAL DATA |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Not for Construction Purposes |  |  |  |  |  |
| Outline Dwg No: |  | Q793A100 |  |  |  |
| Dimensions (Approximate) Ft. (Mts.) |  |  |  |  |  |
| Height |  | (A) | 17.8 (5.42) |  |  |
| Width |  | (B) | 22.3 (6.80) |  |  |
| Depth |  | (C) | 14.9 (4.55) |  |  |
| Height over Cover |  | (D) | 13.0 (3.95) |  |  |
| Untanking (Plus slings) |  | (E) | 23.3 (7.10) |  |  |
| Shipping Dimensions:Ft |  | W x D x H | 12.7 x 9.6 x 13 |  |  |
| Masses (Approximate) pounds (Kg) |  |  |  |  |  |
| Core and Coils |  |  | 59,190 (26,850) |  |  |
| Tank and Fittings |  |  | 32,410 (14,700) |  |  |
| Liquid | 4,910 | GL | 36,930 (16,750) |  |  |
| Total Mass |  |  | 128,530 (58,300) |  |  |
| Shipping without OIL |  |  | 79,480 (36,050) |  |  |
| Shipping with OIL |  |  | 109,240 (49,550) |  |  |