|  | 1999 Facilities |  |  |  |  | 2000 Facilities |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | BROWNSVILLE | caledonia | new albany |  |  | GleasoN | wheatland | wilton center |
| Region | SERC | SERC | SERC |  |  | SERC | ECAR | MAIN |
| Interconnected Area | TVA (500 kV) | TVA (500 kV) | TVA (500 kV) |  |  | TVA (500 kV) | IPL/CIN (345 kV) | CE (345 kV) |
| Control Area Name | ENSE | ENCA | ENNA |  |  | ENGL | ENWI/ENWC | ENLC |
| Turbine No./Type | 2 x W 501 D5, 2 x W 501 D5A | 6 x GE 7EA | 6 x GE 7B |  |  | 1 x W 501 FC, 2 x W 501 FD | 4 x W 501 D5A | 8 x GE 7EA |
| NOx Compliance Technology | 2 x Water Injected D5A, 2 x Steam Injected | DLN | DLN |  |  | Water Injected | Water Injected | DLN |
| NOx (Per Unit) | < 15 PPM (501 D5), < 25 PPM (501 D5A) | < 15 PPM | < 25 PPM |  |  | < 25 PPM | < 25 PPM | < 9 PPM |
| CO (Per Unit) | < 25 PPM | < 25 PPM | < 15 PPM |  |  | < 30 PPM | < 42 PPM | < 25 PPM |
| Start-Cost (2000 $/Start/Turbine) | 1,500 | 1,000 | 1,000 |  |  | 1,500 | 1,500 | 1,000 |
| Estimated Variable O&M (2000 $/MWh) | 1.50 | 1.00 | 1.00 |  |  | 1.50 | 3.00 | 2.00 |
| Estimated Fixed O&M (2000 $000) | 1,564 | 1,721 | 1,878 |  |  | 1,242 | 1,516 | 1,449 |
| Dispatch Blocks | 100 – 120 1 unit 200 – 240 2 units 320 – 360 3 units 430 – 460 4 units | 63- 75 1 unit 126 – 150 2 units 189 – 225 3 units 252 – 300 4 units 315 – 375 5 units 400 – 450 6 units | 50 – 60 1 unit 100 – 120 2 units 150 – 180 3 units 200 – 240 4 units 250 – 300 5 units 325 – 360 6 units |  |  | 150 – 175 1 unit 300 – 350 2 units 450 – 510 3 units | 100 – 120 1 unit 200 – 235 2 units 300 – 350 3 units 425 – 470 4 units | 63 – 77 1 unit 130 – 150 2 units 200 – 225 3 units 250 - 300 4 units 350 - 375 5 units 425 - 450 6 units 475 - 525 7 units 550 – 600 8 units |
| Normal Unit Ramp from cold to full load (Min) | 35 | 30 | 30 |  |  | 30 | 30 | 30 |
| Capacity @ 900 degrees(1) (MW) | 458 | 466 | 371 |  |  | 510 | 470 | 608 |
| Heat Rate @ 900 (HHV, Btu/kWh) | 11,406 | 12,064 | 12,500 |  |  | 10,592 | 11,734 | 11,973 |
| Gas Interconnect | ANR | Tennessee Gas | Columbia Gulf |  |  | ANR | Midwestern Gas | Northern Border |
| Permitted Hours | 1,365 | 1,685 | 1,086 |  |  | 915 | 902 | 3,250 |

- Includes additional capacity of 20 MW at Caledonia and 15 MW at New Albany, with installation of evaporative coolers by June 2000.