July 31, 2000

# Excess Emissions Report

## Four Stationary Gas Turbines

(Second-Half, 2000)

Brownsville Power 1, L.L.C.

Brownsville, Tennessee

ENRON/OEC

#### Excess Emissions Report

For Four Stationary Gas Turbines

(Second-Half, 2000

at

Brownsville Power 1, L.L.C.

### July 31, 2000

Submitted by;

______________________________

Mitchell D. Hurt

Plant Manager

#### Project Background

Name of Source Owner:					Brownsville Power 1, L.L.C.

Address of Owner:						333 Clay Street, Suite 1800

Houston, TX  77002-7361

##### Source Identification:						Peaking Power Plant

With four (4) gas turbines

Location of Source:						948 Beechgrove Road

Brownsville, TN  38012

Type of Operation:						Peaking Power Plant

Reporting Period:						Jan 1 through June 30, 2000

Owner’s Representative:					Mr. Gus Eghneim

Mr. Tom Callaghan

#### Table of Contents

Section 1.0	Introduction……………………………………………………5

Section 2.0	Source Description…………………………………………….6

Section 3.0	Continuous Emission Monitoring System Description……….7

Section 4.0	Facility Permit Conditions…………………………………….8

Section 5.0	Excess Emission and Exceedences……………………………9

Section 6.0	CGA/Linearity Results…………….………………………….10

Table 1.0	Heat Input Log………………………………………………...11

#### Section 1.0

#### Introduction

An Excess Emissions Report for four peaking gas turbines owned by Brownsville Power 1, L.L.C. (BPI) and located at Brownsville, Tennessee.  This report addresses continuous emission monitoring system (CEMS) data for the period of January 1, 2000 through June 30, 2000.  Parameters monitored by the CEMS include nitrogen oxides (NOx).  The purpose of the report is to satisfy 40 CFR Part 60.7 (c) and special conditions of the Air permit, as issued by the Tennessee Department of Environment and Conservation.  This requires a detailed excess emissions report, including facility and CEMS downtime and Linearity/Cylinder gas audit (CGA) results, to be submitted semi-annually to TDEC.

CEMS data for the period of January 1 through June 30, 2000 were reviewed and emission exceedances, based on permit conditions, were identified.  Facility and CEMS operating logs were reviewed and downtime periods identified.  All results and summary tables presented in Section 5.0 are in a format consistent with those specified in Title 40 of the Code of Federal Regulations-“Standards of Performance for New Stationary Sources,” Part 60 Subpart A-Section 60.7.

In general, emissions of monitored parameters were within limits for the majority of the reporting period. These exceedences were primarily attributed to the startup and shutdown of the four gas turbines, along with steam/water injection (process control) equipment problems.  Further details regarding these exceedences can be found in Section 5.1 of this report.

The Facility CEMS data availability was within the established 90 percent requirement during the reporting period.  Results of the CGA conducted on the Facility during the reporting period were within the criteria required for compliance determination and are presented in Section 5.2 of this report.

#### Section 2.0

#### Source Description

The Brownsville Power 1, L.L.C. Facility in Brownsville, Tennessee is a peaking power plant with four (4) gas turbine generators.  The plant operates at a gross output of 460 MW.

The facility consists of two (2) Westinghouse 501D5 and two (2) Westinghouse 501D5A gas turbine generators with Westinghouse Powerlogic II control systems.  Exhaust gas from the two (2) 501D5 turbines is directed to two (2) Once Through Steam Generators (OTSG).  The steam from each OTSG will be injected into the respective turbine for control of NOx emissions.  Each of the two (2) 501D5A turbines are equipped with a water injection system for control of NOx emissions and its own exhaust stack.  All units have an installed evaporative cooling inlet air system.

#### Section 3.0

#### Continuous Emission Monitoring System Description

To meet the requirements of the Environmental Protection Agency (EPA) and the Tennessee Air Pollution Control Board, BPI installed two (2) Continuous Emission Monitoring Systems from KVB-Enertec.

The CEMS are dry extractive systems with analyzers to measure NOx and O2.  The instruments included in the CEMS are API Model 252 NOx analyzers and Servomex 1440C O2 analyzers.  The two CEMS are located in individual shelters. Each CEM is a two-point timeshare system.  The two CEMS are controlled by individual GE 90-30 Programmable logic Controllers (PLCs).  The PLC transmits data to a KVB-Enertec Data Acquisition and Handling System (DAHS).

#### Section 4.0

#### Facility Permit Conditions

NOx emissions limits for each turbine specified by TDEC permit conditions are outlined below.

- The total annual heat input for this source shall not exceed 7,127,857 MMBTUs per calendar year based on the higher heating value (HHV) of the fuel combusted.

- NOx emission limit is 0.057 lb/MMBTU, HHV for the 501-D5 gas turbines

- NOx emission limit is 0.090 lb/MMBTU, HHV for the 501-D5A gas turbines

- May not exceed 249 Total Tons per Year of NOx

Further information regarding these emission limits and CEMS requirements can be found in the special conditions of the Facilities Air permit.

#### Section 5.0

#### Excess Emissions and Exceedances

#### Section 6.0

#### CGA/Linearity Test Results

#### Table 1.0

#### Heat Input Log

#### Monthly Log of Fuel Heat Content, Fuel Usage, and Total Heat Input

| Jan-00 |  |  |  |  |
| --- | --- | --- | --- | --- |
| Unit ID | Heat Content of Fuel (BTU/ft3) | Fuel Usage (ft3/month) | Heat Input (MMBTU/month) (as calculated on site) | Heat Input (MMBTU/month) (as calculated by ANR) |
| AA-001 | 1,072.00 | 58,499,627.11 | 62,711.60 |  |
| AA-002 | 1,072.00 | 69,532,680.56 | 74,539.03 |  |
| AA-003 | 1,072.00 | 93,771,669.88 | 100,523.23 |  |
| AA-004 | 1,072.00 | 89,357,567.61 | 95,791.31 |  |
| AA-005 | 1,072.00 |  | - |  |
|  | PLANT MONTHLY TOTALS | 311,161,545.16 | 333,565.18 | 325,396.00 |
| Feb-00 |  |  |  |  |
| Unit ID | Heat Content of Fuel (BTU/ft3) | Fuel Usage (ft3/month) | Heat Input (MMBTU/month) (as calculated on site) | Heat Input (MMBTU/month) (as calculated by ANR) |
| AA-001 | 1,018.00 | 0.00 | 0.00 |  |
| AA-002 | 1,018.00 | 12,109,386.19 | 12,327.36 |  |
| AA-003 | 1,018.00 | 36,326,840.22 | 36,980.72 |  |
| AA-004 | 1,018.00 | 24,129,082.37 | 24,563.41 |  |
| AA-005 | 1,018.00 |  | - |  |
|  | PLANT MONTHLY TOTALS | 72,565,308.78 | 73,871.48 | 68,885.00 |
| Mar-00 |  |  |  |  |
| Unit ID | Heat Content of Fuel (BTU/ft3) | Fuel Usage (ft3/month) | Heat Input (MMBTU/month) (as calculated on site) | Heat Input (MMBTU/month) (as calculated by ANR) |
| AA-001 | 1,018.00 | 0.00 | 0.00 |  |
| AA-002 | 1,018.00 | 0.00 | 0.00 |  |
| AA-003 | 1,018.00 | 0.00 | 0.00 |  |
| AA-004 | 1,018.00 | 0.00 | 0.00 |  |
| AA-005 | 1,018.00 | 2306.17 | 2.35 |  |
|  | PLANT MONTHLY TOTALS | 2306.17 | 2.35 | 0.00 |
| Apr-00 |  |  |  |  |
| Unit ID | Heat Content of Fuel (BTU/ft3) | Fuel Usage (ft3/month) | Heat Input (MMBTU/month) (as calculated on site) | Heat Input (MMBTU/month) (as calculated by ANR) |
| AA-001 | 1,016.00 | 2,588,311.56 | 2,629.72 |  |
| AA-002 | 1,016.00 | 6,133,994.76 | 6,232.14 |  |
| AA-003 | 1,016.00 | 9,938,529.61 | 10,097.55 |  |
| AA-004 | 1,016.00 | 4,092,048.17 | 4,157.52 |  |
| AA-005 | 1,016.00 | 7,292.23 | 7.41 |  |
|  | PLANT MONTHLY TOTALS | 22,760,176.33 | 23,124.34 | 23,587.00 |
| May-00 |  |  |  |  |
| Unit ID | Heat Content of Fuel (BTU/ft3) | Fuel Usage (ft3/month) | Heat Input (MMBTU/month) (as calculated on site) | Heat Input (MMBTU/month) (as calculated by ANR) |
| AA-001 | 1,017.00 | 107,208,339.07 | 109,030.88 |  |
| AA-002 | 1,017.00 | 120,472,155.21 | 122,520.18 |  |
| AA-003 | 1,017.00 | 107,929,342.38 | 109,764.14 |  |
| AA-004 | 1,017.00 | 128,516,221.56 | 130,701.00 |  |
| AA-005 | 1,017.00 | 73,229.28 | 74.47 |  |
|  | PLANT MONTHLY TOTALS | 464,199,287.50 | 472,090.68 | 480,158.00 |
| Jun-00 |  |  |  |  |
| Unit ID | Heat Content of Fuel (BTU/ft3) | Fuel Usage (ft3/month) | Heat Input (MMBTU/month) (as calculated on site) | Heat Input (MMBTU/month) (as calculated by ANR) |
| AA-001 | 1,018.00 | 34,191,160.31 | 34,806.60 |  |
| AA-002 | 1,018.00 | 57,856,112.70 | 58,897.52 |  |
| AA-003 | 1,018.00 | 62,062,165.87 | 63,179.28 |  |
| AA-004 | 1,018.00 | 82,128,181.74 | 83,606.49 |  |
| AA-005 | 1,018.00 | 56,905.36 | 57.93 |  |
|  | PLANT MONTHLY TOTALS | 236,294,525.98 | 240,547.83 | 238,513.00 |

| UNIT YTD TOTALS |  |  | Total Fuel Usage By UNIT YTD (ft3) | Total Heat Input by Unit YTD (MMBTU) (As calculated on Site) |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| AA-001 |  | 202,487,438.05 | 209,178.81 |  |
| AA-002 |  | 266,104,329.42 | 274,516.23 |  |
| AA-003 |  | 310,028,547.96 | 320,544.93 |  |
| AA-004 |  | 328,223,101.45 | 338,819.73 |  |
| AA-005 |  | 139,733.04 | 142.16 |  |
|  |  | Total Plant Fuel Usage | Total YTD Heat Input (MMBTU) | Total YTD Heat Input (MMBTU) |
|  |  | YTD | (As calculated on Site) | As Calculaated by ANR |
|  | PLANT YTD TOTALS | 1,106,983,149.92 | 1,141,299.63 | 1,136,539.00 |