# Technical Data Sheet	ENRON	April 6, 2000

# City of Austin Project	GSU (3W) Transformer	Tender No.: HU-Enron-2C

## RATING

| Type | CP | Temp. rise |  | Cooling | HV winding |  |  | 2LV windings |  | TV winding |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Phases | 3 | Wind & Oil |  | Class | 138 |  | kV | 13.8/13.8 | kV |  |  | kV |
| Frequency | 60 | 65 |  | OA | 64 |  | MVA | 32/32 | MVA |  |  | MVA |
| Connection |  | 65 |  | FOA | 85 |  | MVA | 42.5/42.5 | MVA |  |  | MVA |
| Standards | ANSI | 65 |  | FOA | 106 |  | MVA | 53/53 | MVA |  |  | MVA |
| Off circuit taps: |  |  | +/-2 X 2.5% of 138 KV |  |  |  |  |  |  |  |  |  |

## PERFORMANCE DATA

| Voltage | Impedance |  | Load Losses * |  | No Load |  |  | Sound L. | Auxiliary |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| kV | Base MVA | % | MVA | kW | % Volt. | kW | % Cur. | dB(A) | kW |
| 138 | 64 H/(X-Y) | 9.0 | 64 | 138.6 | 100 | 43.2 | 0.18 | 79/81/82 | 7.2 |
|  | X/Y | 18.0 |  |  |  |  |  |  | - |

* Based on 85°C winding temperature

## DIELECTRIC TESTS

| Applied to Ground |  |  | Over Voltage |  |  |  | Full Wave Impulse |  |  |  | Switching Impulse |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | kV |  |  |  | kV |  | H1, H2, H3 | 550/350 | kV |  |  |  | kV |
|  |  | kV |  |  |  | kV |  | X1, X2, X3 | 110 | kV |  |  |  | kV |
|  |  | kV |  |  |  |  |  | Y1,Y2,Y3 | 110 | kV |  |  | - | kV |

## DIMENSIONS (inches) AND WEIGHTS (lbs) **

| Outline drawing |  |  |  | Core & coils weight |  | 125700 |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Total height | 236 | Untanking height | 323 |  | Tank & fittings weight |  | 49100 |
| Total length | 275 | Transport height | 184 |  | Oil weight |  | 63900 |
| Total width | 225 | Transport length | 185 |  | Total weight |  | 238700 |
| Height over cover | 173 | Transport width | 125 |  | Transport |  | 161100 |

** Approximate, not for construction purpose

## ADDITIONAL DATA

### HV Bushings will have 650 KV BIL