# Technical Data Sheet	ENRON 	June 5, 2000

# Las Vegas-FC011400-2D-LS	GSU (2W) Transformer	 HU-Enron-2D-Lower Sound

## RATING

| Type | CP | Temp. rise |  | Cooling | HV winding |  |  | LV winding |  | TV winding |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Phases | 3 | Wind & Oil |  | Class | 138 |  | kV | 13.8 | kV |  |  | kV |
| Frequency | 60 | 65 |  | OA | 84 |  | MVA | 84 | MVA |  |  | MVA |
| Connection |  | 65 |  | FA | 112 |  | MVA | 112 | MVA |  |  | MVA |
| Standards | ANSI | 65 |  | FA | 140 |  | MVA | 140 | MVA |  |  | MVA |
| Off circuit taps: |  |  | +/-2 X 2.5% of 138 |  |  |  |  |  |  |  |  |  |

## PERFORMANCE DATA

| Voltage | Impedance |  | Load Losses * |  | No Load |  |  | Sound L. | Auxiliary |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| kV | Base MVA | % | MVA | kW | % Volt. | kW | % Cur. | dB(A) | kW |
| 138 | 84 H/X | 9.0 | 84 | 161.0 | 100 | 57.0 | 0.17 | 70/72/73 | 6.5 |

* Based on 85°C winding temperature

## DIELECTRIC TESTS

| Applied to Ground |  |  | Over Voltage |  |  |  | Full Wave Impulse |  |  |  | Switching Impulse |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | kV |  |  |  | kV |  | H1, H2, H3 | 650/350 | kV |  |  |  | kV |
|  |  | kV |  |  |  | kV |  | X1, X2, X3 | 110 | kV |  |  |  | kV |
|  |  | kV |  |  |  |  |  | Y1,Y2,Y3 | 110 | kV |  |  | - | kV |

## DIMENSIONS (inches) AND WEIGHTS (lbs) **

| Outline drawing |  |  |  | Core & coils weight |  | 158200 |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Total height | 243 | Untanking height | 338 |  | Tank & fittings weight |  | 66600 |
| Total length | 350 | Transport height | 190 |  | Oil weight |  | 90200 |
| Total width | 195 | Transport length | 200 |  | Total weight |  | 315000 |
| Height over cover | 179 | Transport width | 143 |  | Transport |  | 200000 |

** Approximate, not for construction purpose

## ADDITIONAL DATA

### HV Bushings will have 650 KV BIL