003.1 Electric Facility Data and Communications for
the Alberta Control area

# 1.	Purpose

To specify the data needed by the System Controller in fulfilling real-time operational responsibilities, and the communications requirements for the transmittal of real-time data to the System Coordination Center for both new and existing facilities.

# 2.	Background

The Alberta Control Area includes the Alberta Interconnected Electric System (AIES) and the the City of Medicine Hat Electric System (MHES).  The Power Pool of Alberta operates, through  the System Controller, a spot electric energy market and is the real-time operating authority for the AIES. In accordance with the Electric Utilities Act, Section 12, the System Controller acts to ensure the safe, reliable and economic operation of the AIES, including the operation of interconnections with neighboring systems, generation dispatch, and ancillary services.

To meet those responsibilities, the System Controller requires, among others, the following:

- A computer model representing the electric power  system of the Alberta Control Area

- Real-time visibility of selected Alberta Control Area electrical facilities and of selected data related to these facilities

# 3.	Definitions

The following definitions apply within this document. For general terms used within the Power Pool, refer to the Glossary (Section 004).

Availability

A measure of the percentage of time when the system can perform its critical functions.

Analog

The continuous reading of  quantities such as voltage, watts, vars, ampers and transformer tap positions.

Facility

Facilities, in the context of this standard, include:

- Power generating stations, that are operated synchronized to the grid, including the following  equipment:

- Generating units

- Power system stabilizers and automatic voltage controllers

- -	Unit breakers

- -	Unit transformers

- -	Ancillary service equipment

- -	Protection and telecommunication equipment

- Substation facilities that may include equipment like:

- Breakers and other isolation devices

- Protection equipment

- Static and/or dynamic VAR devices

- Telecommunications equipment

- Transformers

- Points of delivery where load-related ancillary service is offered.

- Transmission lines.

Energization

The process by which the equipment is brought up to operating voltage and frequency.

Data

The status and analog information telemetered to the System Coordination Center.

Interval

The time period needed to transfer real-time information from the facility to the System Coordination Centre.

Status

The information that indicates the  state of operation or condition of a facility or of a network element.

# 4.	References

- Power Pool of Alberta: Pool Rules, specifically Section 2.5.1, subsection f.

- Power Pool of Alberta: Participants Manual

- Province of Alberta Electric Utilities Act

- Pool Technical Standard 003.2 - Automated Dispatch and Messaging System for the AIES

- Pool Technical Standard 003.3 - Operational Voice Communications for the AIES

# 5.	Standards

## 5.1	Network model requirements

1.	The Alberta Control Area network model is comprised of static information and is maintained to include existing and new facilities that are within two weeks of energization.  This model is continuously updated with real-time data to help the Operations and Operations Planning staff of the System Controller in performing both real-time and off-line system studies (see Table 1).

## 5.2	New facility additions or modification to existing facilities

1.	During the project initial design stage, each Facility Owner will provide the System Controller - Operations Planning - with the corresponding preliminary single line diagrams.  These diagrams should include all pertinent high voltage equipment, isolation points, breakers, current and voltage transformers, locations of metering points, as well as the connections of the proposed generators, transmission lines, substations and major load devices to the existing installations.

2.	Within 10 business days of receipt of the single line diagrams, the System Controller will confirm the facility-specific information, data and compliance with the telecommunication requirements.

3.	As the project evolves, the Facility Owner must keep the System Controller - Operations Planning - staff informed of any changes. The Pool must receive the final design single line diagrams 30 days prior to the energization of the new facility.

4.	The Facility Owner must complete the full commissioning of each individual visibility point at least one week prior to the energization of the main electric power equipment installed in the facility.

## 5.3	System Controller’s real-time data requirements

1.	Real-time data requirements for monitoring aspects of  system security are categorized into two visibility levels. The visibility level associated with each facility depends on the individual facility parameters (see Table 2).

2.	AC interconnections to electrical systems located outside the Alberta Control Area require distinctive real-time data and telecommunication specifications that depend on the configuration of the interconnection.  These specifications will be established on a case by case basis.

3.	Status information is to be reported by exception (see Table 4 Note 2).  Analog scaling will not exceed the greater of 200% of the rating of the device used for measuring the parameter or the largest expected range of values.  Real-time data must reflect the actual status, conditions and flows or levels within 2% of the actual values and resolution within 0.5% (see Table 3 and 8).

## 5.4	Data update rates and integrity scans

Refer to Table 4.

## 5.5	Supplemental requirements for ancillary service providers

Ancillary Service Providers must meet all applicable requirements specified elsewhere in this standard as well as the supplementary requirements listed in Table 5.

## 5.6	Communication protocol and physical medium combinations for real time data communication

The Facility Owners have to provide the necessary hardware and software, and make the necessary arrangements so that their facilities could transmit to the System Coordination Centre data and status information, as requested in this standard, using one of the methods (i.e. combination of protocol and medium) specified in Table 6.

## 5.7	Telemetry data availability specification

The Pool will track and collect statistics on telemetry data availability/unavailability.  The acceptable limits are specified in Table 7.

## 5.8	Notification of planned outages for real time data communication equipment

The Facility Owner will submit in advance, to the System Controller – Operations Planning, the next week schedule of planned outages for equipment that collects and/or transmits the real time data.

## 5.9	Communication contingency plans

During the loss of real time data, the Facility Owner is responsible for  informing the System Controller, by other means of communication, of any change in status or data that under normal conditions would be transmitted  to the System Coordination Centre.

# 6.	Revisions and Approval

| Issued | Description |
| --- | --- |
|  | Supercedes 2001-07-06 |
| 2001-07-06 | New issue |

### Table 1

Information required by the System Controller to maintain the network model of the Alberta Control Area

Facility Overall Configuration: Single line diagram showing all pertinent high voltage equipment, isolation points, breakers, current and voltage transformers, revenue metering points, and connections of proposed generators or loads

Bus Data: Typical operating voltage range (bus emergency and sustainable maximum / normal / minimum)

Bus Shunt Reactor or Capacitor: (where applicable) Nominal rating (MVAR @ nominal voltage) Bus used as voltage monitoring point

Transformer Data: (where applicable) Transformer name plate data including the following: Transformer nominal voltage, resistance and reactance values (for all windings) Transformer tap positions(voltage ratios and corresponding tap positions) Configuration of transformer windings (star, delta, etc.) Rated capabilities (for each set of transformer windings)

Transmission Line Data: (where applicable) Line resistance and reactance values (R, X, B) Rated voltage Line MVA capacity rating (summer / winter / emergency) Line length (km)

Load Point Information: Identification of breakers for loads providing under frequency load shedding, ancillary services or demand bids.

Remedial Action Schemes or Thermal Protection Schemes: (where applicable) Description, triggers, actions and (where appropriate) amount of load effected

Protection and Communication Configurations: High level description of equipment protection (primary and secondary telecommunication aided protection) Communication method and paths used for protection and SCADA ( primary and backup, if applicable)

Generating Unit Information: (where applicable) Unit primary energy source (nuclear, bio-mass, coal, gas, oil, wind, solar, hydro) Unit capability: Maximum/minimum capability ratings (MCR) and curves (in MVA/MW/MVAR) for normal conditions Emergency capability rating (ECR)

Additional requirements for generators greater than 50 MW (gross): Normal unit ramp rates – up, down (MW/minute) Maximum unit ramp rates – up, down (MW/minute) Specify if the unit has any rough zones (upper and lower MW/MVAR limit of each)

### Table 2

Required visibility levels corresponding to individual facility parameters

| Facility Parameters* (Parameters determine the Required Visibility Level) | Required Visibility Level |  | Visibility Not Required |
| --- | --- | --- | --- |
|  | Standard | Basic |  |
| Facility generation capability levels |  |  |  |
| The facility contains generation totaling less than 5 MW (sum of MCRs) |  |  |  |
| The facility contains generation totaling 5 MW or greater, but less than 50 MW (sum of MCRs) |  |  |  |
| The facility contains generation totaling 50 MW or greater (sum of MCRs) |  |  |  |
| Generator provides ancillary services (see above and Table 5) |  |  |  |
| Facility voltage controls or voltage levels |  |  |  |
| Contains switchable VAR device (capacitor or reactor bank,) |  |  |  |
| On line tap changer (OLTC) mounted on transformer connected to busses operating above 30 kV |  |  |  |
| Facility contains buses which are operated at two or more nominal voltage classes (25 kV and higher) |  |  |  |
| Facility contains an SVC or synchronous condenser |  |  |  |
| Facility operates at, or contains a bus with nominal voltage greater than 200 kV |  |  |  |
| Facility capability/configuration |  |  |  |
| Facility connects 3 or more transmission lines |  |  |  |
| Facility supplies local (site) loads, with simultaneous total peak values of 5 MW or greater, that are offered for ancillary service or are included in RAS schemes |  |  |  |
| Facility supplies local (site) loads with simultaneous total peak values of 50 MW or greater |  |  |  |

*	The additions to existing facilities, which already provide visibility, will also have to provide visibility

### Table 3

Real time data requirements based on the facility visibility level

| Data Requirements (Visibility Level determines data requirements) | Facility Visibility Level |  |
| --- | --- | --- |
|  | Standard | Basic |
| Bus |  |  |
| Bus voltage |  |  |
| Breaker and isolation devices status |  |  |
| Visibility of any load shed (RAS) breaker status |  |  |
| Bus- or line-connected capacitors/reactors (where applicable) |  |  |
| Control device (status point) |  |  |
| Capacitor/Reactor MVAR analog |  |  |
| Transformers (where applicable) |  |  |
| Regulator auto/manual status (see note 1) |  |  |
| Tap position (see note 1) |  |  |
| Line |  |  |
| Power flows (MW/MVAR) |  |  |
| Generator (for each unit, where applicable, see Note 2) |  |  |
| Unit gross generation (MW/MVAR) analogs (see Figure 1 and Note 2) |  |  |
| Unit service load (MW/MVAR) analogs (optional) – see Figure 1 and Note 2 |  |  |
| Unit net generation (MW/MVAR) analogs – see Figure 1 and Note 2 |  |  |
| Unit transformer OLTC auto/manual status - see Note 1 |  |  |
| Generator breaker status - see Note 2 |  |  |
| Generator power system stabilizer status - enabled or disabled (where equipped) |  |  |
| Generator excitation control / voltage regulation – automatic or manual - status |  |  |
| Power Station (generating plant) and Site Information |  |  |
| Station (plant) service load (MW/MVAR) analogs – see Figure 1 and Note 3 |  |  |
| Total Site Load (MW/MVAR) analogs – plant and generator service not included – see Figure 1 and Note 3 |  |  |
| Net to Grid (MW / MVAR) analogs – see Figure 1 |  |  |
| Bus (plant) frequency |  |  |
| Remedial action scheme (where applicable) |  |  |
| Arming status and actual load on line (MW) |  |  |
| Remedial action scheme-operated alarm |  |  |
| Communications and RTU: |  |  |
| Communication failure alarm |  |  |
| RTU failure alarm |  |  |

Notes:

- OLTC tap position information and regulator control is required only for transformers which have two windings operating  at a voltage higher than 60 kV, generating unit transformers larger than 5 MVA, and transformers that connect capacitor banks and reactors.

- If the individual generator maximum rated capacity (MCR) is less than 5 MW and the total plant generation capacity is equal to, or greater than 5 MW, the plant generation data can be telemetered instead of the unit generation data.

- Unit  generation should be provided in “gross” and “net” values. A net (MW/MVAR) value has be metered at the high voltage side of the unit step-up transformer.

If net generation (measured at the generator terminals, or equivalent) metering is provided, telemetering of unit service (ancillary) loads is optional.  Telemetering of net generation values is preferred instead of telemetering separately gross generation and unit service load values.

- Station service should be telemetered separately, as well as the calculated net values for individual generators.  Industrial sites and CMH should also telemeter the total site load (excluding plant and generator ancillary services).

### Table 4

Data update rates and integrity scans based on visibility level

| Data Update Rates | Standard Visibility Level | Basic Visibility Level |
| --- | --- | --- |
| Analog |  |  |
| 2 second poll interval | (see notes 1and 4) |  |
| 10 second poll interval |  |  |
| 60 second poll interval |  | (see note 3) |
| 10 second exception reporting for ancillary services provision |  |  |
| Status (see note 2) |  |  |
| Report by exception – poll once every 2 seconds | (see note 1) |  |
| Report by exception – poll once every 10 seconds |  |  |
| Report by exception - poll once every 60 seconds |  |  |
| Integrity Scan – initiated from master | (once per hour) | (once per day) |

Notes:

1.	For generators with a Maximum Continuous Rating (MCR) equal to or larger than 300 MW, the following data has to be reported at 2 sec intervals: MW, MVAR, frequency, and status of devices that disconnect the generator or the interconnection to the grid.  Status is to be reported by exception – see Note 2.

2.	The term “report by exception (also known as unsolicited report)” is used for instances when data is sent only when its value changes.  Data that is sent using reports by exception must be polled at time intervalsdefined in above Table 4.

- Report by exception may be used instead of 60 second interval poll when appropriate analog dead band exists.

- For generators providing Regulating Reserve

### Table 5

Supplementary  requirements for Facility Owners offering ancillary services

| Ancillary Service Offered | Supplementary Requirements for Telemetered Information* |
| --- | --- |
| Spinning Reserve | No additional requirements. |
| Supplemental Generation Reserves | No additional requirements. |
| Supplemental Load Reserves | Site load (MW) contracted for ancillary service and totaling 5 MW or greater - analog |
| Regulating Reserves | High and low regulation limits - analogs Frequency source - analog Automatic generation control data - mode of automatic generation control for the unit (set point or pulse) Additional specific information may be required based on unit controller and unit tuning testing. |
| Voltage Support | Telemetered MVAR data for facilities where dynamic voltage support is offered (i.e. SVC, synchronous condenser) |
| Power System Stabilizers | No additional requirements |
| Automatic Voltage Regulator | No additional requirements |
| Fast-acting Remedial Action Schemes (RAS) for loads | Total load available (MW) Total load contracted for RAS and armed (MW) |
| Black Start Service | Frequency at generation facility updated every 2 seconds |
| Transmission Must Run Service | No additional requirements |
| Remedial Action Schemes for Generators | Status of remedial action scheme (armed / disarmed)* Status – trip-initiated alarm * |

* for update rates see provisions

### Table 6

Communication protocol and physical medium combinations based on the required level of real time visibility

| Visibility Level | ICCP | DNP 3.0 | Medium |
| --- | --- | --- | --- |
| Standard |  |  | ATM |
|  |  |  | ISDN |
|  |  |  | Frame relay |
|  |  |  | Dedicated copper |
| Basic |  |  | Dedicated copper |
|  |  |  | Digital cellular packet data |
|  |  |  | Dedicated Internet Connection |

### Table 7

Visibility level – based availability requirements for the communication path

| Visibility Level | Availability (%) | Upper Limit of Acceptable Values |  |
| --- | --- | --- | --- |
|  |  | Unavailability (hrs off/year) | Expected Mean Time to Repair |
| Standard | 99.8 | 17.5 | 4 hours |
| Basic - without Ancillary Services - with Ancillary Services | 98.0 99.8 | 175.2 17.5 | 2 days 4 hours |

### Table 8

Allowable Dead-bands for Analog Report by Exception Using Basic Visibility*

| Value | Allowable Dead-band |
| --- | --- |
| MW: -without Ancillary Services - with Ancillary Services | 1 MW Deadband is no greater than the maximum allowable resolution of 0.5% |
| MVAR | 1 MVAR |
| kV | 0.5% of nominal voltage |
| OLTC tap | 0 (no deadband allowed) |

### Figure 1

“i” Unit Gross Generation  =  Gi				“i” Unit Service Load=  USi

Site Load = SL								Station Service	          =  SS

“i” Unit Net Generation “i”= GI – USi - Unit Transformer Losses

“i” Unit Calculated Net Generation =  CNGi   = NGi – SS x Gii=1nGi

Plant Net to Grid = NTG = i=1nCNGi- SL