AGREEMENT

By and Between

E-NEXT GENERATION LLC,

Acting Through Its Agent

ENRON NORTH AMERICA CORP.

and

GE PACKAGED POWER, INC.

For The Purchase Of

FOUR LM6000 ENHANCED SPRINT GAS TURBINE GENERATOR SETS

TABLE OF CONTENTS

ARTICLE I. DEFINITIONS	1

1.1	Acceptance	1

1.2	Adjusted Electrical Output	1

1.3	Adjusted Emissions	2

1.4	Adjusted Exhaust Gas Energy	2

1.5	Adjusted Exhaust Gas Temperature	2

1.6	Adjusted Heat Rate	2

1.7	Affected Party	2

1.8	Affiliate	2

1.9	Agreement	2

1.10	Applicable Laws	2

1.11	Base Load	2

1.12	Basis Conditions	2

1.13	BTU	2

1.14	Cancellation Charge	2

1.15	Change in Law	2

1.16	Change Order	3

1.17	Claim	3

1.18	Commercial Operation	3

1.19	Commissioning Period	3

1.20	Cover Damages	3

1.21	Day	3

1.22	Delivery Liquidated Damages	3

1.23	Delivery Point	3

1.24	Effective Date	3

1.25	Emissions	3

1.26	Emissions Guarantee	3

1.27	Electrical Output	3

1.28	Electrical Output Guarantee	3

1.29	Equipment	3

1.30	Event of Force Majeure	3

1.31	Event of Purchaser Default	3

1.32	Event of Seller Default	3

1.33	Exhaust Gas Energy	3

1.34	Exhaust Gas Temperature	4

1.35	Extended Warranty Period	4

1.36	Facility	4

1.37	Far Field Sound Level Guarantee	4

1.38	Guaranteed Levels	4

1.39	Guaranteed Unit Delivery Dates	4

1.40	Hazardous Materials	4

1.41	Heat Rate	4

1.42	Heat Rate Guarantee	4

1.43	Heat Rate Liquidated Damages	4

1.44	Heat Rate Liquidated Damages Refund Reduction	4

1.45	Installation Period	4

1.46	Insurability Certificate	4

1.47	Insurance Representative	4

1.48	Interest Rate	4

1.49	kW	4

1.50	kWh or kwh	5

1.51	Lender	5

1.52	Liquidated Damages	5

1.53	Liquidated Damages Events	5

1.54	Major Components	5

1.55	Marketing Agreement	5

1.56	Maximum Liability Amount	5

1.57	Near Source Sound Level Guarantee	5

1.58	Notice	5

1.59	O & M Instruction Liquidated Damages	5

1.60	O&M Manuals	5

1.61	Optional Delivery Point	5

1.62	Order Definition Meeting (ODM)	5

1.63	Output Liquidated Damages Refund Reduction	5

1.64	Patent Indemnities	6

1.65	Payment Date	6

1.66	Payment Schedule	6

1.67	Performance Liquidated Damages	6

1.68	Performance Test	6

1.69	Performance Test Completion Certificate	6

1.70	Performance Test Certificate	6

1.71	Power Purchaser	6

1.72	Primary Warranty Period	6

1.73	Project Manager	6

1.74	Proper Scope Value	6

1.75	Punchlist	6

1.76	Purchase Amount	6

1.77	Purchaser	6

1.78	Purchaser Claimant	7

1.79	Purchaser Indemnitees	7

1.80	Purchaser Related Parties	7

1.81	Purchaser’s Representative	7

1.82	Refund Amount	7

1.83	Related Dispute	7

1.84	Retention Amount	7

1.85	Retention Letter of Credit	7

1.86	Scope of Work	7

1.87	Scope Value Due	7

1.88	Seller	7

1.89	Seller Claimant	7

1.90	Seller’s Indemnitees	7

1.91	Shortfall	7

1.92	Site	7

1.93	Site Delivery Date	7

1.94	Sound Levels	7

1.95	Sound Level Guarantee	7

1.96	Sound Level Test	7

1.97	Sound Level Test Procedures	7

1.98	Specific Performance	8

1.99	Specific Performance Electrical Output Guarantee	8

1.100	Specific Performance Exhaust Gas Temperature Guarantee	8

1.101	Specific Performance Exhaust Gas Energy Guarantee	8

1.102	Specific Performance Heat Rate Guarantee	8

1.103	Specific Performance Levels	8

1.104	Specification	8

1.105	Takeover	8

1.106	Take Over Criteria	8

1.107	Take Over Liquidated Damages	8

1.108	Technical Direction of Installation (TD of I)	8

1.109	Termination Costs	8

1.110	Termination Settlement	8

1.111	Test Procedures	8

1.112	Time for Completion	8

1.113	Training	9

1.114	Transportation Option	9

1.115	Unit	9

1.116	Unit Output Liquidated Damages	9

1.117	Unit Liability Amount	9

1.118	Vendor	9

ARTICLE II. RESPONSIBILITIES OF PURCHASER	9

2.1	Purchaser Responsibilities	9

2.2	Purchaser Conduct	9

ARTICLE III. RESPONSIBILITIES OF SELLER	9

3.1	General Obligations	9

3.2	Delivery of Equipment and Documentation.	10

3.2.1	Delivery of Equipment to the Delivery Point	10

3.2.2	Delivery to Optional Delivery Point	10

3.2.3	Impact Indicators	10

3.2.4	Packing List	10

3.3	Relevant Information	10

3.4	Hazardous Materials Notification.	11

3.5	Employment of Trained and Experienced Personnel	11

3.6	Not Used.	11

3.7	Guarantee	11

3.8	Compliance with Governmental Rules	11

3.9	Approved Vendors	13

3.10	Packing and Insurance Surveyor.	14

3.10.1	Packing Recommendation	14

3.10.2	Insurability Certificate	14

3.10.3	Notice of Shipment	14

3.10.4	Compliance with Recommendation	15

3.10.5	Coordination	15

3.11	Financing and Insurance Assistance	15

3.12	Purchaser Permit Support	15

3.13	Order Definition Meeting	15

3.14	Not Used.	15

3.15	Key Personnel	15

3.16	Seller’s Representations	15

ARTICLE IV. RESPONSIBILITY FOR INFORMATION	16

4.1	Purchaser Supplied Information	16

ARTICLE V. PURCHASE AMOUNT AND OTHER CHARGES	16

5.1	Purchase Amount	16

5.2	Taxes and Contributions.	16

5.2.1	Seller’s Responsibility for Personal Taxes	16

5.2.2	Seller’s Responsibility for Taxes	17

5.2.3	Tax Penalties	17

5.3	Changes to the Purchase Amount	17

5.4	Cancellation.	18

5.4.1	Cancellation by Purchaser	18

5.4.2	Marketing Agreement	18

5.5	Suspension or Change of Delivery.	18

ARTICLE VI. PAYMENT TERMS	19

6.1	Payment of Purchase Amount.	19

6.1.1	Payment Periods	19

6.1.2	Payment Schedule.	19

6.1.3	Retention Letter(s) of Credit	19

6.2	Payment Disputes	19

6.3	Payments Withheld or Offset.	20

6.3.1	Payments Withheld	20

6.3.2	Offset for Liquidated Damages	20

6.4	Payment of Liquidated Damages.	20

6.4.1	Payment of O&M Instruction Liquidated Damages	21

6.4.2	Payment of Delivery Liquidated Damages	21

6.4.3	Payment of Take Over Liquidated Damages	21

6.4.4	Payment of Performance Liquidated Damages	21

6.5	Payment for Changes	21

6.6	Lien Release	21

6.7	Invoices.	22

6.7.1	Agreement Reference	22

6.7.2	Payee and Address for Invoices	22

6.7.3	Date of Receipt	22

6.8	Method of Payment	22

6.9	Payments Not Acceptance of Work	23

ARTICLE VII. COMMENCEMENT OF THE WORK AND TERMINATION	23

7.1	Not Used.	23

7.2	Not Used.	23

7.2.1	Not Used.	23

7.2.2	Not Used.	23

7.2.3	Not Used.	23

7.2.4	Not Used.	23

7.3	Termination	23

ARTICLE VIII. NOT USED	23

ARTICLE IX. INSPECTION AND CORRECTION OF WORK	23

9.1	Inspections	23

9.2	Resident Facilities	24

9.3	Quality Plan	24

9.4	Notice	24

9.5	Correction of Equipment	24

9.6	Additional Factory Testing	25

9.7	Release for Delivery	25

ARTICLE X. DELIVERY AND PERFORMANCE	25

10.1	Delivery of Documentation.	25

10.1.1	Purchaser Review of Documents	25

10.1.2	Delivery of Final O & M Instructions	26

10.2	Delivery of Equipment.	26

10.2.1	Guaranteed Unit Delivery Dates	26

10.2.2	Inventory Upon Delivery	26

10.2.3	Delivery	27

10.2.4	Extensions of the Guaranteed Unit Delivery Date.	27

10.2.5	Loading Responsibilities at Delivery Point	28

10.2.6	OffLoading Responsibilities at Optional Delivery Point	28

10.2.7	Unit(s) Storage	28

10.3	Delivery Liquidated Damages.	28

10.3.1	Unit Delivery Liquidated Damages	28

10.3.2	Take Over Liquidated Damages	29

10.3.3	Invoicing for Delivery and Take Over Liquidated Damages	30

10.4	Specific Performance Exhaust Gas Temperature and Energy Guarantees.	30

10.4.1	Not Used.	30

10.4.2	Specific Performance Exhaust Gas Temperature Guarantee For Combined Cycle Application of Units	31

10.4.3	Not Used.	31

10.4.4	Specific Performance Exhaust Gas Energy Guarantee For Combined Cycle Application of Units	31

10.4.5	Interaction of Exhaust Gas Energy and Exhaust Gas Temperature with Turbine Net Output	31

10.5	Sound Level Specific Performance Guarantee.	31

10.5.1	Specific Performance Near Source Sound Level Guarantee	31

10.5.2	Specific Performance Far Field Sound Level Guarantee	31

10.5.3	Not Used.	32

10.5.4	Sound Level Test	32

10.6	Specific Performance Exhaust Emissions Guarantee	32

10.7	Electrical Output Guarantees.	33

10.7.1	Electrical Output Guarantee	33

10.7.2	Specific Performance Electrical Output Guarantee	33

10.8	Heat Rate Guarantees.	33

10.8.1	Heat Rate Guarantee	33

10.8.2	Not Used.	33

10.8.3	Specific Performance Heat Rate Guarantee	33

10.8.4	Specific Performance Guarantee	33

10.9	Performance Liquidated Damages	33

10.9.1	Unit Output Liquidated Damages	33

10.9.2	Heat Rate Liquidated Damages	34

10.9.3	Most Recent Performance Test	34

10.9.4	Performance Test Required	34

10.9.5	Setting Out of Performance Liquidated Damages	34

10.9.6	Not Used	34

10.9.7	Seller’s Improvement of Performance	34

10.9.8	Reduction in Performance Liquidated Damages	34

10.10	Maximum Liabilities for Liquidated Damages	36

10.10.1	Maximum O&M Instruction Liquidated Damages	36

10.10.2	Maximum Delivery Liquidated Damages	36

10.10.3	Maximum Take Over Liquidated Damages	36

10.10.4	Maximum Unit Output Liquidated Damages	36

10.10.5	Maximum Heat Rate Liquidated Damages	36

10.10.6	Maximum Aggregate Liquidated Damages	36

10.11	Liquidated Damages Not Penalty	36

10.12	Performance Tests.	37

10.12.1	Concurrence of Tests	37

10.12.2	Election to Conduct a Performance Test	37

10.12.3	Specific Performance Achievement	37

10.12.4	Timing of Tests.	37

10.12.5	Seller Presence at Tests	38

10.12.6	Test Results	38

10.12.7	Performance Test Procedures	38

10.12.8	Reconduct Tests	38

10.12.9	Not Used.	39

10.12.10	Fittings, Instrumentation and Test Uncertainty.	39

10.12.11	Consumable Spare Parts During Retests	39

10.13	Remedies For Failure to Meet Specific Performance Requirements.	39

10.13.1	Corrective Actions	39

10.13.2	Failure to Achieve Specific Performance	40

10.14	Acceptance	40

10.15	Unit Serial Numbers	41

ARTICLE XI. CHANGE ORDER	41

11.1	Adjustment of Purchase Amount	41

11.2	Purchaser Requested Change Order	41

11.3	Seller Requested Change Order	41

11.4	Adjustment to Guaranteed Unit Delivery Dates	42

11.5	Disputes	42

11.6	Change Order Pricing	42

ARTICLE XII. (NOT USED)	42

ARTICLE XIII. ORDER OF PRECEDENCE	42

13.1	Order of Precedence	42

ARTICLE XIV. WARRANTY	42

14.1	Seller’s Warranty	42

14.1.1	Primary Warranty Period	43

14.1.2	Warranty Clarification	43

14.1.3	Warranty Breach Notice	44

14.2	Extended Warranty Period.	44

14.2.1	Continued Warranty on Corrections or Repairs Performed During the Primary Warranty Period	44

14.2.2	Extension of Warranty Due to Unavailability	44

14.3	Obligations, Responsibilities and Recourse	44

14.4	Not Used.	45

14.5	Limited Warranty	45

14.6	Repairs and Alterations by Others	45

14.7	Termination of Warranty	45

ARTICLE XV. RISK OF LOSS AND TITLE	46

15.1	Risk of Loss	46

15.2	Title.	46

15.2.1	Passage of Title	46

15.2.2	Infringement Cures and Defense	46

15.3	Seller’s Drawings, Etc. for Use by Purchaser	47

15.4	Licensing Procedure	47

ARTICLE XVI. TRAINING AND TECHNICAL DIRECTION OF INSTALLATION	48

ARTICLE XVII. DEFAULT	48

17.1	Events of Default by Seller	48

17.2	Purchaser’s Remedies Against Seller	49

17.3	General Obligations	50

17.4	Payment Obligations.	50

17.4.1	Determination of Obligations	50

17.4.2	Damages and Expenses	51

17.4.3	Cover Damages	51

17.4.4	Settlement	51

17.5	Events of Default by Purchaser	52

17.6	Seller Remedies	52

ARTICLE XVIII. FORCE MAJEURE	53

18.1	Failure to Perform Due to an Event of Force Majeure	53

18.2	Events of Force Majeure	53

18.3	Notice of Event of Force Majeure	53

18.4	Events of Force Majeure	54

18.5	Certain Events Not Excused	54

18.6	Continued Performance	55

18.7	Not Used.	55

18.8	Event of Force Majeure - Delays	55

18.9	Event of Force Majeure - Cost	55

ARTICLE XIX. INSURANCE	55

19.1	Insurance - General	55

19.1.1	All Risk	55

19.1.2	Workers Compensation and Employers Liability Insurance	56

19.1.3	Commercial General Liability Insurance	56

19.1.4	Hull and Protection and Indemnity Insurance	56

19.1.5	Business Automobile Liability Insurance	56

19.1.6	Aircraft Liability Insurance	57

19.1.7	Excess Umbrella Liability Coverage	57

19.1.8	Vendors	57

19.1.9	Certificate of Insurance	57

19.1.10	Other Requirements	57

19.1.11	Vendor Waiver of Subrogation	58

19.1.12	Compliance with Insurance	58

19.1.13	Limitation	58

19.2	Purchaser’s Insurance.	59

19.2.1	Cargo Insurance	59

19.2.2	Builder’s All Risk Insurance	59

ARTICLE XX. INDEMNIFICATION	59

20.1	Third Party	59

20.2	Survival of Obligation	61

ARTICLE XXI. NON-DISCLOSURE OF INFORMATION	61

21.1	Proprietary Information	61

21.2	Press Releases	62

21.3	Confidentiality of Seller	62

21.4	Confidentiality of Purchaser	64

ARTICLE XXII. ASSIGNMENT	65

22.1	Assignment by Seller	65

22.2	Assignment by Purchaser	65

ARTICLE XXIII. RELATIONSHIP OF THE PARTIES	66

23.1	Independent Contractor	66

23.2	Responsibilities of Seller as Principal for its Employees	67

23.3	Not Used.	67

ARTICLE XXIV. LIENS AND CLAIMS	67

ARTICLE XXV. NOTICES AND COMMUNICATIONS	67

25.1	Notices	67

25.2	Effectiveness of Notices	68

25.3	Technical Communications	68

ARTICLE XXVI. ARBITRATION	69

26.1	Negotiation of Disputes and Disagreements	69

26.2	Arbitration Resolution	69

26.3	Continuation of Work	70

26.4	Not Used.	70

26.5	Not Used.	70

ARTICLE XXVII. LIMITATION OF LIABILITY	70

27.1	Maximum Liability	70

27.2	Consequential Losses	70

27.3	Releases Valid in All Events	70

27.4	Seller’s Advice or Assistance	71

ARTICLE XXVIII. DRUG AND ALCOHOL-FREE WORKPLACE	71

ARTICLE XXIX. PROJECT PLANNING AND CONTROLS	71

ARTICLE XXX. MISCELLANEOUS	71

30.1	Validity and Enforceability	71

30.2	Governing Law	72

30.3	Entire Agreement	72

30.4	Agreement Modification	72

30.5	Waiver	72

30.6	Headings	72

30.7	Third-Party Beneficiaries	72

30.8	Counterparts	72

30.9	Equal Employment Opportunity	72

30.10	Cooperation on Site	72

30.11	Nuclear Material	72

EXHIBIT A  BASIS CONDITIONS	75

EXHIBIT A-1 BASIS FUEL	76

EXHIBIT A-2 NOT USED	77

EXHIBIT A-3  NOT USED	78

EXHIBIT B  SCOPE OF WORK/SPECIFICATION	79

EXHIBIT B-1  SPECIFICATION FOR LM6000 SPRINT™ GAS TURBINE GENERATOR SET	81

EXHIBIT B-2  NOT USED	129

EXHIBIT B-3  NOT USED	130

EXHIBIT B-4  APPROVED VENDORS	131

EXHIBIT B-5  DOCUMENT REVIEW STATUS CRITERIA	138

EXHIBIT C-1  SELLER PARENT GUARANTEE	140

EXHIBIT C-2  NOT USED	142

EXHIBIT E NOT USED	145

EXHIBIT F  PERFORMANCE TEST GUIDELINES	146

EXHIBIT F-1  SOUND LEVEL TEST GUIDELINES	150

EXHIBIT F-2  EMISSIONS TEST GUIDELINES	152

EXHIBIT G-1  PERFORMANCE TEST CERTIFICATE	156

EXHIBIT G-2  PERFORMANCE TEST COMPLETION CERTIFICATE	157

EXHIBIT H-1  TECHNICAL DIRECTION OF INSTALLATION	159

EXHIBIT H-2  TRAINING	163

EXHIBIT I  CANCELLATION CHARGE	169

EXHIBIT J  QUALITY	170

EXHIBIT K  PROJECT PLANNING	175

EXHIBIT L EQUIPMENT REQUIRING INSURABILITY CERTIFICATE	177

EXHIBIT M-1  NOT USED	178

EXHIBIT M-2 NOT USED	179

EXHIBIT N-1  NOT USED	180

EXHIBIT N-2  OPTIONS	181

EXHIBIT O  HAZARDOUS MATERIAL NOTIFICATION	183

EXHIBIT P  UNIT SERIAL NUMBER	185

EXHIBIT Q SAMPLE PACKING LIST	186

EXHIBIT R  NOT USED	188

EXHIBIT S  FINAL WAIVER  OF LIENS FORM	189

EXHIBIT T  NOT USED	193

EXHIBIT U  NOT USED	194

AGREEMENT

This Agreement is made and entered into as of this ____ day of ________, 2001, (hereinafter, the “Effective Date”), by and between E-Next Generation LLC, (“Purchaser”), a Delaware limited liability company, acting through its agent Enron North America Corp., a corporation incorporated under the laws of the state of Delaware, and GE Packaged Power, Inc. a corporation incorporated under the laws of Delaware, with offices located at 2707 North Loop West, Houston, Texas 77008 (“Seller”).

RECITALS

WHEREAS, Purchaser has a need to acquire four (4) LM6000 Enhanced Sprint combustion turbine generator sets (the “Units,” whether one or more) for installation in its 224,000 kW (nominal) electricity generation plant to be located in or near the City of North Las Vegas, Nevada (the “Facility”); and

WHEREAS, Seller is in the business of designing, engineering, manufacturing, and supplying Units and auxiliary services in connection therewith;

WHEREAS, Purchaser has agreed to purchase from Seller, and Seller has agreed to sell to Purchaser, the Units pursuant to the terms of this Agreement; and

NOW, THEREFORE, in consideration of the mutual covenants herein contained, and intending to be legally bound, the parties hereto agree as follows:

# DEFINITIONS

Terms used in this Agreement without other definition shall have the meanings specified in this ARTICLE I, unless the context requires otherwise.

As used in this Agreement, the terms “herein”, “herewith” and “hereof” are references to this Agreement, taken as a whole, the term “includes” or “including” shall mean “including, without limitation,” and references to a “Section”, “subsection”, “clause”, “Article”, “Exhibit”, “Appendix” or “Schedule” shall mean a Section, subsection, clause, Article, Exhibit, Appendix or Schedule of this Agreement, as the case may be, unless in any such case the context requires otherwise.  All references to a given agreement, instrument or other document shall be a reference to that agreement, instrument or other document as modified, amended, supplemented and restated through the date as of which such reference is made, and reference to a law, regulation or ordinance includes any amendment or modification thereof.  A reference to a person includes its successors and permitted assigns.  The singular shall include the plural and the masculine shall include the feminine, and vice versa.

## Acceptance»

.  Shall have the meaning as set forth in Section 10.14.

## Adjusted Electrical Output»

.  Shall mean the Electrical Output adjusted from test conditions to  Basis Conditions by the methods described in Exhibit F.

## Adjusted Emissions»

.  Shall mean the Emissions as measured during the Performance Tests and adjusted to Basis Conditions by the methods described in Exhibit F.

## Adjusted Exhaust Gas Energy»

.  Shall mean the Exhaust Gas Energy of a Unit as measured during a Performance Test and adjusted from test conditions to Basis Conditions by methods described in Exhibit F.

## Adjusted Exhaust Gas Temperature»

.  Shall mean the Exhaust Gas Temperature of a Unit as measured during a Performance Test and adjusted from test conditions to Basis Conditions by methods described in Exhibit F.

## Adjusted Heat Rate»

.  Shall mean the Heat Rate adjusted from test conditions to Basis Conditions by the methods described in Exhibit F.

## Affected Party»

.  Shall have the meaning set forth in Section 18.1.

## Affiliate»

.  Shall mean a person or entity who, with respect to a specified  person or entity, directly or indirectly through one or more intermediaries controls, or is controlled by, or is under common control with, the person or entity specified.

## Agreement»

.  Shall mean this Agreement, including all Exhibits attached hereto and the Specification, as amended from time to time as provided herein.

## Applicable Laws»

.  Shall mean any applicable national, municipal or local statute, ordinance or other law, regulation or by-law or any rule, code or direction or any license, consent, permit, authorization or other approval including any conditions attached hereto (whether relating to the environment or otherwise) of the government of the United States or foreign jurisdiction or of any public body or authority, local or national agency, department, inspector, ministry, official or public or statutory person (whether autonomous or not) which has appropriate jurisdiction pertaining to a particular Unit.

## Base Load»

.  Shall mean the operation of the Units at 100% Electrical Output for the prevailing ambient temperature, relative humidity, barometric pressure, fuel heating value, exhaust temperature limitation, rated frequency, power factor and voltage.

## Basis Conditions»

.  Shall mean the conditions set forth in Exhibit A which are the basis for the Guaranteed Levels and Specific Performance Levels.

## BTU»

.  Shall mean British Thermal Unit, where one (1) BTU is equal to 1055.056 joules.

## Cancellation Charge»

.  Shall have the meaning as set forth in Section 5.4.1.

## Change in Law»

.  Shall mean any change in, or binding change in the judicial or administrative interpretation of, or adoption of, any Applicable Law, which is implemented after May 12, 2000, and which has an adverse affect on Seller’s ability to perform its obligations under this Agreement; provided, however, that a change in any federal, commonwealth, state or local income or franchise tax law, workers’ compensation, or payroll or withholding tax law shall not constitute a change in law hereunder.

## Change Order»

.  Shall have the meaning as set forth in Section 11.2.

## Claim»

. Shall have the meaning set forth in Section 20.1(a).

## Commercial Operation»

.  Shall mean the reliable operation of the Unit by Purchaser in accordance with industry standards while the Unit is connected to the utility grid and producing electrical energy for sale. This does not include power that may be sold during start up, commissioning, or a performance test unless the generation of such power prevents commissioning.

## Commissioning Period»

.  Shall mean Purchaser’s allowance of thirty (30) days from first roll of each Unit to complete Unit commissioning check outs, any needed replacement, adjustments or corrections to make the Unit(s) ready for testing.

## Cover Damages»

.  Shall have the meaning set forth in Section 17.4.3.

## Day»

.  Shall mean a calendar day, including weekdays, weekends, and holidays.

## Delivery Liquidated Damages»

.  Shall have the meaning as set forth in Section 10.3.1.

## Delivery Point»

.  Shall mean 16415 Jacinto Port Blvd., Houston, Texas.

## Effective Date»

.  Shall have the meaning as set forth in Recitals.

## Emissions»

.  Shall mean the exhaust emissions of a Unit as measured during a Performance Test.

## Emissions Guarantee»

.  Shall have the meaning and value as set forth in Section 10.6.

## Electrical Output»

.  Shall mean the electric output of a Unit measured at the generator terminals during a Performance Test deducting actual electrical consumption of the auxiliaries listed in Exhibit F.

## Electrical Output Guarantee»

.  Shall have the meaning as set forth in Section 10.7.1.

## Equipment»

.  Shall mean for each Unit the equipment comprising an LM6000 generator set described in the Specification and all other material and supplies including without limitation, software, installation and operations manuals and drawings to be furnished by Seller and/or its Vendors pursuant to the Scope of Work.

## Event of Force Majeure»

.  Shall have the meaning as defined in Section 18.4.

## Event of Purchaser Default»

.  Shall have the meaning as defined in Section 17.5.

## Event of Seller Default»

.  Shall have the meaning as defined in Section 17.1.

## Exhaust Gas Energy»

.  Shall mean the exhaust gas energy of a Unit measured or calculated at the gas turbine exhaust outlet during a Performance Test.

## Exhaust Gas Temperature»

.  Shall mean the exhaust gas temperature of a Unit measured or calculated at the gas turbine exhaust outlet during a Performance Test.

## Extended Warranty Period»

.  Shall have the meaning as set forth in Section 14.2.1.

## Facility»

.  Shall have the meaning set forth in the Recitals.

## Far Field Sound Level Guarantee»

.  Shall have the meaning as set forth in Section 10.5.2.

## Guaranteed Levels»

.  Shall mean the Electrical Output Guarantee, and Heat Rate Guarantee.

## Guaranteed Unit Delivery Dates»

.  Shall have the meaning as set forth in Section 10.2.1.

## Hazardous Materials»

.  Shall mean any hazardous substance or hazardous waste as defined in the Comprehensive Environmental Response, Compensation and Liability Act of 1980, as amended, the Resource Conservation and Recovery Act, as amended, the Hazardous Waste Transportation Act, as amended, and regulations promulgated pursuant to these Acts and any similar federal, state or local law or regulation defining hazardous substances or hazardous waste, and any equipment containing polychlorinated biphenyls or asbestos that may become friable.

## Heat Rate»

.  Shall mean the actual fuel energy consumed during the Performance Test determined from the actual lower heating value of the fuel multiplied by the quantity of fuel consumed and expressed in BTU, divided by the Electrical Output measured in kWh at the generator terminals during the Performance Tests in accordance with the testing guidelines set forth in Exhibit F, expressed as BTU/kWh(LHV).

## Heat Rate Guarantee»

.  Shall have the meaning as set forth in Section 10.8.1.

## Heat Rate Liquidated Damages»

.  Shall have the meaning as set forth in Section 10.9.2.

## Heat Rate Liquidated Damages Refund Reduction»

.  Shall have the meaning as set forth in Section 10.9.8.

## Installation Period»

.  Shall mean the period of 9 months from the date the applicable Unit is delivered to the Site, but no later than 15 months after the later of the applicable Guaranteed Unit Delivery Date or the date  the Unit is placed in storage at Purchaser’s election.

## Insurability Certificate»

.  Shall have the meaning as set forth in Section 3.10.2.

## Insurance Representative»

.  Shall have the meaning as set forth in Section 3.10.1.

## Interest Rate»

.  Shall mean the Prime Rate as published by Citibank, N.A. at its New York City  office plus two percent (2%) per annum, provided however, that the rate of interest hereunder shall never exceed the highest applicable lawful rate.

## kW»

.  Shall mean kilowatt.

## kWh or kwh»

.  Shall mean kilowatt hour.

## Lender»

.  Shall mean any financial institution or financier from which financing in connection with the Facility and associated facilities and services is obtained by Purchaser or its Affiliate.

## Liquidated Damages»

.  Shall mean any or all Take Over Liquidated Damages, Delivery Liquidated Damages, O & M Instruction Liquidated Damages, and/or Performance Liquidated Damages.

## Liquidated Damages Events»

.  Shall have the meaning set forth in Section 10.11.

## Major Components»

.  Shall mean and consist of all parts and materials of the following for each Unit:

Inlet Filter Module

Gas Turbine (drive module) with Combustors Installed

Electric Generator (driven module)

Combined Starting Auxiliary Skid

Water Injection High Pressure Pump Skid

Unit Control Panel

Sprint Injection Pump Skid

## Marketing Agreement»

.  Shall have the meaning as set forth in Section 5.4.2.

## Maximum Liability Amount»

.  Shall be xxxxxxxxx, as such amount may be increased by approved Change Orders.

## Near Source Sound Level Guarantee»

.  Shall have the meaning as set forth in Section 10.5.1.

## Notice»

.  Shall mean any notification of one party hereto by the other party hereto with respect to any matter arising under or in connection with this Agreement, to be given as provided in Section 25.1 hereof.

## O & M Instruction Liquidated Damages»

. Shall have the meaning set forth in Section 10.1.2.

## O&M Manuals»

.  Shall have the meaning set forth in Section 10.1.2.

## Optional Delivery Point»

.  Shall mean the place for delivery of the Units as set forth in Section 10.2.3.1.

## Order Definition Meeting (ODM)»

. Shall have the meaning set forth in Section 3.13.

## Output Liquidated Damages Refund Reduction»

.  Shall have the meaning as set forth in Section 10.9.8.

## Patent Indemnities»

. Shall have the meaning set forth in Section 15.2.2.

## Payment Date»

.  Shall have the meaning set forth in Section 6.1.1.

## Payment Schedule»

.  Shall have the meaning as set forth in Section 6.1.2.

## Performance Liquidated Damages»

.  Shall mean the Unit Output Liquidated Damages and Heat Rate Liquidated Damages.

## Performance Test»

.  Shall mean the test(s) conducted at the Site on the Unit(s) in accordance with the Test Procedures to determine Emissions, Heat Rate, Electrical Output and Sound Levels.  In the case of combined cycle applications, Units will be tested for Exhaust Gas Energy and Exhaust Gas Temperature.

## Performance Test Completion Certificate»

.  Shall mean the certificate prepared by  Purchaser in the format attached hereto as Exhibit G-2 and provided to Seller, certifying the results of the Performance Tests that have been completed and quantifying Performance Liquidated Damages, if any, due.

## Performance Test Certificate»

.  Shall mean the certificate prepared by Purchaser in the format attached hereto as Exhibit G-1 and provided to Seller, certifying that a Performance Test has been completed and setting forth the results thereof in such detail to reflect the performance of the Units as tested with respect to Electrical Output, Emissions, Heat Rate and Sound Levels.  In the case of combined cycle applications, testing for Exhaust Gas Energy and Exhaust Gas Temperature will be performed by Purchaser if the combined cycle Facility has demonstrated a shortage of steam-generated performance.

## Power Purchaser»

.  Shall mean the applicable utility or any power purchaser, which has entered into a contract with Purchaser, or its Affiliate, to purchase power from the Facility.

## Primary Warranty Period»

.  Shall have the meaning as set forth in Section 14.1.1.

## Project Manager»

.  Shall mean the project manager designated by Seller pursuant to Section 3.3(a) hereof.

## Proper Scope Value»

.  Shall have the meaning as set forth in Section 17.4.1.

## Punchlist»

.  Shall mean the list of the incomplete or deficient work or materials associated with Seller’s Scope of Work, which is comprised of those items which are minor in nature and do not affect the performance of the Equipment, safety or personnel working on or operating the Equipment or the ability of the Equipment to be used for its intended purpose.  Punchlists shall be produced by Seller and approved by Purchaser for each Unit or the Facility.

## Purchase Amount»

.  Shall mean the $50,785,900.00 payable to Seller that constitutes the balance due for the Units, as adjusted pursuant to the terms of this Agreement.

## Purchaser»

.  Shall mean E-Next Generation LLC, its successors and permitted assigns.

## Purchaser Claimant»

. Shall have the meaning set forth in Section 20.1(a).

## Purchaser Indemnitees»

. Shall have the meaning set forth in Section 20.1(a).

## Purchaser Related Parties»

.  Shall have the meaning as set forth in Section 19.1.11.

## Purchaser’s Representative»

.  Shall mean the individual designated by Purchaser pursuant to Section 2.1(a) hereof, who shall have the responsibility and authority specifically delegated to such individual by Purchaser and made known in writing to Seller.

## Refund Amount»

.  Shall have the meaning as set forth in Section 17.4.1.

## Related Dispute»

.  Shall have the meaning as set forth in Section 26.2(c).

## Retention Amount»

.  Shall have the meaning as set forth in Section 6.1.3.

## Retention Letter of Credit»

.  Shall have the meaning as set forth in Section 6.1.3.

## Scope of Work»

.  Shall mean all design, engineering, manufacture, delivery, transportation, technical direction of installation, training, technical services, Equipment, drawings, documentation, supplies and materials to be performed and/or furnished by Seller or its Vendors pursuant to this Agreement or would have been reasonably expected to be supplied by a prudent supplier to ensure the successful operation of the Units.

## Scope Value Due»

.  Shall have the meaning as set forth in Section 17.4.1.

## Seller»

.  Shall mean GE Packaged Power, Inc., its successors and permitted assigns.

## Seller Claimant»

. Shall have the meaning set forth in Section 20.1(b).

## Seller’s Indemnitees»

. Shall have the meaning set forth in Section 20.1(b).

## Shortfall»

.  Shall mean the amount by which a Unit fails to meet a Guaranteed Level.  Such shortfall shall be measured in the same units as the respective guarantee.

## Site»

.  Shall mean any part of the land of the Facility.

## Site Delivery Date»

.  Shall mean the date on which a Unit is delivered  to the Site.

## Sound Levels»

.  Shall mean the Near Source Sound Level Guarantee and the Far Field Sound Level Guarantee.

## Sound Level Guarantee»

.  Shall mean the Near Source Sound Level Guarantee and the Far Field Sound Level Guarantee.

## Sound Level Test»

.  Shall have the meaning as set forth in Section 10.5.4.

## Sound Level Test Procedures»

.  Shall mean the test procedures used to measure Sound Levels as set forth in Exhibit F-1.

## Specific Performance»

.  Shall mean, whether used by itself or as part of another defined term, an obligation that Seller must fulfill or achieve, or otherwise be in breach of its obligations hereunder.  Seller shall not be able to pay Liquidated Damages in lieu of meeting such specific performance requirements.

## Specific Performance Electrical Output Guarantee»

.  Shall have the meaning as set forth in Section 10.7.2.

## Specific Performance Exhaust Gas Temperature Guarantee»

.  Shall have the meaning  as set forth in Section 10.4.2.

## Specific Performance Exhaust Gas Energy Guarantee»

.  Shall have the meaning  as set forth in Section 10.4.4.

## Specific Performance Heat Rate Guarantee»

.  Shall have the meaning as set forth in Section 10.8.3.

## Specific Performance Levels»

.  Shall mean the Specific Performance Electrical Output Guarantee, Specific Performance Heat Rate Guarantee, Emissions Guarantee and Sound Level Guarantee.  If the Facility is a combined cycle plant, it shall also include the Specific Performance Exhaust Gas Temperature Guarantee and the Specific Performance Exhaust Gas Energy Guarantee.

## Specification»

.  Shall mean the specification as issued by Purchaser for the design, manufacture, assembly set forth in Exhibit B, and the specification by Seller for the supply of the Units as set forth in Exhibit B-1.

## Takeover»

.  Shall mean that the Performance Tests have been conducted for a Unit, and  that the Purchaser has accepted the Unit for the purpose of placing the Unit into Commercial Operation.

## Take Over Criteria»

.  Shall mean that a Unit has met its Specific Performance Levels during the applicable Performance Tests and is capable of being commissioned and placed into Commercial Operation.

## Take Over Liquidated Damages»

.  Shall have the meaning as set forth in Section 10.3.2.

## Technical Direction of Installation (TD of I)»

.  Shall have the meaning and scope as set forth in Exhibit H-1.

## Termination Costs»

.  Shall have the meaning as set forth in Section 17.4.2.

## Termination Settlement»

.  Shall have the meaning as set forth in Section 17.4.4.

## Test Procedures»

.  Shall have the meaning as set forth in Section 10.12.7.

## Time for Completion»

.  Shall mean the date of one hundred twenty (120) Days after any specific Unit arrives at the Site.

## Training»

.  Shall have the meaning and scope as set forth in Exhibit H-2.

## Transportation Option»

.  Shall have the meaning set forth in Section 3.2.2.

## Unit»

. Shall mean one LM6000 Enhanced Sprint combustion turbine generator package.

## Unit Output Liquidated Damages»

.  Shall have the meaning as set forth in Section 10.9.1.

## Unit Liability Amount»

.  Shall mean, for each Unit, xxxxxxxxxxxx, as such amount may be increased by approved Change Orders.

## Vendor»

.  Shall mean any vendor, supplier or subcontractor utilized by Seller in the performance of the Scope of Work hereunder.

# RESPONSIBILITIES OF PURCHASER

## Purchaser Responsibilities»

.  Purchaser recognizes and acknowledges the duty to reasonably cooperate with Seller, and agrees not to wrongfully interfere with Seller’s agents, employees or Vendors during the performance of this Agreement.  Without limiting the generality of the foregoing, Purchaser shall be responsible for the following matters and actions to be performed on a timely basis:

##### Purchaser shall designate a Purchaser’s Representative and deliver a Notice to Seller identifying Purchaser’s Representative, within thirty (30) Days of the latest date of signature of this Agreement, who shall act as the primary point of contact for Seller with respect to the prosecution of the Scope of Work;

##### Purchaser shall deliver a Notice within thirty (30) Days of the latest date of signature of this Agreement to Seller identifying such persons within Purchaser’s organization that have authority to approve Change Orders;

##### Purchaser shall pay to Seller the sums required to be paid by Purchaser pursuant to the terms of this Agreement; and

##### the Units shall be installed, operated and maintained by or on behalf of Purchaser as identified in Exhibit B-1, Section 3 and as otherwise stated in the Agreement.

## Purchaser Conduct»

. Purchaser will comply with applicable regulatory requirements and Applicable Laws which pertain to Purchaser’s obligations under this Agreement. Unless otherwise agreed, Purchaser shall procure or cause to be procured the permits necessary for the installation and operation of the Equipment at the Site.

# RESPONSIBILITIES OF SELLER

## General Obligations»

.  Except as expressly set forth in this Agreement, Seller shall provide the new materials and supplies, technical and professional personnel and supervision at Seller’s facilities and as required for Seller to fulfill its transportation responsibilities, tools and equipment, and the services required for performance and timely completion of the Scope of Work, and shall be responsible for timely completing the Scope of Work in accordance with the terms of this Agreement.

References in the Specification to equipment, material, articles or patented processes by trade name, make, or catalog number, shall be regarded as the standard of quality to be met by Seller.  Seller may, subject to written notification to Purchaser, use any equipment, material, article, or process that is operationally, technically and functionally equivalent to that named in the Specification.  For the avoidance of doubt, all equipment, materials and components, whether or not specifically referenced in the Specification or elsewhere in the Agreement, which are incorporated by Seller or its Vendors  into the Scope of Work, shall be new, unrepaired and suitable for the purpose for which it is intended except as otherwise allowed pursuant to this Agreement.

## Delivery of Equipment and Documentation.

### Delivery of Equipment to the Delivery Point»

.  Except as otherwise provided in this Agreement, Seller shall deliver the Equipment to the Delivery Point in accordance with this Agreement by the dates set forth in Section 10.2.1.

### Delivery to Optional Delivery Point»

.  As an added option, to be exercised solely at the discretion of Purchaser, Purchaser may require Seller to deliver some or all of the Equipment to the Optional Delivery Point(s) in lieu of the Delivery Point(s) (the “Transportation Option”), and if so elected Seller shall deliver the specified Equipment to the Optional Delivery Point(s) in accordance with Section 10.2.3.1.  If Purchaser exercises the Transportation Option, the Purchase Amount shall be adjusted per Section 5.3.

### Impact Indicators»

.  To the extent Seller arranges for transportation for any or all of the Units, Seller shall provide Purchaser with details of procedures pertaining to securing the Units during transportation.  If as a result of such review, Purchaser reasonably determines that impact indicators are required, Seller shall do so at no additional cost to Purchaser.

### Packing List»

.  Seller shall provide a pro forma packing list as set forth in Exhibit Q and provide a final packing list thirty (30) Days prior to each shipment.

## Relevant Information»

.  Seller shall provide on a timely basis to Purchaser information reasonably necessary to fulfill Seller’s obligations pursuant to this Agreement, including, without limitation:

##### within fifteen (15) Days of the latest signature date of this Agreement, the identity  of a project manager (the “Project Manager”) who shall have full supervision over the completion of  the Scope of Work and who shall act as the primary point of contact with Purchaser regarding all matters relating to the Scope of Work;

##### such information as is requested by Purchaser in dealing with the Lenders, Power Purchaser and/or any governmental authority in matters relating to the Scope of Work.  Such obligation shall not include information such as grid or power generation studies for the total power system;

##### the project management plan proposed for this Agreement to include, but shall not be limited to staffing, milestones, scheduling, quality control, transportation, technical interface, and other mutually agreed matters required to successfully manage the project to conclusion; and,

##### no later than fourteen (14) Days prior to the shipment of the Unit, or first Unit if these shall be more than one, provide a master equipment bill of materials (BOM) for use by both parties to effectively track deliveries of each Unit’s components and facilitate verification of shipping,  inventory at Site, expediting of shortage lists and look-ahead planning in support of installation. Seller shall provide updates to the BOM periodically as the parties shall reasonably agree is necessary to maintain the effectiveness of the document.

## Hazardous Materials Notification.

##### Seller warrants to Purchaser that in relation to the Scope of Work, it will use reasonable skill and care to ensure that there will not be Hazardous Material specified or permanently incorporated into the Scope of Work; provided that where in the opinion of Seller this results in any conflict with any relevant statutory requirements or where the Scope of Work would be prejudiced through lack of suitable alternatives, then Seller shall immediately notify Purchaser in writing specifying the conflict or prejudice which has arisen and the substance which Seller wishes to stipulate or use and Seller shall not stipulate or use the same without, in each case, the prior written consent of Purchaser which shall not be unreasonably withheld.

##### Seller shall immediately upon the request of Purchaser certify in writing that to the best of its knowledge that no Hazardous Materials have been specified or permanently incorporated in the Scope of Work. In the event Seller, with Purchaser’s approval, incorporates any Hazardous Materials into the Equipment, Seller shall provide Purchaser with notification as set forth in Exhibit O.

## Employment of Trained and Experienced Personnel»

.  Seller shall be responsible for employing and utilizing personnel and for ensuring that its Vendors employ and utilize personnel who possess the proper training and experience and are capable of performing the tasks for which they are employed or utilized.

## Not Used.

## Guarantee»

.  As a condition precedent to the effectiveness of any assignment pursuant to Section 22.1, Seller shall deliver to Purchaser an unconditional parent company guarantee from General Electric Company in the form set forth in  Exhibit C-1  hereto, which shall guarantee full payment and performance of all Seller obligations under this Agreement as due in accordance with the terms of this Agreement.

## Compliance with Governmental Rules»

.  Seller shall comply with Applicable Laws, including but not limited to those described below:

##### Seller Conduct.  Seller shall comply with applicable regulatory requirements including, without limitation, all Applicable Laws issued or promulgated by units of government and regulatory bodies with jurisdiction over any aspect of the performance of this Agreement by Seller. Seller shall not act in violation of the U.S. Foreign Corrupt Practices Act or similar law of the United States, and in connection therewith shall not make any payments, loans, or gifts directly or indirectly, to or for the use or benefit of any official employee, agency or instrumentality of any government, political party or candidate thereof, or any other person or entity, the payment of which would violate the laws or policies of the United States, or the country or countries in which the Scope of Work is performed, in whole or in part.  Seller shall possess or procure all permits, certificates, and licenses necessary to allow Seller to perform this Agreement at all locations of performance and shall ensure that Vendors have all permits, certificates, and licenses necessary for such Vendors to perform under this Agreement. Seller shall answer promptly and in reasonable detail any questionnaire or other written or oral communications, to the extent the same pertain to compliance with this Section 3.8(a) or (b) whether such questionnaires or communications are from Purchaser, their outside auditors, or other representatives.  Seller further agrees to pay any government assessed penalties, fines, and charges, and associated damages, costs, losses, and expenses (including, without limitation, court costs and attorneys’ fees) of whatever kind which Purchaser may incur, be required to pay or be liable for as a result of, in connection with, arising out of or related to any noncompliance of Seller’s performance of this Agreement or any portion thereof with any or all of the above laws, regulations, rules, orders, codes, criteria, standards, ordinances or resolutions.

##### Employment Practices.

###### Seller agrees that it shall be at all times during the term of this Agreement in full compliance with all Applicable Laws relative to Seller’s employment of employees and agents of Seller.

###### Seller agrees to pay any government assessed penalties, fines, and charges, and associated damages, costs, losses, expenses (including, without limitation, court costs and attorneys’ fees) of whatever kind which Purchaser may incur, be required to pay or be liable for as a result of, based on, in connection with, related to or arising from Seller’s noncompliance with this Section 3.8(b).

##### Scope of Work to Comply with Applicable Laws.  Subject to the provisions of Section 3.8(c)(iv):

###### Seller shall cause the Scope of Work to comply with Applicable Laws that were:

in effect on May 12, 2000; or

not yet in effect on May 12, 2000, but at such time a change to such valid Applicable Laws, issued or promulgated by units of government and regulatory bodies, had passed but was not yet effective;

In the event Seller fails to cause the Scope of Work to so comply with the Specification and Applicable Laws, Seller shall correct such noncomplying Scope of Work or portion thereof as necessary to comply with the above.  Seller shall bear the costs of correction of such noncomplying Scope of Work.  In the event that Purchaser reasonably determines that Seller is either not capable of performing the corrections or not capable of performing such corrections in time to meet Purchaser’s requirements, Purchaser may, at Seller’s expense, have the corrections made by a third party or make them itself; provided, however prior to Purchaser having the corrections performed by a third party or itself Purchaser shall have provided Seller Notice of its determination that it believes Seller is not capable of such performance of work or performing such corrections in a timely manner.

###### In the event that Seller does not comply with the Specification or Applicable Law, and Purchaser at its sole determination agrees Seller cannot reasonably incorporate the changes necessary for Seller to comply, Purchaser, in its sole discretion, may either (i) terminate the Agreement in whole or in part if Seller does not comply with the Specification or (ii) terminate the Agreement if Seller does not comply with the Applicable Law, each in accordance with ARTICLE XVII, or (iii) direct Seller to complete the Equipment without such changes, in which case Purchaser shall assume full responsibility for obtaining any necessary waivers from the appropriate federal, state or local authorities.

###### Seller shall, on a reasonable efforts basis, advise Purchaser of pending Applicable Laws so that Purchaser may make an informed decision as to whether to have the Equipment designed in anticipation of such pending change as it affects the Scope of Work.

###### In the event a Change in Law occurs subsequent to the times set forth in Section 3.8(c)(i), Seller shall prepare a request for a Change Order to Purchaser identifying the nature of the change, including any proposed extensions of time to the performance of the Scope of Work and the Purchase Amount.  In the event that Purchaser elects to not have Seller comply with such change, Purchaser shall indemnify Seller for such failure of the Scope of Work to comply with such new law requirement.

## Approved Vendors»

.  Purchaser agrees that Seller may utilize the Vendors listed in Exhibit B-4 for procurement of the components under which they are listed.  For those items of Equipment not listed in Exhibit B-4, Seller reserves the right in its sole discretion to obtain, source, subcontract, manufacture, fabricate and assemble the Equipment and any of its components and systems outside of the United States or from non-domestic concerns, or both, subject to the standards and obligations of the Agreement.  Seller will not utilize any Chinese sourced insulation or flanges in any case.

## Packing and Insurance Surveyor.

### Packing Recommendation»

.  Seller shall perform all packaging of the Equipment to the highest commercial standard practices of the industry to prevent damage during its handling and transportation to the Delivery Point or Optional Delivery Point (as the case may be).   Seller shall comply with Purchaser’s insurance representative’s (Salvage Association or similar insurance surveyor as appointed by Purchaser) (the “Insurance Representative”) recommendations concerning:

###### packaging of the Equipment;

###### Seller’s execution of the load plan on its transport to preclude damage during transit;

###### transshipment; and

###### movement to the Delivery Point (or Optional Delivery Point if applicable), including route surveys.

Seller shall immediately notify Purchaser of any unreasonable recommendations.

### Insurability Certificate»

.  Seller expressly acknowledges and agrees that it will not commence transport of the items of Equipment unless;

###### the Insurance Representative conducts a load plan and load survey and issues an insurance certificate, (the “Insurability Certificate”) attesting that its recommendations were carried out for such shipment with respect to the Equipment listed in Exhibit L; or

###### Purchaser’s Representative expressly waives such requirement for that shipment.

### Notice of Shipment»

.  Seller recognizes that failing to comply with this Section may jeopardize Purchaser’s insurance program.  Seller shall provide Purchaser’s Representative with reasonable advance Notice of the expected packing date and the expected loading date of any such shipment, and shall provide two business days advance Notice of the actual packing date and the actual loading date of such shipment.  Purchaser may designate its Insurance Representatives as recipient of such Notice.  Provided Seller has provided Purchaser with such Notice by such Notice dates, if the Insurance Representative is not available to perform the necessary inspections on the dates of loading indicated in Seller’s final Notice, or the recommendations of the Insurance Representative are mutually agreed by Seller and Purchaser to have been unreasonable, Purchaser shall extend the applicable Guaranteed Unit Delivery Date for the affected Unit to the extent Seller is delayed by such unavailability or unreasonable recommendations, and shall compensate Seller for any applicable costs including demurrage attributable thereto.  Seller shall provide the Insurance Representative with a load and transportation plan thirty (30) Days prior to loading. Seller acknowledges that all efforts and delays (other than as set forth in this Section 3.10) associated with receiving the Insurability Certificate shall not be grounds for extension to the Guaranteed Unit Delivery Date(s).

### Compliance with Recommendation»

.  Seller’s compliance with the Insurance Representative’s recommendations shall not relieve Seller of its responsibility for risk of loss and damage of the Equipment in accordance with this Agreement through delivery to the Delivery Point (or Optional Delivery Point if applicable).

### Coordination»

.  Seller agrees to host a transportation coordination meeting at its facility no later than forty-five (45) Days prior to shipment of the first Major Component for each Unit on a mutually agreed date.  Purchaser shall coordinate attendance by its Insurance Representative.

## Financing and Insurance Assistance»

.  Seller shall provide such information as Purchaser may reasonably request in connection with obtaining financing and insurance for the Facility including without limitation providing information related to design, engineering and status of the completion of the Scope of Work and Seller’s credentials and experience, and, as required, perform reasonable travel.  Purchaser shall reimburse Seller at commercially reasonable rates for its time in providing information not related to the Scope of Work.  Power Purchaser, Lender and their respective engineers and consultants shall have the right to participate in all inspections conducted by Purchaser under this Agreement and to attend all tests of the Equipment.  At Purchaser’s request, Seller shall furnish to Lender copies of Notices given to Purchaser hereunder.

## Purchaser Permit Support»

.  Seller shall provide all information, data and documents in a timely fashion that Purchaser may reasonably require for Purchaser to obtain Facility permits.

## Order Definition Meeting»

.  Seller agrees to host an order definition meeting (“ODM”) at its manufacturing facility no later than six (6) months prior to the Guaranteed Unit Delivery Date for the first Unit for the Facility or as otherwise mutually agreed, to finalize project scope issues for the purpose of Seller’s issuance of its ancillary equipment order and commencement of detailed engineering.

## Not Used.

## Key Personnel»

.  Seller shall provide Purchaser with biographical data for the Project Manager, and lead technical advisor for TD of I.  If, in the reasonable opinion of Purchaser, Purchaser determines such a key person is not adequately performing, Purchaser may require Seller to remove such person from work on the Scope of Work under this Agreement and replace with a satisfactory replacement.

## Seller’s Representations»

.  Seller represents and warrants to Purchaser that:

##### Seller is duly incorporated, organized, existing and in good standing under the laws of Delaware; Seller possesses all requisite power and authority to enter into and perform this Agreement, to carry out the transactions contemplated herein, and to conduct business in each of the locations where any portion of the Scope of Work is to be performed; and Seller has all legal power and authority to own and use its properties and to transact the business in which it is engaged and holds or expects to obtain all franchises, licenses, and permits required therefor;

##### Seller’s execution, delivery, and performance of this Agreement have been duly authorized by, and are in accordance with, its articles of incorporation and by-laws; this Agreement has been duly executed and delivered for it by the signatories so authorized; and this Agreement constitutes Seller’s legal, valid, and binding obligation; and

##### Equipment of the same type and model number which is sold by Seller or its Affiliates to other clients is of the same manufacturing technology as the Equipment provided under this Agreement and such equipment has not demonstrated trends of failure.

# RESPONSIBILITY FOR INFORMATION

## Purchaser Supplied Information»

.  Except to the extent that the information provided by Purchaser to Seller is in the form of a specification or performance requirement specifically called out in this Agreement or performance requirements which Purchaser is obligated to provide under the Agreement,  Seller will use reasonable efforts to verify that any supplemental information is accurate, correct, complete and fit for the particular purpose(s) for which Seller utilizes it.

# PURCHASE AMOUNT AND OTHER CHARGES

## Purchase Amount»

.  The Purchase Amount is based on Seller delivering the Equipment to the Delivery Point. The Purchase Amount shall be paid to Seller in accordance with ARTICLE VI.  The Purchase Amount is subject to increases or decreases only as provided in Section 5.3 and in accordance with ARTICLE XI.

Exhibit N-2 lists options, prices and times by which the options must be exercised by Purchaser.  If an option is exercised by Purchaser, the applicable option amount as set forth in Exhibit N-2 shall used to adjust the Purchase Amount.

Seller shall prepare the  initial invoices in the name of Purchaser and forward such invoices to Purchaser for approval and payment pursuant to Section 6.1.1.

## Taxes and Contributions.

### Seller’s Responsibility for Personal Taxes»

.  Seller assumes full responsibility for and agrees to pay or caused to be paid all contributions and taxes payable under all Applicable Laws pertaining to social security laws, unemployment compensation laws and income tax laws as they apply to Seller’s and Vendor’s employees engaged in the performance of the Scope of Work.  Seller acknowledges that Purchaser has no responsibility for such taxes as they apply to Seller or Seller’s employees or the employees.

### Seller’s Responsibility for Taxes»

.  Seller is responsible for taxes arising out of its performance of the Scope of Work including import duties, harbor taxes, personal and corporate taxes.  The price excludes any US state or local jurisdiction imposed property, license privilege, sales, use, excise, gross receipts, valued added, or similar tax which may now or hereafter be applicable to, measured by, or imposed upon with respect to the transaction, the sale, use, value and presence of Seller’s Scope of Work in such taxing jurisdiction, or any services performed in connection therewith.  Such taxes are for the account of Purchaser and Purchaser agrees to pay any such tax when due or reimburse Seller within twenty-five (25) Days after the date of Seller’s invoice Purchaser for any such tax which it is required to pay.  Seller shall provide timely documentation and assistance with respect to any tax paid.  Should Purchaser be exempted from any such tax it shall provide Seller with certification prior to transfer of title of such Scope of Work, or at the time the certification is obtained, whichever first occurs.

### Tax Penalties»

.  Seller further agrees to pay any tax, interest, penalty, fines, costs, losses and expenses (including, without limitation, court costs and reasonable attorney’s fees) of whatever kind, which Purchaser may incur, be required by law to pay, or be liable for as a result of, arising from, in connection with, related to or based on any failure to withhold any amounts from any payments made or any amounts which Seller fails to pay in connection with, as a result of, arising from or based on the Scope of Work or otherwise comply with this Section 5.2.3.

## Changes to the Purchase Amount»

.  The Purchase Amount may only be adjusted if a Change Order has been executed by the parties in accordance with ARTICLE XI due to a change in Purchase Amount due to:

##### Change in Law requiring changes to the Equipment or Scope of Work which have been approved by Purchaser pursuant to Section 3.8.1(iv);

##### suspension pursuant to Section 5.5;

##### material breach or default of Agreement by Purchaser or Seller;

##### an Event of Force Majeure in which Purchaser is the Affected Party, exceeding a duration in the aggregate of 30 Days in accordance with Section 18.9;

##### a change in scope for which an adjustment to the Purchase Amount is expressly provided in this Agreement; and

##### Transportation and costs associated therewith to the Optional Delivery Point.

Seller’s entitlement to an increase in the Purchase Amount shall be conditional upon:

###### its having used reasonable endeavors to mitigate the cost increase (except for Purchaser’s exercise of options or Purchaser instructing Seller in its performance of any option, then compliance would not be considered a breach of this provision);

###### its having given proper and timely Notice in accordance with the terms of this Agreement; and

###### the cost increase not being attributable to its default.

## Cancellation.

### Cancellation by Purchaser»

.  Purchaser may cancel this Agreement at any time in whole or in part, without cause and for its own convenience, upon written Notice to Seller.  If Purchaser cancels this Agreement under this Section 5.4.1, then Purchaser shall pay Seller the Cancellation Charge applicable to the canceled Units in accordance with Exhibit I within thirty (30) Days after the effective date of such cancellation.  If Purchaser cancels this Agreement pursuant to this Section 5.4.1, Seller shall retain title to the Equipment unless title has passed to Purchaser pursuant to ARTICLE XV.

In the event that Purchaser cancels this Agreement in part, the portion of the Purchase Amount attributable to the affected Unit will be adjusted by Change Order.  In the event that Purchaser cancels this Agreement in whole, then upon payment in full of the Cancellation Charge applicable to the canceled Units as provided in the preceding paragraph and the payment in full of the portion of the Purchase Amount due and payable, the Purchaser shall be irrevocably released and forever discharged from any obligations under this Agreement.

### Marketing Agreement»

.  In the event that the project for which one or more Unit is destined is canceled and Purchaser decides to have Seller complete the affected Unit(s), at Purchaser’s request, Purchaser and Seller shall enter into an agreement in which the parties will cooperate to sell the Unit(s) to which Purchaser has taken title.

## Suspension or Change of Delivery.

### »

Purchaser shall be entitled to suspend delivery to the Delivery Point and make such changes to the Delivery Point as it may deem necessary in accordance with Section 5.5.2.

### »

If Purchaser instructs Seller to suspend delivery by written Notice, such Notice to be no later than forty-five (45) Days prior to the Guaranteed Unit Delivery Date of a Unit and the Major Components thereof, and the Equipment or any part of the Equipment cannot be shipped to the Delivery Point in accordance with the Agreement when ready, due to any cause not attributable to Seller, Seller shall ship such Equipment to storage.  If such Equipment is directed by Purchaser to be placed in storage, including storage at the facility where manufactured, the following conditions shall apply: (1) Seller’s delivery obligation shall be deemed fulfilled upon delivery to storage, and title shall thereupon pass to Purchaser if it had not already passed; (2) any amounts otherwise payable to Seller upon delivery shall be payable upon presentation of Seller’s invoices pursuant to Section 6.1.1; (3) all expenses incurred by Seller, such as preparation for and placement into storage, handling, inspection, preservation, insurance, storage, removal charges and any taxes (anything to the contrary in the Agreement notwithstanding), shall be added by Change Order in accordance with Exhibit N-2;  and (4) if the Unit is placed in storage other than at its final use point, when conditions permit, Seller shall arrange on behalf of Purchaser and at Purchaser’s expense for any additional or incremental costs of shipment of the Equipment not then included in Seller’s Scope of Work.  In the event, as a result of direction by Purchaser, to store the Equipment in lieu of shipping to the Delivery Point and to retain care and custody, Seller will also retain risk of damage and loss until delivery to the Delivery Point or Optional Delivery Point.

# PAYMENT TERMS

## Payment of Purchase Amount.

### Payment Periods»

.  Payments shall be due and payable by Purchaser to Seller on the dates contained in Section 6.1.2 (the “Payment Date”); provided that Purchaser has received a properly prepared invoice and any other documentation supporting said payments thirty (30) Days prior to the Payment Date.

### Payment Schedule.

| Payment Date | Payment Amount |
| --- | --- |
| May 15, 2001 | $16,886,400 |
| July 30, 2001 | $16,886,400 |
| August 15, 2001 | $17,013,100 |
| TOTAL | $50,785,900 |

The final payment is also subject to Section 6.1.3.

### Retention Letter(s) of Credit»

. Purchaser shall retain the last seven hundred five thousand and two hundred dollars ($705,200) (the “Retention Amount”) for each Unit acquired pursuant to this Agreement until the expiry of the Primary Warranty Period of such Unit; provided, however, Purchaser shall pay Seller the Retention Amount as earned when:

###### Seller satisfies the requirements set forth in Section 6.6; and

###### Seller provides the Retention Letter(s) of Credit in the amount of the product of (A) the number of Units acquired pursuant to this Agreement and (B) seven hundred five thousand and two hundred dollars ($705,200).

Seller shall present as the “Retention Letter(s) of Credit” an irrevocable on demand retention letter of credit for the full amount of the Retention Amount in a form generally in accordance with the sample set forth in Exhibit D from a U.S. bank located in Houston, Texas  acceptable to Purchaser.  The parties agree that, upon the expiry of the Primary Warranty Period of each Unit, the amount of the Retention Letter(s) of Credit shall reduce incrementally by the Retention Amount attributable to that Unit.

## Payment Disputes»

.  Payment of any invoices or portions of invoices shall not prejudice the right of Purchaser to protest or question the correctness thereof or Seller’s compliance with the terms of this Agreement or any portion thereof or prejudice or constitute a waiver of any right of Purchaser hereunder.  Any amount questioned by either party and found to be in such party’s favor shall be refunded or paid, as appropriate. In the event an amount is withheld because of a dispute, and it is subsequently determined that the disputed amount or a portion of the disputed amount was due and payable, interest shall accrue at the Interest Rate commencing on the date the payment would have been payable if the dispute had not occurred.  Seller’s acceptance of partial payment of the Purchase Amount shall not be deemed to constitute a waiver of the right to receive amounts which are then in dispute, and Seller and Purchaser shall use their best efforts to resolve all disputed amounts as soon as practicable. Any undisputed amounts not paid when due shall bear interest at the Interest Rate.

## Payments Withheld or Offset.

### Payments Withheld»

.  Purchaser may, following Notice to Seller of its intent to withhold, and Seller not having eliminated the basis for the withholding within thirty (30) Days of Purchaser’s Notice, withhold payment on an invoice or a portion thereof in an amount and to such extent as may be reasonably necessary, subject to the dispute resolution provisions of ARTICLE XXVI, to protect Purchaser from loss because of:

##### defective work or Equipment not remedied pursuant to Section 9.5 or the warranty provisions of ARTICLE XIV;

##### third party suits, stop notices or liens for which Seller is liable under this Agreement, whether directly or pursuant to any indemnification obligation hereunder, (other than those provided for by insurance, bonds or other security) made on or filed with Purchaser or with respect to the Site or the Facility and not cleared by Seller by payment, deposit or otherwise to the reasonable satisfaction of Purchaser within ten (10) Days after receipt by Seller of written Notice from Purchaser requesting such action;

##### uninsured damage to Purchaser which results solely from Seller’s failure to obtain or maintain the insurance required by the provisions of ARTICLE XIX or from any action or inaction by Seller or any Vendor which excuses any insurer from liability for any loss or claim otherwise covered by insurance.

In the event a payment is improperly withheld or not paid when due and payable, such payment amounts due and payable shall accrue interest at the Interest Rate commencing on the date that payment would have been payable had the withholding not occurred.

### Offset for Liquidated Damages»

.  Purchaser shall have the right to offset from  any payments due to Seller any amounts due to Purchaser from Seller, including, but not limited to, the amount of any Liquidated Damages due from Seller.  In the event the Liquidated Damages exceed the payment amount, Purchaser shall retain the payment amount and invoice the excess amount of Liquidated Damages in accordance with Section 6.4.  In the event Purchaser offsets a Liquidated Damage which Seller disputes and it is subsequently determined that amount or a portion of the disputed amount should not have been offset, interest on the portion of the offset that should not have been offset shall accrue at the Interest Rate commencing on the date the payment that was offset would have been payable if the amount had not been offset.

## Payment of Liquidated Damages.

### Payment of O&M Instruction Liquidated Damages»

. Purchaser may upon the fifth (5th) Day of each month, invoice Seller for any O&M Instruction Liquidated Damages that accrued during the preceding month.  To the extent Purchaser has not declared that it has offset such O&M Instruction Liquidated Damages Seller shall pay such invoiced amount within thirty (30) Days of receipt of Purchaser’s invoice.

### Payment of Delivery Liquidated Damages»

.  Purchaser may upon the fifth (5th) Day of each month, invoice Seller for any Delivery Liquidated Damages that accrued during the preceding month.  To the extent Purchaser has not declared that it has offset such Delivery Liquidated Damages Seller shall pay such invoiced amount within thirty (30) Days of receipt of Purchaser’s invoice.

### Payment of Take Over Liquidated Damages»

.  Purchaser may upon the fifth (5th) Day of each month invoice Seller for any Take Over Liquidated Damages that accrued during the preceding month.  To the extent Purchaser has not declared that it has offset such Take Over Liquidated Damages Seller shall pay such invoiced amount within thirty (30) Days of receipt of Purchaser’s invoice.

### Payment of Performance Liquidated Damages»

.  Performance Liquidated Damages, if any, shall be calculated in accordance with Sections 10.9 and 10.9.2 and set out in the Units’ Performance Test Completion Certificate as prepared by Purchaser after completion of the Performance Test demonstrating that the Units have not met the Guaranteed Levels.  Purchaser may invoice Seller for Performance Liquidated Damages upon completion of the Performance Test on each Unit.   Purchaser may invoice for Performance Liquidated Damages regardless of whether or not Seller has achieved the Specific Performance Levels that correspond with the Guaranteed Levels.  In the event that the Performance Test which is the basis for the Performance Liquidated Damages occurred after Takeover, the effective date of delivery of the invoice shall be the date of delivery of the invoice to Seller.  Payment of the Performance Liquidated Damages shall be due within thirty (30) Days of the effective date of delivery of the invoice.

## Payment for Changes»

.  Unless a specific Change Order specifies otherwise, the net increase or decrease in the Unit price shall be reflected in the revised Purchase Amount.  Following the execution of an approved Change Order, Seller shall include in its next  invoice that percentage of the change which corresponds to the accumulated Payment Schedule percentages due as of the invoicing date. The remaining balance attributable to the change shall be paid in accordance with the Payment Schedule as a part of the revised Purchase Amount.

## Lien Release»

.  Seller represents that all amounts reflected on invoices submitted by Seller for payment are accurate, just, due and owing under the terms of this Agreement.  Purchaser shall not be required to make a payment under the Payment Schedule unless such invoice is accompanied with its affirmation warranting that all services, equipment, materials and information for which Seller seeks payment are free and clear of liens, claims, security interests and encumbrances arising in favor of Seller and its Vendors, and other persons or entities able to make a claim by reason of having provided labor, materials or equipment relating to performance of this Agreement or any portion thereof.  Seller agrees and represents that in submitting an invoice, Seller waives and releases all liens, claims, security interests and other encumbrances arising in favor of Seller by reason of having provided labor, materials or equipment relating to performance of this Agreement or any portion thereof, to the extent of such invoice.  In the case of payment of the Retention Amount, Seller shall not be entitled to payment of such Retention Amount unless and until Seller submits to Purchaser:

###### an affidavit in the form set forth in Exhibit S; and

###### a release and waiver of liens, claims, security interests and encumbrances for payment for labor, material and services arising out of the Scope of Work for Seller.

## Invoices.

### Agreement Reference»

.  Each invoice will reference Agreement 24-LM6K-2-99, 24LM6000 T-G –LV.

### Payee and Address for Invoices»

.  Invoices will be made out as payable by and mailed or hand carried to:

E-Next Generation LLC

c/o Las Vegas Cogeneration II, L.L.C.

3WTC0306

121 SW Salmon Street

Portland, Oregon  79204

Fax 503-464-3740

Attn:  Jody Blackburn

Purchaser anticipates that the mailing address of the invoice may change, and agrees to notify Seller of such change prior to the change.

### Date of Receipt»

.  Date of receipt of invoice by Purchaser will be evidenced by date stamp, or other generally accepted date receipting system.

## Method of Payment»

.  Payment will be made by electronic wire transfer, unless otherwise requested by Seller, to a United States bank within the United States.  Seller’s invoices must provide all necessary information (including Tax I.D. and account number) to enable Purchaser to effect such payment.

## Payments Not Acceptance of Work»

.  No payment made by Purchaser hereunder shall be considered or deemed to represent that Purchaser has inspected the work or Equipment or checked the quality or quantity thereof or that Purchaser knows or has ascertained how or for what purpose Seller has used sums previously paid, and shall not be deemed or construed as an approval or acceptance of any work or Equipment or Seller’s compliance with any other of its obligations under this Agreement or as a waiver of any claim or right Purchaser may have hereunder.

# COMMENCEMENT OF THE WORK AND TERMINATION

## Not Used.

## Not Used.

### Not Used.

### Not Used.

### Not Used.

### Not Used.

### »

## Termination»

.  This Agreement shall terminate upon the earlier of:

###### the cancellation by Purchaser of all the Scope of Work under Section 5.4; or

###### termination of this Agreement due to an event of default by Seller or Purchaser under ARTICLE XVII; or

###### when all obligations of the Parties under this Agreement are complete;

provided, however, that the rights and obligations of the parties under ARTICLE XVII (Default), ARTICLE XX (Indemnification), ARTICLE XXI (Non-Disclosure of Information), Section 30.2 (Governing Law), ARTICLE XXVI (Arbitration), ARTICLE XXVII (Limitation of Liability) and the indemnities set forth in the Agreement shall survive termination of the Agreement; except that, if termination occurs under (i) or (ii) above, obligations under ARTICLE XIV (Warranties) shall also survive.

# NOT USED

# INSPECTION AND CORRECTION OF WORK

## Inspections»

.  Seller shall provide Purchaser and Lender, or their designated representatives, access to the Scope of Work at all reasonable times wherever in preparation or progress and shall work closely with Purchaser in performing this Agreement.  Purchaser, or its designated representative, shall have the right  from time to time during this Agreement to observe, inspect, examine and review, Seller’s performance of this Agreement.  Purchaser’s rights to inspect under this Section 9.1 shall include but not be limited to manufacturing schedules; compliance with Specification; workmanship; dimensional tolerances; production tests; production inspections; assembly of components; panel inspection and testing; or witnessing testing of Equipment at any stage of design, procurement, production, or manufacture at  Seller’s works or those of its Vendors to verify that the Equipment conforms to the specified requirements of this Agreement. However, any observance, inspection or review of performance of this Agreement shall not constitute or be deemed to be actual control or a right to control Seller, its employees, agents, personnel, Affiliates, or Vendors.  Purchaser’s inspection of any part of the Equipment shall in no way affect Seller’s obligation to perform the Scope of Work in accordance with the Specification and all other terms of this Agreement, and any audit, examination, inspection, review, or testing by Purchaser shall not constitute acceptance or prejudice, be a waiver, or be deemed to be a waiver of any of Purchaser’s rights hereunder or of its rights to reject defective performance of this Agreement or release Seller from any obligation under this Agreement.  Seller shall not be required to provide Purchaser access to areas where Seller is performing proprietary work unless a portion of the Scope of Work is being performed in such an area.  In such event Seller may take measures as it deems appropriate to isolate other ongoing proprietary work from Purchaser’s view, or if not practical, Purchaser agrees to enter into a mutually agreeable confidentiality agreement pertaining to such proprietary work.

## Resident Facilities»

.  If reasonably requested by Purchaser, Seller will provide facilities as reasonably available for a resident quality representative in Seller’s works and those of its Vendors who are manufacturing Major Components.

## Quality Plan»

.  Seller shall maintain a quality plan compliant with ISO 9001, 1994 and with the quality assurance plan set forth in Exhibit J, detailing:

###### specific authorities and responsibilities;

###### procedures, methods and work instructions; and

###### inspection and test plans.

In the event of a conflict between Exhibit J, ISO 9001, 1994 and Seller’s quality system, the order of precedence shall be, ISO 9001, 1994, Seller’s quality system and Exhibit J.

## Notice»

.   The agreed schedule of witness test points is set forth in Exhibit R, excluding those that have transpired on Units currently being manufactured and which test and inspection results have been provided to Purchaser.  Seller shall provide Purchaser with a Notice of the date of a witness test point not less than fourteen (14) Days prior to such date.

## Correction of Equipment»

.  Prior to Acceptance of each Unit, Seller shall, at its sole cost and expense and with exception of defects included in the Punchlist applicable to the Unit, promptly correct any part of the Equipment which is defective or not in accordance with this Agreement, regardless of the stage of its completion or the time or place of discovery of such defects  and regardless of whether Purchaser has previously paid for or accepted such part of the Equipment through oversight or otherwise. Seller shall replace or correct such defective work or condition such that the Equipment is in accordance with this Agreement, including the Specification.  Seller may repair (making an item functional, but not necessarily conforming the work to its original specification) the Equipment or a portion of the Equipment only with Purchaser’s prior written consent.  Seller agrees to complete the Punchlist to the satisfaction of Purchaser.  In the event Seller does not complete such Punchlist either (i) to the standards of the Agreement, or  (ii) within a reasonable period of time, but not later than one hundred eighty (180) Days after Takeover, Purchaser may, after prior written Notice to Seller, draw down against the Retention Letter of Credit the estimated value of the uncompleted work in order to have such work completed by others or invoice Seller for any deficiency.

## Additional Factory Testing»

.  Prior to delivery of Equipment at the Delivery Point, Purchaser may request Seller to repeat a test, perform the test using more precise instrumentation than planned, or conduct a test not in Seller’s standard factory test program. If commercially reasonable, Seller shall accommodate that request. In the event as a result of such Purchaser requested test requirement the Equipment is found to not be compliant with the requirements of this Agreement, Seller shall correct such noncompliance and the cost and time associated with such Purchaser test requirement shall be to Seller’s account.  If the Equipment is found to be compliant with this Agreement, Seller shall be eligible for a Change Order arising out of such Purchaser test requirement. If Seller is unable to accommodate Purchaser’s request under this section, and the Equipment is later found to be not compliant with this Agreement, any time spent by TD of I personnel in diagnosing or remedying the problem shall not be counted against Purchaser’s  TD of I hours.

## Release for Delivery»

.  In addition to other conditions set forth in this Agreement, prior to Seller performing any Major Component packing and prior to actual shipment, Seller shall provide, seven (7) Days in advance, Notice of such packing and request in writing to Purchaser’s Quality Assurance Manager for release to ship such Major Components.  Purchaser’s approval shall not be unreasonably withheld provided Seller has met the requirements of this Agreement.  In the event Purchaser fails to respond to Seller’s Notice of intent to pack and ship the Major Component within seven (7) Days, Seller  will proceed to perform packing and will complete staging at Seller’s facility pursuant to the Notice.

# DELIVERY AND PERFORMANCE

## Delivery of Documentation.

### Purchaser Review of Documents»

.  Seller shall provide the documentation described in this Agreement for Purchaser’s review and comment.  Purchaser’s review of such documentation shall be governed by Exhibit B-5.  The parties shall comply with the following in connection with the submittal, review and revision of all such documentation:

##### Upon delivery of each item of documentation Purchaser shall diligently review the document and provide Seller the applicable status code and comments within ten (10) business days of receipt;

##### Upon receipt of any comments from Purchaser, Seller shall diligently correct and resubmit such returned documentation within ten (10) business days; and

##### If Purchaser does not provide comments within ten (10) business day period after receipt, the document shall be deemed to be assigned a Status 1.

Purchasers review of any drawing or documents hereunder shall not be construed as constituting approval of Seller’s work, nor shall Purchaser’s failure to review or failure to comment be construed as approval or disapproval.  Seller at all times shall retain responsibility for a Scope of Work that meets the requirements of this Agreement, regardless of whether or not Purchaser has reviewed Seller’s drawings or documents.  Changes to the documentation for the convenience of Purchaser, which can be accommodated by Seller shall be adopted pursuant to ARTICLE XI of the Agreement.

### Delivery of Final O & M Instructions»

.  Seller shall provide the final operations and maintenance instruction manuals (the “O&M Manuals”) within forty-five (45) Days after the Site Delivery Date for the first Unit.  In the event Seller delivers such instructions later than forty-five (45) Days after the Site Delivery Date, Seller agrees that Liquidated Damages shall accrue at the rate of five hundred dollars ($500.00) for each Day of lateness (the “O & M Instruction Liquidated Damages”), not to exceed fifty (50) Days.  Purchaser may draw down the O & M Instructions Liquidated Damages from the Retention Letter of Credit upon the earlier of (i) delivery of completed final O&M Manuals, or (ii) fifty (50) Days of lateness in delivering the final O&M Manuals has accrued.  Installation and commissioning instructions will be provided by Seller’s TD of I representative at the Site to support installation, start-up and commissioning.

## Delivery of Equipment.

### Guaranteed Unit Delivery Dates»

.  Seller shall deliver the Units to the Delivery Point by no later than the dates listed below (the “Guaranteed Unit Delivery Dates”):

| Item: | Guaranteed Unit Delivery Date: |
| --- | --- |
| Unit 19 turbine SN 310889 | July 30, 2001 |
| Unit 20 turbine SN 310890 | July 30, 2001 |
| Unit 23 turbine SN 309994 | July 30, 2001 |
| Unit 24 turbine SN 310891 | August 15, 2001 |

The delivery dates set forth herein shall be referred to as the “Guaranteed Unit Delivery Date” for each respective Unit.

#### Delivery Restrictions»

.  Seller shall use its reasonable efforts to deliver the Units up to thirty (30) Days earlier than the times set forth in Section 10.2.1, provided that Purchaser has delivered a written Notice to Seller at least forty-five (45) Days prior to the Guaranteed Unit Delivery Date and Seller shall provide written Notice to Purchaser a minimum of fourteen (14) Days before early delivery.

### Inventory Upon Delivery»

.  Seller shall be required, and Purchaser shall have the right, to inspect the Equipment for completeness, condition and packing upon delivery to the Delivery Point and Seller shall immediately inform Purchaser of any damage discovered.

### Delivery»

.  Purchaser shall have the right to inspect the Equipment for completeness, condition and packing prior to loading on Seller’s or Purchaser’s  transport at the Delivery Point for the purposes of determining whether delivery of the Unit has occurred prior to the Guaranteed Unit Delivery Date.  Purchaser reserves the right to reject damaged Equipment.  In the event the Equipment is damaged or defective, Purchaser after making an initial assessment of the damage and consulting with Seller as to how such damage or defect will affect the installation, operation, performance, reliability, efficiency, and warranty of the damaged Equipment may either (i) reasonably determine that such damage or defect is such that the preceding criteria is so adversely affected that Purchaser cannot accept delivery of the damaged Equipment and declare that delivery has not occurred (in which case delivery for the purposes of assessing Delivery Liquidated Damages pursuant to Section 10.3.1 shall not have occurred), or (ii) after taking into account such criteria and Seller’s proposed plan for correcting such damage or defect in accordance with Section 9.5, declare that delivery has occurred.  In the event Purchaser discovers such a damage or defect, it shall immediately notify Seller of such damage.

#### Optional Delivery Point.  In the event Purchaser elects by Change Order  to have one or more Units delivered to the Site (the “Optional Delivery Point”), Seller shall deliver such Unit(s) on an expedited basis to Purchaser’s designated laydown area at the Site as soon as possible after the Unit is made available to ship at Seller’s facility.  Both parties shall inspect the Equipment for completeness and condition upon delivery to the Optional Delivery Point to determine if all of the Unit’s components have been delivered and if any Equipment has been lost or damaged. In the event any portion of the Equipment is not received or is found to be damaged or defective upon inspection at the Optional Delivery Point, Purchaser and Seller shall assess the damage, file appropriate insurance documents and Seller shall present Purchaser its plan for either (i) repairing the damage at the Site or (ii) replacing and delivering the missing, damaged or defective Equipment in accordance with this Agreement.  Seller shall repair such item in lieu of replacement with Purchaser’s prior approval which shall not be unreasonably withheld by Purchaser.

### Extensions of the Guaranteed Unit Delivery Date.

#### A Guaranteed Unit Delivery Date may only be extended if a Change Order has been executed by the parties in accordance with ARTICLE XI due to a delay caused by:

##### an Event of Force Majeure which justifies an extension under the terms of this Agreement;

##### a material breach of the Agreement or default (as defined in Section 17.5) thereunder by Purchaser; or

##### a Change in Law requiring changes to the Equipment as provided in Section 3.8.1(iv);

#### Seller’s entitlement to an extension of time shall be conditional upon:

##### its having used reasonable endeavors to mitigate the delay;

##### its having given proper and timely Notice in accordance with the terms of this Agreement; and

##### the delay not being attributable to Seller’s default.

### Loading Responsibilities at Delivery Point»

.  Seller shall provide written Notice of readiness to ship at least two weeks in advance of the expected date when the Equipment (or portions thereof) will be ready for shipment, specifying the date the Equipment will be ready to ship.  Seller shall be responsible for promptly loading the Equipment at the Delivery Point within forty-eight (48) hours of arrival of Purchaser’s transportation carrier at the Delivery Point.  Seller shall reimburse Purchaser all demurrage charges caused by its failure of its obligations under this section except to the extent that such failure is attributable to Purchaser’s acts or omissions.

### OffLoading Responsibilities at Optional Delivery Point»

.  Purchaser shall be responsible for promptly offloading the Equipment at the Optional Delivery Point from Seller’s mode of transportation within forty-eight (48) hours after arrival of Seller’s transportation carrier at the Optional Delivery Point.   Purchaser shall reimburse Seller all demurrage charges caused by its failure of this obligation except to the extent that such failure is attributable to Seller’s acts or omissions.

### Unit(s) Storage»

.  Seller agrees to provide ninety (90) Days of storage of each Unit without charge to Purchaser.  Seller shall assess storage charges ninety (90) Days after the later of the Guaranteed Unit Delivery Date or the date the Unit is delivered ex-works at the rates set forth in Exhibit N-2.  Seller shall retain all risk of loss and damage for Units while in its storage facility.

## Delivery Liquidated Damages.

### Unit Delivery Liquidated Damages»

.  For each Day that Seller delivers a Unit as defined in Section 10.2.3 to the Delivery Point  after its respective Guaranteed Unit Delivery Date, Purchaser may assess and Seller shall pay to Purchaser Delivery Liquidated Damages at the following rates per Day per Unit (the “Delivery Liquidated Damages”) for such lateness:

# Days Late			$/Day/Unit

1  - 15				$10,000.00

16 +				$25,000.00

For the avoidance of doubt, no Delivery Liquidated Damages shall be assessable as a result of Seller delivering an item of Equipment which is not a Major Component of the applicable Unit after such Unit’s Guaranteed Unit Delivery Date, unless such non-Major Component is shown by Purchaser to impede the continuous progress of installation of the Unit.  The Delivery Liquidated Damages rate assessable due to the late non-Major Component shall commence on the date(s) impedance first occurs and continues to occur, against the respective Delivery Liquidated Damages assessable on such date(s) after the applicable Guaranteed Unit Delivery Date.    All Delivery Liquidated Damages shall begin to accrue at 12:01 a.m. on the day following the Guaranteed Unit Delivery Dates.

For purposes of clarity, the following example is provided:

| Example 1 | - All Major Components of Unit 1 are on time |
| --- | --- |
| Situation: | - one or more non-Major Component of Unit 1 is 25 Days late and the first impedance occurs at Day 20 and lasts until delivery |
| LD Calculation: | 5 Days x $10,000/Day = $50,000 TOTAL: $50,000 |

| Example 2 |  |
| --- | --- |
| Situation: | - A Major Component of Unit 1 is 20 Days late - non-Major Component of Unit 1 is 25 Days late and causes an impedance commencing on Day 10 which lasts until Day 25 (15 Days) |
| LD Calculation: | - Major Component Delivery Liquidated Damages 15 Days x $10,000/Day = $150,000 5 Days x $25,000/Day = $125,000 |
|  | For Day 10 to 20 there are no additional Delivery Liquidated Damages assessable due to the late delivery of the non-Major Component since the Unit is considered not delivered because a Major Component has not been delivered and Delivery Liquidated Damages are assessed on that basis. |
|  | For Day 21 through Day 25 there are 5 Days of Delivery Liquidated Damages assessable associated with the lateness of the non-Major Component. |
|  | 5 Days x $25,000 = $125,000 TOTAL: $400,000 |

### Take Over Liquidated Damages»

.  Purchaser at its sole discretion may assess and Seller agrees to pay Liquidated Damages (the “Take Over Liquidated Damages”) at the rate of twenty-five thousand dollars ($25,000.00) per Day per Unit for each Day that the Unit fails to meet the Take Over Criteria by the end of the Time for Completion.

Assessment of such Take Over Liquidated Damages shall be subject to the following conditions:

##### Purchaser elects at its sole discretion not to Takeover a Unit which fails to meet its Specific Performance Levels or operate reliably;

##### During the Commissioning Period, Purchaser makes reasonable efforts to provide the necessary time and operating loads for Seller and Purchaser to commission and check out the Units.  Seller’s time and load requirement shall not be to the exclusion of the needs of other Facility equipment being commissioned.  Purchaser shall coordinate the most advantageous utilization of time and assets whenever conflicting requirement exist and such situations shall not be deemed delay by Purchaser;

##### Subject to (d) below, Purchaser may not assess Take Over Liquidated Damages prior to the expiry of the Commissioning Period;

##### In the event Seller fails to have a number of qualified TD of I personnel on Site in accordance with the requirements of Exhibit H-1 or to use its reasonable efforts to minimize time to make corrections, adjustments or repairs to the deficiently performing Unit(s) during the Commissioning Period, Purchaser shall have the right to void the Commissioning Period and assess Take Over Liquidated Damages without regard for the period afforded by the Commissioning Period;

##### Purchaser provides prompt oral Notice of delays affecting commissioning which is followed up in writing within seventy-two (72) hours of such Notice; and

##### Purchaser provides Seller its commissioning schedule no less than forty-five (45) Days prior to commencement of commissioning on the first Unit and provides periodic updates thereto.

#### In the event a Unit fails to meet its Emissions Guarantee or a Sound Level Guarantee (whether Purchaser elects to Takeover or not), without limiting Seller’s obligations hereunder and at Purchaser’s option, Seller shall use reasonable efforts to obtain, or assist Purchaser in obtaining, a permit variance or modification which will enable the Facility to operate at the electrical output demonstrated during the Performance Test at such higher sound or emissions levels.

In the event that one or more Units fail to meet the Emissions Guarantee or Sound Level Guarantee, in parallel with Seller’s efforts to remedy such failure, Purchaser and Seller agree to pursue alternate remedies including, at the Seller’s expense, improving or modifying other Facility components in order to mitigate the effects of such Unit(s) on the Facility’s performance.  Such alternate remedies must be mutually agreed to by Seller and Purchaser.

### Invoicing for Delivery and Take Over Liquidated Damages»

.  Except to the extent of an offset in accordance with Section 6.3, invoicing for and payment of O&M Instruction, Delivery and Take Over Liquidated Damages shall be in accordance with Section 6.4.

## Specific Performance Exhaust Gas Temperature and Energy Guarantees.

### Not Used.

### Specific Performance Exhaust Gas Temperature Guarantee For Combined Cycle Application of Units»

.  As a Specific Performance obligation, in the event the Facility is a combined cycle plant, Seller guarantees that the Adjusted Exhaust Gas Temperature of each Unit, as measured during the most recent Performance Test, shall not be less than 811 degrees Fahrenheit (ºF) (the “Specific Performance Exhaust Gas Temperature Guarantee”). Subject to the provisions of Section 10.12.8, if the Adjusted Exhaust Gas Temperature of a Unit is greater than or equal to the Specific Performance Exhaust Gas Temperature Guarantee, Seller will be considered to have satisfactorily caused the Unit to meet the Specific Performance requirement associated with the Specific Performance Exhaust Gas Temperature Guarantee.

### Not Used.

### Specific Performance Exhaust Gas Energy Guarantee For Combined Cycle Application of Units»

.  As a Specific Performance obligation, in the event the Facility is a combined cycle plant, Seller guarantees that the Adjusted Exhaust Gas Energy of each Unit will be greater than or equal to 55,162 BTU/sec., reference 50 ºF (the “Specific Performance Exhaust Gas Energy Guarantee”).  Subject to the provisions of Section 10.12.8, if the Adjusted Exhaust Gas Energy of a Unit is greater than or equal to the Specific Performance Exhaust Gas Energy Guarantee, Seller will be considered to have satisfactorily caused the Unit to met the Specific Performance requirement associated with the Specific Performance Exhaust Gas Energy Guarantee.  The Parties agree to amend the Specific Performance Exhaust Gas Energy Guarantee to reflect changes in Basis Conditions to reflect the Site conditions for the combined cycle Facility within a reasonable time after receipt of Purchaser’s request.  Purchaser will only perform testing for compliance with the Specific Performance Exhaust Gas Energy Guarantee if a Unit when operated in combined cycle during the Performance Test fails to meet the combined cycle Facility Performance Guarantees.

### Interaction of Exhaust Gas Energy and Exhaust Gas Temperature with Turbine Net Output»

.  Exhaust heat measurement will be performed per the guidelines of ASME PTC 4.4.  The Specific Performance Exhaust Gas Energy Guarantee will be corrected to account for Adjusted Electrical Output in excess of the Specific Performance Electrical Output Guarantee.

## Sound Level Specific Performance Guarantee.

### Specific Performance Near Source Sound Level Guarantee»

.  As a Specific Performance obligation, Seller guarantees that the near field average A-weighted sound pressure levels of each Unit shall not exceed 85 dB(A) (referenced to 20 micropascals) (the “Near Source Sound Level Guarantee”) when measured during a Performance Test or Sound Level Test in accordance with the Sound Level Test Procedures at one and a half (1.5) meters above any working elevation and one (1) meter from the surface.

The Near Source Sound Level Guarantee is limited to normal continuous sound sources within the Scope of Work.

### Specific Performance Far Field Sound Level Guarantee»

.  As a Specific Performance obligation, Seller guarantees that the far field average A-weighted sound pressure level of one (1) Unit as installed with Seller provided auxiliary equipment (referenced to 20 micropascals) shall not exceed a contribution of 65 dB(A) proposed for a gas fueled and water injected Unit at 400 feet  (the “Far Field Sound Level Guarantee”) when measured during a Performance Test or Sound Level Test while operating at steady state loads from 50 to 100 percent in accordance with the Sound Level Test Procedure.

The Far Field Sound Level Guarantee is limited to normal continuous sound sources at Base Load within the Scope of Work.

### Not Used.

### Sound Level Test»

.  Purchaser may conduct tests at the Site to measure the Sound Levels generated by the Equipment in accordance with the procedures set out in Exhibit F-1 (the “Sound Level Test”).

###### Purchaser will (a) provide or cause to be provided, all instrumentation (including special test instrumentation), operations, labor, consumables required for the Sound Level Test (b) provide sufficient load during the Sound Level Test (c) read and record the Sound Level Test data, and (d) calculate the Sound Level Test results, all at no cost to Seller.

###### Seller (a) has the right of representation at the Sound Level Test (b) has the right to take its own data (c) will have access to all data resulting from the Sound Level Test, and (d) may verify the calculated Sound Level Test results.

## Specific Performance Exhaust Emissions Guarantee»

.  As a Specific Performance obligation, Seller guarantees that the Adjusted Emissions of a Unit when operated at Base Load at Basis Conditions (the “Emissions Guarantee”) will not be greater than the following values:

| Category | Value | Units of Measure |
| --- | --- | --- |
| Nox | 30 | ppmvd @ 15% O2 |
| CO | 38 | ppmvd @ 15% O2 |
| VOCs | 10 | ppmvd @ 15% O2 |
| PM10 | 4.5 | lb/hr (front and back half) |

NOx and PM10 emissions guarantees are valid for a load range of 30-100% of Base Load, a compressor temperature (CIT) range of -18F through 110F and a relative humidity range of 0-100% (except the CIT range does not include those coincident ambient temperature/humidity conditions in which the ambient air must be heated to prevent inlet frosting).  CO and VOC emissions are valid for a load range of 60-100% at Basis Conditions.  Where Facility conditions warrant, a CO and VOC emissions guarantee will be provided for load below 60% and for a range of compressor inlet temperature and relative humidity other than the Basis Conditions.

In no case shall the CO emission from any individual Unit (regardless of the number of Units at the Facility) exceed 56 ppmvd @ 15% O2 at loads of 60-100% of Base Load at Basis Conditions.  Subject to the provisions of Section 10.12.8 if the Adjusted Emissions of a Unit are less than Emissions Guarantee values, Seller will be considered to have satisfactorily caused the Unit to have met the Specific Performance requirement associated with the Emission Guarantee.  The above NOx and CO guarantees must include ambient contribution for NOx and CO.

## Electrical Output Guarantees.

### Electrical Output Guarantee»

.  Seller guarantees that the Adjusted Electrical Output of each Unit, as demonstrated during the most recent Performance Test, shall be equal to or greater than 43,994 kW (net of Unit auxiliary loads as listed in Exhibit F) (the “Electrical Output Guarantee”).

### Specific Performance Electrical Output Guarantee»

.  As a Specific Performance obligation, Seller guarantees that the Adjusted Electrical Output of each Unit, as demonstrated during the most recent Performance Test, shall be equal to or greater than 42,234 kW (net of Unit auxiliary loads as listed in Exhibit F)  (the “Specific Performance Electrical Output Guarantee”).

## Heat Rate Guarantees.

### Heat Rate Guarantee»

.  Seller guarantees that the Adjusted Heat Rate of each Unit, as demonstrated during the most recent Performance Test, shall not exceed 8,969 BTU/kWh (LHV) (the “Heat Rate Guarantee”).

### Not Used.

### Specific Performance Heat Rate Guarantee»

. As a Specific Performance obligation Seller guarantees that the Adjusted Heat Rate of each Unit, as demonstrated during the most recent Performance Test, shall not be more than 9,392 BTU/kWh (LHV) (the “Specific Performance Heat Rate Guarantee”).

### Specific Performance Guarantee»

. In the case of a dual fuel engine, specific performance guarantees shall also be provided for Electrical Output, Heat Rate and Emissions for liquid fuel operation.  The emissions guarantees will include all categories of emittants are contained in Section 10.6 and SO2 based on the Facility liquid fuel specification.

## Performance Liquidated Damages»

.

### Unit Output Liquidated Damages»

. In the event that a Unit fails to achieve the Electric Output Guarantee, Liquidated Damages shall be assessed by Purchaser, and Seller agrees to pay at the rate of five hundred dollars ($500.00) for each kW that the Adjusted Electrical Output of a Unit (as measured during the most recent Performance Test) is less than the Electrical Output Guarantee (the “Unit Output Liquidated Damages”).

Seller recognizes the Units in the Facility will become ready for testing sequentially, and therefore agrees that Purchaser will conduct Performance Tests on each Unit at such time as Seller is confident that the Unit(s) can be successfully tested, but not later than the end of the Commissioning Period.  Seller further agrees to pay the Unit Output Liquidated Damages attributable to the Shortfall of each individual Unit upon completion of the Performance Test on the last tested Unit at the Facility.  If Purchaser expressly elects in writing not to test a Unit(s) in a multiple Unit Facility for reasons not attributable to Seller, the untested Unit(s) will be deemed to have made its Performance Guarantees.

### Heat Rate Liquidated Damages»

. Liquidated Damages shall be assessed by Purchaser, and Seller agrees to pay, if a Performance Test has been conducted on a Unit, at the rate of three thousand five hundred dollars ($3,500) for each BTU/kWh (LHV) that the Adjusted Heat Rate of the  Unit (as measured during the most recent Performance Test) exceeds the Heat Rate Guarantee (the “Heat Rate Liquidated Damages”).

Seller recognizes the Units will become ready for testing sequentially, and therefore agrees that Purchaser will conduct a Performance Test on each Unit at such time as Seller is confident that the Unit can be successfully tested, but not later than the end of the Commissioning Period.  Seller further agrees to pay Unit Output Liquidated Damages and Heat Rate Liquidated Damages attributable to the Shortfall of each individual Unit upon the completion of the Performance Test.

### Most Recent Performance Test»

.  Performance Liquidated Damages shall be assessed by Purchaser, and Seller agrees to pay on the results of the most recent Performance Test, including any reperformance of the Performance Tests in accordance with Section 10.12.8, regardless of whether the performance improves or worsens upon the later Performance Test.

### Performance Test Required»

.  No Performance Liquidated Damages shall be payable if no Performance Test has been conducted.

### Setting Out of Performance Liquidated Damages»

.  Performance Liquidated Damages, if any, shall be due and payable by Seller pursuant to Section 6.4 in accordance with the rates set forth in this Section 10.9 and the calculations set forth in the Performance Test Completion Certificate prepared by Purchaser.

### Not Used»

.

### Seller’s Improvement of Performance»

.  In the event one or more of the Units fail to meet a Guaranteed Level but meet the Specific Performance Levels, Seller shall use its reasonable best efforts, for a period of not more than one hundred eighty (180) Days after the initial Performance Test is run for a Unit, to cause such Unit to meet the Guaranteed Levels.  Prior to Takeover of the Facility, Purchaser shall provide Seller a reasonable opportunity to implement such changes or improvements; however, it is understood by both parties that Purchaser will not be required to delay commencement of Commercial Operation of the Facility for the purpose of Seller making such changes or improvements.  After Purchaser places any Unit into Commercial Operation Purchaser shall provide Seller reasonable opportunity to make such corrections or improvements during scheduled and unscheduled outages.

### Reduction in Performance Liquidated Damages»

.  In the event Seller improves a Unit’s performance for which Performance Liquidated Damages are payable after Purchaser has:

###### made an offset in accordance with Section 6.3 against payments due Seller to cover Performance Liquidated Damages; and/or

###### been paid all Performance Liquidated Damages invoiced to Seller;

then Seller shall be entitled to a reduction/refund in the Performance Liquidated Damages subject to the following:

A) If:

###### the Shortfall has not prevented Purchaser from placing the Unit into Commercial Operation;

###### such corrections are made and are complete prior to Commercial Operation of the applicable Unit;  and

###### such corrections cause a reduction in the performance Shortfall;

then Purchaser shall:

###### refund to Seller an amount equal to the Performance Liquidated Damages associated with such reduction in the Shortfall; and/or

###### reduce the offset associated with such reduced Shortfall;

however, such reduction in offset or amount of refund shall not exceed the amount actually offset in accordance with Section 6.3 or paid in accordance with Section 6.4 for such Shortfall; or

B)   If:

###### such Shortfall has prevented Purchaser from placing the Unit into Commercial Operation; or

###### the corrections to reduce a Shortfall are completed after the Unit goes into Commercial Operation, and such corrections are completed within One Hundred Eighty (180) Days after the Unit went into Commercial Operation, and such corrections cause a reduction in the Shortfall;

then Purchaser shall:

###### refund to Seller an amount equal to the Performance Liquidated Damages associated with such reduction in the Shortfall; and/or

###### reduce the offset associated with such reduced Shortfall;

however, such refund of Performance Liquidated Damages or reduction of offset will not exceed the amount actually offset in accordance with Section 6.3 or paid in accordance with Section 6.4 for such Shortfall and the amount of such refund or reduction of offset shall itself be reduced by the following amounts (based on a ten (10) year lifespan and a net present value factor of seven (7)) for each Day that passes from date of the Performance Test on which the Performance Liquidated Damages were originally based upon until the date that Seller demonstrated the improved performance.

##### At a rate of $0.20/kW per Day that the total Adjusted Electrical Output Shortfall of the Unit is reduced (the “Output Liquidated Damages Refund Reduction”).

##### At a rate of $1.37/BTU/kWh per Day that the average Adjusted Heat Rate Shortfall of the Unit is reduced (the “Heat Rate Liquidated Damages Refund Reduction”).

### »

No refund of Performance Liquidated Damages shall be made if the corrections are made after one hundred eighty (180) Days after Takeover of the Facility, unless Purchaser elects to do so as a result of the corrective action plan presented by Seller prior to the expiry of such one hundred eighty (180) Day period.  In the event Seller determines the cause of a portion or all of the Shortfall prior to the expiry of the one hundred eighty (180) Day period following Takeover, but in spite of its best efforts is not able to effect the necessary corrections to the Equipment, Seller may present a correction plan that extends beyond such one hundred eighty (180) Day period.  Purchaser, at its sole discretion, may elect to permit Seller the opportunity to make such corrections.

## Maximum Liabilities for Liquidated Damages»

.

### Maximum O&M Instruction Liquidated Damages»

.  Seller’s maximum aggregate liability for O&M Instruction Liquidated Damages shall be fifty thousand dollars ($50,000.00).

### Maximum Delivery Liquidated Damages»

.  Seller’s maximum aggregate liability for Delivery Liquidated Damages shall be fifteen percent (15%) of the Maximum Liability Amount.

### Maximum Take Over Liquidated Damages»

.  Seller’s maximum liability for Take Over Liquidated Damages shall be fifteen percent (15%) of Maximum Liability Amount.

### Maximum Unit Output Liquidated Damages»

.  Seller’s maximum liability for Unit Output Liquidated Damages shall be ten percent (10%) of Maximum Liability Amount.

### Maximum Heat Rate Liquidated Damages»

.  Seller’s maximum liability for Heat Rate Liquidated Damages shall be ten percent (10%) of Maximum Liability Amount.

### Maximum Aggregate Liquidated Damages»

.  Notwithstanding Section 10.3 and Section 10.9, Seller’s maximum aggregate liability for Liquidated Damages, if any, under this Agreement shall be thirty percent (30%) of the Maximum Liability Amount.

## Liquidated Damages Not Penalty»

.  The parties acknowledge and agree that because of the unique nature of the Equipment and the time requirements for performance:

###### Purchaser shall be damaged by:

Seller failing to accomplish delivery of documents;

Seller failing to deliver the Units by the Guaranteed Unit Delivery Date;

A Unit’s performance causing Purchaser a delay in Take Over of the Unit; and/or

Seller failing to cause the Units to achieve Guaranteed Levels (the “Liquidated Damages Events”);

###### it would be impracticable or extremely difficult to fix the actual damages resulting from late delivery or failure to meet the Guaranteed Levels;

###### any sums which would be payable under this ARTICLE X are in the nature of Liquidated Damages, and not a penalty, and are fair and reasonable; and

###### such payment represents a reasonable estimate of fair compensation for the losses that may reasonably be anticipated from such Liquidated Damages Events.  Such payments are compensation solely for Liquidated Damages Events and shall not prejudice any other rights of Purchaser hereunder and shall not relieve Seller of its obligations hereunder.

## Performance Tests.

### Concurrence of Tests»

.  To the extent practical Purchaser shall conduct the Performance Tests for a Unit concurrently so as to assure itself that the Unit is capable of meeting all of the Guaranteed Levels and Specific Performance Levels concurrently.

### Election to Conduct a Performance Test»

.  Purchaser shall conduct the first series of Performance Tests prior to the expiry of the Installation Period, provided however, Purchaser at it’s sole discretion may elect to waive the conduct of the Performance Test.

### Specific Performance Achievement»

.  In the event that as a result of the performance functional checks it is reasonably evident that the Equipment is performing significantly out of compliance with a Specific Performance Level; Purchaser may require Seller to take corrective actions in accordance with Section 10.13 without the benefit of Performance Test or Sound Level Test results; otherwise, Performance Test or Sound Level Test results will be required to be the basis of such action.

### Timing of Tests.

#### Purchaser may conduct or cause a Performance Test or Sound Level Test to be conducted on the Units as soon as possible after commissioning and after Seller’s representative certifies that the Units to the best of his knowledge:

###### are properly installed;

###### can be safely tested; and

###### have been and may be run up to full load.

#### In the event that a Performance Test or Sound Level Test has been conducted on the Units within the Installation Period and corrective measures or modifications have been performed, if Purchaser elects to conduct a retest in accordance with Section 10.12.8, it shall conduct such retest within thirty (30) Days of the completion of such corrective measures or modifications.

Unit performance shall not be adjusted for degradation unless such Unit has been operated for more than three hundred (300) operating hours at the time of conduct of the initial Performance Test.  Operating hours necessary to diagnose a Unit’s failure to operate in accordance with the requirements of this Agreement shall not be added to the hour count.  Operating hours associated with the conduct of Performance Tests shall be added to the operating hour count.  Methods of correcting for degradation shall be set out in the Performance Test Procedures.

### Seller Presence at Tests»

.  Seller shall have the right to be present or to have a representative present at each Performance Test and Sound Level Test.  Purchaser shall provide Seller with a thirty (30) Days initial Notice and a five (5) Days’ confirmation Notice in advance of each Performance Test.

### Test Results»

.  Upon the completion of each Performance Test, or Sound Level Test, Purchaser will issue a Performance Test Certificate setting forth the results achieved during such test.

### Performance Test Procedures»

. No later than six (6) months after the Order Definition Meeting, Seller will submit to Purchaser a complete set of recommended procedures for the conduct of the Performance Tests and Sound Level Tests (the “Test Procedures”) and for verification of all major systems.  Purchaser shall review and respond to Seller’s recommended Test Procedures within  thirty (30) Days of the submission.  In the event the Test Procedures are not approved by Purchaser in such response, the parties shall meet to finalize the Test Procedures within thirty (30) Days of Purchaser’s response.

### Reconduct Tests»

.  In the event that Seller has made repairs (including those pursuant to ARTICLE XIV) or has taken other corrective action to correct a Shortfall subsequent to the conduct of the Performance Test or Sound Level Test, Purchaser at its sole reasonable discretion may require the conduct of another Performance Test(s) or Sound Level Test to:

###### demonstrate that such repairs or corrective actions have caused the Equipment to now meet the previously failed Specific Performance Level or Guaranteed Level which such repairs or corrective actions were intended to correct;

###### demonstrate that such repairs or corrective actions have not caused the performance of the Equipment as it pertains to the Specific Performance Levels to degrade so that the Equipment no longer meets the Specific Performance Levels; and/or

###### demonstrate that such repairs or corrective actions have not caused the performance of the Equipment as it pertains to the Guaranteed Levels to degrade since the last Performance Test or Sound Level Test.

### Not Used.

### Fittings, Instrumentation and Test Uncertainty.

###### Seller shall be responsible for ensuring that the Units are designed and manufactured with the proper fittings, orifices, and connections necessary to permit the conduct of the Performance Tests in accordance with the Test Procedures.  Seller shall also be responsible for identifying to Purchaser the necessary fittings, orifices, and connections that should be installed in the remainder of the Facility to allow a proper Performance Test to be conducted.

###### The parties anticipate using station instrumentation for Performance Tests.  In the event that Purchaser elects to conduct the first Performance Test on a Unit, the cost of the necessary instrumentation that is not Facility instrumentation shall be borne by Purchaser, and in the case of subsequent Performance Tests caused by Seller’s Equipment not meeting a Guaranteed Level or Specific Performance Level the cost of instrumentation shall be to Seller’s account.

###### Seller will be allowed to account for test uncertainty when comparing the Adjusted Electrical Output to the Electrical Output Guarantee and the Specific Performance Electrical Output Guarantee, and the Adjusted Heat Rate to the Heat Rate Guarantee and the Specific Performance Heat Rate Guarantee.  The definition of and calculation of the test uncertainty shall be in accordance with ASME PTC 22, ASME PTC 19.1 and the Performance Test guidelines set forth in Exhibit F.

### Consumable Spare Parts During Retests»

.  The cost of consumable spare parts during retests caused by Seller’s failure to achieve Guaranteed Levels or Specific Performance Levels shall be to Seller’s account.

## Remedies For Failure to Meet Specific Performance Requirements.

### Corrective Actions»

.  If one or more of the Units at the Facility fails to satisfy one or more of the Specific Performance Levels or a Guaranteed Level, Purchaser will, if Seller so requests and if Takeover has not occurred, operate the Facility or cause the Facility to be operated at the loads and conditions necessary to allow Seller to determine the causes of the nonconformity, if any, and the expedient remedial action.

Following the commissioning functional checks or Performance Test as applicable, or additional running of the Facility for such diagnostic purposes, Seller shall at its own expense:

###### repair at the Site such parts of the Unit(s); or

###### remove the defective parts and provide and install the new parts,

to cause such failed Unit(s) to meet Specific Performance Levels (such election subject to Purchaser’s approval, such approval shall not be unreasonably withheld).

If such failed Unit(s) still fail to satisfy Specific Performance Levels, Seller shall at its own expense make such further repair or replacement until the Units meet Specific Performance Levels.

### Failure to Achieve Specific Performance»

.  In the event of any failure to achieve the Specific Performance Levels within one hundred eighty (180) Days of the completion of the applicable Unit’s initial Performance Test, Purchaser shall have the right to terminate the Agreement in accordance with Sections 7.2.7, 17.2, 17.3 and 17.4.

## Acceptance»

.  Acceptance for each Unit shall occur upon:

##### the earliest of:

###### if, through no fault of Seller, a Performance Test or Sound Level Test on the Unit has not been conducted by the end of the Installation Period (except as provided in Section 10.12.4.2);

###### upon the issuance of a Performance Test Completion Certificate by Purchaser evidencing that the Specific Performance Levels and the Guaranteed Levels have been achieved (such Performance Test Completion Certificate to be issued within thirty (30) Days after successful completion of testing); or

###### in the event that the Unit has passed the Specific Performance Levels, but not the Guaranteed Levels and (1) Seller has for a period of one hundred eighty (180) Days after the initial Performance Test of the Unit made reasonable best efforts to improve the Unit’s performance and still have met the Specific Performance Levels, but not the Guaranteed Levels, and, (2) Seller has paid Liquidated Damages in accordance with Section 6.4 hereof with respect to any Guaranteed Levels not achieved;

Provided that:

##### all special tools provided hereunder shall have been delivered to Purchaser;

##### Seller has delivered to Purchaser a waiver of liens in form as shown in Exhibit S that have been or could have been placed upon the Equipment and that there are no outstanding claims of Seller or any Vendor with respect to the Equipment;

##### Seller has paid any Take Over Liquidated Damages due;

##### Seller has paid any Delivery Liquidated Damages due;

##### Seller has paid any O & M Instruction Liquidated Damages;

##### All Punchlist items have been completed;

##### Seller has satisfied all other material obligations required for Purchaser to achieve Takeover; and

##### Seller has provided all O&M Manuals.

Upon the occurrence of these events, Seller may submit a certificate to Purchaser indicating it has achieved Acceptance.  Purchaser shall within ten (10) Days of receipt of such certificate, either sign such certificate acknowledging concurrence or reject such certificate specifically stating the reasons for such rejection.

## Unit Serial Numbers»

.  Seller has identified and listed in Exhibit P, the Unit serial numbers which are available at the Effective Date of this Agreement.  To the extent Unit serial numbers are not so identified, the serial numbers of the remaining Units will be made available one hundred twenty (120) Days prior to the Guaranteed Unit Delivery Date.  Seller may not change the Units associated with such serial numbers or the serial numbers themselves without Purchaser’s prior written agreement. Purchaser shall only withhold such written agreement if, based upon the reasons given by Seller and verified by Purchaser, Purchaser reasonably believes that such change would result in a delay of the Units.

# CHANGE ORDER

## Adjustment of Purchase Amount»

.  The Purchase Amount shall be subject to adjustment solely for (a) Purchaser-requested changes in the Scope of Work in accordance with Section 11.2, (b) Seller-requested changes in the Scope of Work, which are approved in writing by Purchaser in accordance with Section 11.3, and (c) the circumstances described in Section 5.3.

## Purchaser Requested Change Order»

.  If Purchaser desires to make any change in the Scope of Work (a “Change Order”), Purchaser shall advise Seller, and Purchaser and Seller shall consult concerning the estimated cost and impact on the Guaranteed Unit Delivery Date(s) and the Purchase Amount. Thereafter, Purchaser may request, and Seller shall upon receipt of such reasonable request prepare, a detailed estimate of the cost of such change, taking into account the effect of such change on the Scope of Work and other agreed upon and contemplated Change Orders.  Purchaser shall review Seller’s estimate, and if Purchaser accepts or the parties otherwise agree as to the Change Order, it shall be endorsed by Purchaser.  Thereafter, the parties shall promptly adjust the Guaranteed Unit Delivery Date(s) and the Purchase Amount and any other Exhibits requiring adjustment to reflect the Change Order.  In the event Seller proceeds with any proposed changes in the Scope of Work prior to execution of a Change Order, Seller shall do so at its own risk.  Purchaser has no obligation to pay Seller for any additional cost and Seller is not entitled to any extension of time for performance as a result of any change implemented by Seller without an executed Change Order.  Modifications or changes in the Specification which are within the general scope  of the Agreement may be made at any time by Purchaser’s Representative written order to Seller.

## Seller Requested Change Order»

.  If Seller determines that a condition or the occurrence of an event requires a change in the Scope of Work, Seller shall within fifteen (15) Days of being aware of the occurrence or condition of the event prepare and deliver to Purchaser a request for a Change Order which shall describe such condition or event in detail.  Within fifteen (15) Days following delivery of such request, or such other period as may be agreed upon by the parties, Seller shall specify the  proposed adjustment to the Scope of Work, the Guaranteed Unit Delivery Date(s) and/or the Purchase Amount requested by it.  Following receipt of such request, Purchaser shall determine in its sole and exclusive discretion whether any changes to the Scope of Work, the Guaranteed Unit Delivery Date(s) and/or the Purchase Amount shall be effected, but failure by Purchaser to approve any such changes  shall not affect or modify any of Seller’s obligations hereunder or cause an increase in the Purchase Amount and/or extension of the Guaranteed Unit Delivery Date(s).  If Seller proposes changes in the Scope of Work to Purchaser, Seller shall not make such changes without receiving the prior written consent of Purchaser which shall be reflected on a Change Order, in accordance with the procedures as described in Section 11.2.

## Adjustment to Guaranteed Unit Delivery Dates»

. The Guaranteed Unit Delivery Dates shall be subject to adjustment solely for (a) Purchaser-requested changes in the Scope of Work in accordance with Section 11.2,  (b) Seller- requested changes in the Scope of Work, which are approved in writing by Purchaser in accordance with Section 11.3, and (c) the circumstances described in Section 10.2.4.1., if and to the extent that such circumstances directly result in delay.

## Disputes»

.  In the event of an unresolved dispute regarding a Change Order, the parties agree that the matter shall be submitted to dispute resolution in accordance with ARTICLE XXVI.

## Change Order Pricing»

.  All changes to this Purchase Amount resulting from a Change Order shall be either lump sum, or unit price.

# (NOT USED)

# ORDER OF PRECEDENCE

## Order of Precedence»

.  This Agreement shall be read as a whole and in the event of a conflict between documents, the following order of precedence shall govern:

a:  Articles I through XXX

b:  Exhibits, other than Exhibits B and B-1

c:  Exhibit B

d:  Exhibit B-1

# WARRANTY

## Seller’s Warranty»

.  Seller warrants with respect to each Unit on a continuing basis during the Primary Warranty Period, that:

##### the Equipment and all other materials and articles furnished hereunder are new, unrepaired (except as permitted in writing by Purchaser) and of suitable grade for the purpose intended;

##### the Scope of Work was performed in a good and workmanlike manner and in  accordance with the degree of care, skill and diligence consistent with industry standards, the Equipment is free of defects in materials and/or workmanship and the Equipment is designed and fit for the purpose of generating electric power when operated in accordance with Seller’s specific written operation instructions and, in the absence thereof, in accordance with generally accepted operation practices of the electric power producing industry;

##### the Equipment conforms to the Specification and other requirements of this Agreement;

##### the Equipment will be “Year 2000 Capable,” meaning that (i) the computer hardware and software that is part of said Equipment and any information technology contained therein will accurately process date and time data within the Warranty Period and (ii) neither performance nor functionality of the said Equipment will be affected materially by dates within the Warranty Period.

### Primary Warranty Period»

. With respect to each Unit, the Primary Warranty Period shall be for one (1) year commencing upon the earlier of:

###### Acceptance; or

###### Commercial Operation (the “Primary Warranty Period”).

### Warranty Clarification»

.  Seller shall have no obligation for correction, repair or replacement of the Equipment in accordance with this ARTICLE XIV to the extent that a defect is the result of:

###### normal wear and tear;

###### normal degradation in the performance of the Equipment;

###### Purchaser’s misuse or negligence;

###### the Equipment not having been operated and maintained in accordance with Seller’s written operating limitations and maintenance instructions, or accepted industrial practice.

###### installation of the Equipment or any relevant part thereof by Purchaser or its contractors other than in conformance with Seller’s or its Vendor’s written specifications, manuals or other written instructions (except as specifically set forth in this Agreement); or

###### a Purchaser directed change in the design or construction of the Equipment which Seller reasonably disputes as not being in accordance with good workmanship or generally accepted professional engineering standards, provided that Seller has given Purchaser written Notice of its dispute prior to performing any such change and such dispute ultimately is resolved in Seller’s favor.

###### Seller also shall have no obligation for defects in the Equipment to the extent that, after the commencement of the Primary Warranty Period, such defect arises out of Purchaser’s failure to: notify Seller within a reasonable time after an Equipment defect becomes apparent (such Notice not to be later than thirty (30) Days from the date supervisory level personnel of Purchaser responsible for the Facility become aware of such defect).

###### Seller shall have no Year 2000 Warranty responsibility for any such failure of the Equipment that is directly or indirectly caused by the failure of products used with the Equipment to function properly, use of data or information that is inaccurate or incompatible with the Equipment’s interfaces, requirements, or specifications, or use of the Equipment other than in accordance with written instructions of Seller.

### Warranty Breach Notice»

.  In the event Purchaser believes that a defect has arisen, Purchaser shall notify Seller of such a defect in writing (fax notification followed by mailed Notice) describing the nature of the breach.

## Extended Warranty Period.

### Continued Warranty on Corrections or Repairs Performed During the Primary Warranty Period»

.  With respect to any portion of the Equipment corrected, repaired, modified or replaced as a result of a defect manifesting during the Primary Warranty Period,  Seller shall warrant such portion of the Equipment in accordance with Section 14.1 for a period of twelve (12) months from the date of such modification or correction (the “Extended Warranty Period”), but in no event shall the Extended Warranty Period extend more than twelve (12) months beyond the Primary Warranty Period.

### Extension of Warranty Due to Unavailability»

.  The Primary Warranty Period or Extended Warranty Period shall be extended by a period equal to the period during which the Unit(s) (or that part in which the defect or damage has appeared or occurred) cannot be reliably operated as intended by reason of that defect or damage.

## Obligations, Responsibilities and Recourse»

.  If the warranties set forth in Section 14.1 hereof are breached, Seller shall repair, replace, and/or correct the applicable portion of the Scope of Work immediately or on an expedited basis such that it meets the requirements of this Agreement but at no cost to Purchaser.  Seller shall provide a service engineer to begin corrective action on the Equipment as soon as reasonably possible after receipt by Seller of Purchaser’s Notice referred to in Section 14.1.3 but not later than seventy-two (72) hours after receipt of such Notice.  Seller shall, at its sole expense, disassemble, remove, replace and reinstall the Equipment to the extent necessary while minimizing the downtime required for Seller to perform its warranty obligation.  Purchaser shall provide Seller with full and free access to the Facility to perform its warranty obligations under this Agreement, so long as such access does not unreasonably interfere with operation of the Facility.  Any change to parts or equipment that would alter conformance with the Specification may be made only with prior written approval of Purchaser in accordance with the terms of ARTICLE XI hereof.  If, after notification of such defect, Seller shall unreasonably delay the commencement, continuance or completion of making good such defect(s), Purchaser may then, following written Notice to Seller, correct such defect(s) in accordance with this Agreement, and Seller shall be liable for all reasonable costs, charges and expenses incurred by Purchaser in connection with such reasonable repair or replacement and shall forthwith pay to Purchaser an amount equal to such costs, charges and expenses upon receipt of invoices certified by Purchaser.  In an emergency where delay would cause serious risk of loss or damage, and Notice to and corrective action by Seller is not possible in a timely manner, Purchaser may take such actions as reasonably necessary to mitigate such risk and correct the deficiency with oral Notice followed immediately with written confirmation of the Notice to Seller in accordance with Section 14.1.3.  Such emergency actions shall be to the account of Seller.

## Not Used.

## Limited Warranty»

.  THE WARRANTIES AND REMEDIES FOR BREACH OF WARRANTY CONTAINED IN THIS AGREEMENT ARE THE EXCLUSIVE WARRANTIES AND WARRANTY REMEDIES BY SELLER APPLICABLE TO THE EQUIPMENT AND ARE EXPRESSLY IN LIEU OF ANY OTHER WARRANTIES, EXPRESS OR IMPLIED, INCLUDING ANY IMPLIED WARRANTY OF SATISFACTORY QUALITY (MERCHANTABILITY) OR FITNESS FOR A PARTICULAR PURPOSE, OR ANY OTHER WARRANTY EXPRESS OR IMPLIED AGAINST VICES OR DEFECTS, LATENT  OR OTHERWISE.  SELLER NEITHER ASSUMES NOR AUTHORIZES ANY OTHER PERSON TO ASSUME FOR IT ANY OTHER WARRANTY OBLIGATION IN CONNECTION WITH THE EQUIPMENT OR ANY PART THEREOF.

## Repairs and Alterations by Others»

.  Unless Seller has failed to provide a service representative or otherwise comply with its repair obligations under this Agreement, Seller shall have no obligation hereunder to the extent that the Equipment becomes defective in whole or in part as a direct result of repairs (other than normal maintenance as set out in Seller’s instruction manuals, approved emergency repairs, and replacing defective parts with Seller approved spares) not made by Seller or a GE-managed depot repair facility.  In the event that Purchaser or a third party other than a GE-managed depot undertakes major unauthorized alterations or repairs to the Equipment without Seller’s written consent, any warranty applicable to the Equipment adversely affected by such alterations or repairs shall be terminated.

## Termination of Warranty»

.  If a defect covered by the warranty is discovered by Purchaser and Purchaser does not:

###### promptly take reasonable action to mitigate the damage consequent to the occurrence of the defect; or

###### notify Seller and allow Seller to correct the defect in accordance with Section 14.3.

Seller shall not be responsible for repair of that part of the damage attributed to Purchaser’s failure to take such action.

# RISK OF LOSS AND TITLE

## Risk of Loss»

.  Seller shall bear the risk of loss and damage with respect to an item of Equipment until Seller has completed the delivery at the Delivery Point in accordance with Section 10.2.5.  In the event Purchaser elects to use the Optional Delivery Point, the point of transfer of risk of loss and damage will be set out in the applicable Optional Delivery Point Change Order pursuant to Section 10.2.3.1.

## Title.

### Passage of Title»

.  Title to Equipment, drawings, specifications, O & M Manuals and like materials prepared specifically for the Scope of Work under this Agreement will pass from Seller to Purchaser when the Equipment is ready for shipment to the Delivery Point(s) and Seller has notified Purchaser that the Equipment is ready for shipment.  Seller shall be the importer of record for all such non-U.S. manufactured Major Components, and will be responsible for all import duties and costs associated with clearing U.S. customs. Seller warrants that legal title to and ownership of the Equipment (including, subject to the use and disclosure limitations in ARTICLE XXI, all calculations, as-built, arrangements drawings, detailed engineering drawings and other drawings and documentation required by Purchaser in connection with the operation and maintenance of the Equipment) shall be free and clear of any and all liens, claims, security interests or other encumbrances when title thereto passes to Purchaser.  Title to Seller’s standard drawings and documents which are provided to Purchaser shall remain with Seller, provided however Seller grants permission without charge to Purchaser, Lender, Purchaser’s operator and subsequent owners and operators to use such documents as set out in Section 15.3.

### Infringement Cures and Defense»

.  In the event a suit or proceeding is brought against Purchaser, Lender, Purchaser’s Facility operator or their Affiliates, (the “Patent Indemnities”) for infringement of any patent, copyright, trademark, trade secret or other intellectual property right, Seller shall indemnify and hold harmless Patent Indemnities, their authorized agents, and anyone directly or indirectly employed by them from and against all claims, damages, losses and expenses (including attorneys’ fees) arising out of any infringement of patent rights or copyrights incident to the use or production of the Equipment or incorporation therein of any invention, design process, product or device not specified in the Agreement, and shall defend all such claims in connection with any alleged infringement of such rights.  Seller shall pay all costs and expenses of any such action or suit or threat thereof, including compensation and expenses of experts and counsel of its choice and selection and Seller shall also pay and hold Patent Indemnitees free and harmless from expenses incurred or any damages or other sums awarded or assessed in any such action or suit including costs resulting from imposition of any injunction against Patent Indemnitees.  Patent Indemnitees may be represented by counsel of their own selection and expense, but agree to cooperate fully in the defense of any such action or suit and to furnish all the evidence in its control.

Nothing herein shall authorize Seller to settle any such suit or action as referred to in this Section 15.2.2 without prior authorization from the affected Patent Indemnitee if, by such settlement, the affected Patent Indemnitee shall be obliged to make any monetary payment, part with any property or any interest therein, to assume any obligation or restriction upon operation of the Equipment or Facility or production of electricity, to be subject to any injunction or to grant licenses or other rights under its patent or other industrial or intellectual property rights, or surrender or release any other rights, remedies, interests or claims.

In the event a Patent Indemnitee is as a result of such suit or proceeding prevented from using such alleged infringing Equipment or other deliverables, Seller shall undertake and conclude as quickly as reasonably possible at its option and expense one of the following courses of action:

###### obtain the right to continued use of the Equipment or other deliverables under this Agreement;

###### correct or modify the infringing aspect of the Equipment or other deliverables under this Agreement so that it becomes non-infringing; or

###### replace the infringing Equipment or other deliverables under this Agreement with equivalent non-infringing Equipment or other deliverables.

THIS SECTION IS AN EXCLUSIVE STATEMENT OF ALL THE DUTIES OF THE PARTIES RELATING TO PATENTS AND DIRECT OR CONTRIBUTORY PATENT INFRINGEMENT AND OF ALL THE REMEDIES OF PURCHASER RELATING TO ANY CLAIM, SUIT, OR PROCEEDING INVOLVING PATENTS, COPYRIGHT, TRADEMARK, TRADE SECRET OR OTHER INTELLECTUAL PROPERTY RIGHTS.  Compliance with this Section as provided herein and ARTICLE XXI shall constitute fulfillment of all liabilities of the parties under the Agreement with respect to patents, copyright, trademark, trade secret or other intellectual property rights.

## Seller’s Drawings, Etc. for Use by Purchaser»

.  All drawings, documents, engineering and other data furnished or to be furnished by Seller in performing the Scope of Work may be used by Purchaser, Purchaser’s operator or a subsequent owner for the purpose of designing, procuring, constructing, operating, maintaining, repairing and altering the Equipment and Facility.

## Licensing Procedure»

.  Seller grants Purchaser a non-exclusive license to use the Equipment supplied under this Agreement for operating, maintaining and repairing the Facility.  Purchaser shall have no right to the source code; provided, however in the event Seller or Seller’s vendor discontinue maintenance of such Equipment, Seller shall on a best efforts basis attempt to obtain such source code for Purchaser.  The non-exclusive license granted herein to Purchaser may be transferred by Purchaser to Purchaser’s Facility operator, Lender(s), or successor owners of the Facility (for the sole purpose of operating the Facility).

Seller and/or its licensors shall at all times remain owners of the software/firmware licensed.

# TRAINING AND TECHNICAL DIRECTION OF INSTALLATION

Seller shall provide technical direction of installation of the Equipment in accordance with Exhibit H-1.  Seller shall provide on Site operation and maintenance training for Purchaser’s operations and maintenance personnel in accordance with Exhibit H-2.  Purchaser shall be responsible for the travel and per diem costs of its personnel and for providing or procuring all training facilities on or in the immediate vicinity of the Site.

# DEFAULT

## Events of Default by Seller»

.  Seller shall be in default hereunder upon the occurrence of any one of the following events, which shall be events of default (each an “Event of Seller Default”) if not cured within thirty (30) Days following delivery to Seller of a Notice of such event from Purchaser, or, if not curable in such thirty (30) Day period, if Seller has not commenced the cure within such period and does not thereafter diligently pursue such cure, provided that in no event shall such extended cure period exceed one hundred twenty (120) Days and further provided that the event described in paragraph (e) below shall be an Event of Seller Default upon its occurrence without the aforesaid Notice or cure period:

##### Seller shall have assigned or transferred this Agreement or any right or interest herein except as expressly permitted by this Agreement;

##### any representation made by Seller in this Agreement (which shall be true and correct throughout the performance of this Agreement)  shall be materially false or misleading as made, including without limitation the following representations:

###### Seller is not in breach of, in default under, or in violation of, any applicable statute, law, ordinance, decree, rule, or regulation of any governmental authority, or the provisions of  its articles of incorporation or by-laws or any franchise or license, or in breach of, in default under, or in violation of, any provision of any indenture or any evidence of indebtedness or security therefor, lease, contract, license or other agreement by which it is bound if such breach, default or violation may result in a material adverse effect on the business or financial condition of Seller; and the execution and delivery of this Agreement and the performance of its obligations hereunder will not constitute or result in any such breach, default or violation; and

###### no suit, claim, action, arbitration, or legal, administrative or other proceeding is pending or to the best of Seller’s knowledge threatened against Seller that would affect the validity or enforceability of this Agreement, the ability of Seller to fulfill its commitments hereunder in any material respect, or that could result in any material adverse change in the business or financial condition of Seller;

##### Seller shall have defaulted in its performance under any material provision of this Agreement or failed to comply with any covenant herein.  The parties agree that Purchaser may not terminate for default based upon a Unit’s failure to meet Guaranteed Levels if Seller has caused the Unit to meet Specific Performance Levels in accordance with the terms of this Agreement.

##### Purchaser may also terminate this Agreement for default in part as to the applicable Unit in the event of the following, each of which shall constitute an Event of Seller Default:

###### Seller’s liability for Delivery Liquidated Damages with respect to a Unit, as determined in accordance with Section 10.3, amounts to fifteen percent (15%) of the Unit Liability Amount; or

###### Seller’s liability for Take Over Liquidated Damages with respect to a Unit, as determined in accordance with Section 10.3.2, amounts to fifteen percent (15%) of the Unit Liability Amount; or,

###### Seller fails to cause a Unit to achieve a Specific Performance Level within one hundred eighty (180) Days after Purchaser conducts the initial Performance Tests or Sound Level Test; or

###### Seller’s liability for Liquidated Damages with respect to a Unit, determined as provided in ARTICLE X, amounts to exceeds thirty percent (30%) of the Unit Liability Amount.

If the defaulting Unit is to be used in conjunction with other Units at the same Facility, at Purchaser’s sole discretion, the Agreement may be terminated as to those Units as well if (i) the default in relation to the affected Unit impacts Purchaser’s ability to comply with obligations to a third party, (ii) the value of the remaining Units is materially diminished by the defaulting Unit, or (iii) it reasonably appears to Purchaser that Seller will be unable to comply with its  obligations under this Agreement relating to the remaining Units.

##### any proceeding is instituted against Seller seeking to adjudicate Seller as a  bankrupt or insolvent, or Seller makes a general assignment for the benefit of its creditors, or a receiver is appointed on account of the insolvency of Seller, or Seller files a petition seeking to take advantage of any other law relating to bankruptcy, insolvency, reorganization, winding up or composition or readjustment of debts and, in the case of any such proceeding instituted against Seller (but not by Seller), such proceeding is not dismissed within sixty (60) Days of such filing.

## Purchaser’s Remedies Against Seller»

.  The provisions of ARTICLE XXVI hereof notwithstanding, and without limitation of Purchaser’s rights under ARTICLE X for those Liquidated Damages paid or due prior to an Event of Seller Default, if an Event of Seller Default shall have occurred and be continuing, Purchaser or its assignee shall have the right to terminate this Agreement in whole or in part by delivery of a Notice of termination to Seller.  For the avoidance of doubt, the Agreement, may be partially terminated on a Unit basis as a result of an Event of Seller Default in accordance with the provisions of this Agreement.

## General Obligations»

.  If Purchaser elects to terminate this Agreement in whole or in part  pursuant to Section 17.2 hereof, Seller shall, and at Seller’s expense, subject to Section 27.1 hereof,  at Purchaser’s option either:

##### promptly refund all amounts paid to date and pay Cover Damages plus Termination Costs described in Sections 17.4.2(i) and 17.4.2(iv) described below; or

##### perform the following services relative to the Scope of Work so affected;

assist  Purchaser in preparing an inventory of all Equipment and documentation to which Purchaser has not already taken title;

assign to Purchaser, or to any person designated by Purchaser without any right to compensation not otherwise provided for herein, title to all portions of the Equipment and documentation not already owned by Purchaser, together with all subcontracts and other contractual agreements (including warranties) as may be designated by Purchaser, all of which subcontracts and contractual agreements shall be so assignable, and to Purchaser to the extent assignable all issued licenses,  authorizations, approvals and rights to complete and to use the Equipment under patents and other proprietary or intellectual property rights then held by Seller or its Vendors pertaining to the Equipment;

afford to Purchaser all design, expertise and other information as may be  necessary for the operation of the Equipment for which title has passed to Purchaser (subject to the requirements of Section 21.1 hereof); and

supply any proprietary components or procure and supply substituted nonproprietary components need for the completion and operation of the Equipment.

## Payment Obligations.

### Determination of Obligations»

.  If Purchaser terminates this Agreement pursuant to Section 17.2 hereof, and requests delivery of the Equipment and the materials and services described in Section 17.3(b) above, Purchaser shall determine the value of that portion of the Scope of Work, which has been properly completed, if any (the “Proper Scope Value”).  The Proper Scope Value shall not exceed the Unit Liability Amount on a Unit basis or Maximum Liability Amount on an aggregate Unit basis.  If Purchaser has paid Seller an amount greater than the Proper Scope Value the difference between the amount paid to Seller, considering amounts paid prior to execution of this Agreement, and the  Proper Scope Value (the “Refund Amount”) shall be settled between the parties in accordance with Section 17.4.4 below.  If the amount paid by Purchaser to Seller is less than the Proper Scope Value, considering amounts paid prior to execution of this Agreement, the difference between the amount paid and the Proper Scope Value (the “Scope Value Due”) shall be settled between the parties in accordance with Section 17.4.4 below.  If Seller disagrees with Purchaser’s determination of the Proper Scope Value, such dispute shall be resolved in accordance with ARTICLE XXVI.

### Damages and Expenses»

.  Purchaser shall determine the total damages and reasonable and necessary expenses incurred in connection with:

###### the termination of this Agreement or part thereof (including all legal fees and expenses for,  inter alia, the negotiation of an agreement with an alternate supplier);

###### if Section 17.3(b) hereof is applicable, any rework, modifications or replacement of the Equipment to cause it to comply with the requirements of this Agreement;

###### if Section 17.3(b) hereof is applicable, the completion of the Scope of Work and all associated incidental costs, and

###### amounts otherwise due Purchaser from Seller pursuant to this Agreement (including but not limited to Liquidated Damages).

The total of items (i) through (iv) above shall be referred to as the “Termination Costs”.  In the case of Event of Seller Default as set forth in Section 17.1.1(i), (ii) or (iv), Purchaser shall be entitled to such Liquidated Damages plus Termination Costs.

### Cover Damages»

.  If Section 17.3(a) hereof is applicable, the amount of “Cover Damages” shall be the difference between the Maximum Liability Amount under this Agreement (or portion thereof in the case of partial termination) and the purchase price payable by Purchaser for a replacement contract for substantially similar Equipment and Scope of Work under this Agreement, suitable for the Facility and substantially meeting the Specifications set forth in this Agreement, plus incremental transportation costs incurred.  Purchaser agrees that it has a duty to mitigate any damages and that it shall use commercially reasonable efforts to minimize Cover Damages it may incur as a result of procuring a replacement contract in the event of termination hereunder.

### Settlement»

.   Upon determining the Proper Scope Value and the Termination Costs, if any, the termination settlement (the “Termination Settlement”) shall be determined and invoiced as follows:

##### if Section 17.3(a) is applicable, the Termination Settlement shall be the amounts described in Section 17.3(a).

##### if Section 17.3(b) hereof is applicable, the Termination Settlement shall be as follows:

###### if the Scope Value Due is greater than zero (0), and if

the Termination Costs are greater than the Scope Value Due, Seller shall pay Purchaser the difference of the Termination Costs less the Scope Value Due, or

the Scope Value Due is greater than the Termination Cost, Purchaser shall pay Seller the difference of the Scope Value Due less the Termination Costs.

###### if the Refund Amount is greater than zero (0), then Seller shall pay Purchaser the sum of the Refund Amount plus the Termination Costs.

###### if the Refund Amount and the Scope Value Due are each zero (0), Seller shall pay Purchaser the Termination Costs.

Seller or Purchaser, as applicable, shall make payment of an invoice received for Termination Settlement within thirty (30) Days of receipt of such invoice.  Any such Termination Settlement not paid when due shall accrue interest at the Interest Rate.

## Events of Default by Purchaser»

.  Purchaser shall be in default hereunder upon the occurrence of any one of the following events, which shall be events of default (each an “Event of Purchaser Default”) if not cured within thirty (30) Days following delivery to Purchaser of a Notice of such event from Seller or if not curable in such thirty (30) Day period, if Purchaser has not commenced the cure within such period and does not thereafter diligently pursue such cure, provided that in no event shall such extended cure exceed one hundred twenty (120) Days further provided that the event described in paragraph (d) below shall be an Event of Purchaser Default upon its occurrence without the aforesaid Notice or cure period:

##### Purchaser shall have assigned or transferred this Agreement or any right or interest herein except as expressly permitted by this Agreement;

##### any representation made by Purchaser in this Agreement shall have been materially false or misleading when made;

##### Purchaser shall have defaulted in its performance under any material provision of this Agreement; or

##### any proceeding is instituted against Purchaser seeking to adjudicate Purchaser as a bankrupt or insolvent, or Purchaser makes a general assignment for the benefit of its creditors, or a receiver is appointed on account of the insolvency of Purchaser, or Purchaser files a petition seeking to take advantage of any other law relating to bankruptcy, insolvency, winding up or composition or readjustment of debts and in the case of any such proceeding instituted against Purchaser (but not by Purchaser) such proceeding is not dismissed within sixty (60) Days of such filing.

## Seller Remedies»

.  The provisions of ARTICLE XXVI hereof notwithstanding, if an Event of Purchaser Default shall have occurred and be continuing beyond the time allowed in Section 17.5, Seller shall have the right, as its sole and exclusive remedy, to terminate this Agreement by delivery of a Notice of termination to Purchaser and receive as liquidated damages the applicable Cancellation Charge pursuant to Section 5.4 as if the Agreement was cancelled by Purchaser.

# FORCE MAJEURE

## Failure to Perform Due to an Event of Force Majeure»

.  Subject to the terms of this ARTICLE XVIII, either party shall be excused from performance and shall not be considered to be in default with respect to any obligation hereunder, to the extent such party’s (the “Affected Party”) failure of performance is due to an Event of Force Majeure.

## Events of Force Majeure»

.  Events of Force Majeure shall be limited to the circumstances set forth in Section 18.4 (the “Event of Force Majeure”)  but only if, and to the extent:

###### such circumstance is not within the reasonable control of the Affected Party;

###### such circumstance, despite the exercise of reasonable diligence, can not be prevented, avoided or removed by Affected Party;

###### such circumstance prevents the Affected Party from fulfilling its obligations under the Agreement;

###### the Affected Party has taken all reasonable precautions, due care and reasonable alternative measures in order to avoid the effect of such event on the Affected Party’s ability to fulfill its obligations under the Agreement and to mitigate the consequences thereof; and

###### such event is not the result of any failure of the Affected Party to perform any of its obligations under the Agreement.

## Notice of Event of Force Majeure»

.  As soon as possible following the date of commencement of any Event of Force Majeure, if either party desires to invoke such Event of Force Majeure as a cause for delay in the performance of any obligation hereunder or as potential adjustment of the Purchase Amount, it shall promptly (but not later than three (3) Days upon learning of such Event of Force Majeure), advise the other party in writing of such date.  Notices shall be in accordance with Section 25.1.  Within seven (7) Days, the Affected Party shall provide in writing a description of the event and reasonable alternative measures which the Affected Party has taken in order to avoid the effect of such event on such party’s ability to fulfill its obligations under the Agreement and to mitigate the consequences thereof, and the nature and expected duration of such Event of Force Majeure.  The Affected Party shall provide additional information concerning the event as reasonably requested by the other party (including, without limitation, updating of any information already provided under this Section 18.3).  As soon as practicable after the commencement of the Event of Force Majeure, the Affected Party shall allow the other party’s professional advisers access to its premises and equipment to enable the other party to assess the event and the steps to avoid or remove the circumstances constituting the event.  Within a reasonable time following the date of termination of such Event of Force Majeure, the party having invoked such Event of Force Majeure as a cause for such delay or potential adjustment of the Purchase Amount shall submit to the other party as soon as practicable, reasonable proof of the nature of such delay and its effect upon the Guaranteed Unit Delivery Date, or the basis for an adjustment of the Purchase Amount.  The burden of proof to demonstrate that an Event of Force Majeure has occurred and affects the Affected Party’s ability to perform, rests with the Affected Party.  The parties will meet within ten (10) Days after receipt of the Notice by the unaffected party to discuss appropriate measures that should be taken.  The parties shall thereupon consult with one another concerning the effect of such Event of Force Majeure and an extension of the Guaranteed Unit Delivery Date(s) described in Section 10.2.1 or, if applicable, an adjustment in the Purchase Amount described in Section 5.1 shall be made by the parties to take into account such effect on the ability of Purchaser and Seller to reschedule project activities to avoid or minimize overall delays or additional costs resulting from the Event of Force Majeure.  The parties:

###### shall make all reasonable efforts to prevent and reduce to a minimum and mitigate the effect of any delay or potential adjustment of the Purchase Amount occasioned by any Event of Force Majeure including recourse to alternate acceptable source of services, equipment and materials and construction equipment; and

###### shall use their best efforts to ensure resumption of normal performance of this Agreement after the occurrence of any Event of Force Majeure and shall perform their obligations to the maximum extent practicable as agreed between the parties.

## Events of Force Majeure»

.  Subject to the provisions of Section 18.2 and Section 18.5, Events of Force Majeure shall mean the following:

##### explosions, fires, nuclear radiation contamination, hurricanes, earthquakes, floods, natural disasters, epidemics, other acts of God, and any other similar circumstances;

##### war and other hostilities (whether declared or not), revolution, public disorders, insurrection, rebellion, sabotage, acts of public officials or terrorist action;

##### any action or relative material inaction taken by any national or local government or judicial authority after the date of this Agreement, including without limitation any order, legislation, enactment, judgement, ruling or decision; or

##### national or regional strikes (to the extent affecting the Seller’s performance of Scope of Work) and strikes specific to the Site or to Seller’s manufacturing facility.

## Certain Events Not Excused»

.  Notwithstanding that an Event of Force Majeure may otherwise exist, the provisions of this  ARTICLE XVIII shall not excuse:

##### late delivery of equipment or materials caused by Seller, or caused by any of the subcontractors of Seller if Seller could have avoided such late delivery by exercising all reasonable endeavors as a prudent equipment supplier;

##### late performance by Seller caused by Seller’s failure to engage qualified subcontractors and suppliers or to hire an adequate number of personnel or labor or by inefficiencies on the part of Seller; or

##### delays resulting from reasonably foreseeable unfavorable weather or reasonably foreseeable unsuitable ground conditions.

## Continued Performance»

.  Upon the occurrence of any Event of Force Majeure, the parties shall endeavor to continue to perform their obligations under the Agreement so far as reasonably practicable and Seller shall during the period of such circumstances protect and secure the works in such manner as Purchaser shall require.  Seller shall notify Purchaser of the steps it proposes to take including any reasonable alternative means for performance of the works not prevented by the Event of Force Majeure.

## Not Used.

## Event of Force Majeure - Delays»

.  If either party becomes unable to perform all or part of its obligations under the Agreement because of an Event of Force Majeure, and the Affected Party has properly invoked and observed the provisions of Section 18.3 in respect thereof, the Affected Party shall be permitted a delay in the performance of its obligations affected by the Event of Force Majeure and, to the extent affected, an extension of the Guaranteed Unit Delivery Date(s).

## Event of Force Majeure - Cost»

.  Seller shall bear its own delay costs occasioned by any Event of Force Majeure for the first thirty (30) Day period during the occurrence or continuance of each such Event of Force Majeure.  If an Event of Force Majeure continues beyond such thirty (30) Day period in which Seller is the Affected Party, provided Seller has properly invoked and observed the provisions of Section 18.3 in respect thereof, Seller shall be entitled, subject to the provisions of Section 11.3, to recover costs occasioned by each such Event of Force Majeure which accrue after each such thirty (30) Day period pursuant to a Purchase Amount adjustment in accordance with Section 5.5 and ARTICLE XI hereof. Notwithstanding the foregoing, Seller shall not be entitled to an increase in cost due to strikes specific to its manufacturing facilities.

# INSURANCE

## Insurance - General»

.  Seller shall procure insurance at its own expense and maintain in full force and effect at all times throughout Seller’s performance under this Agreement (to include Seller’s performance of its warranty obligations) with responsible insurance carriers as set forth in this Agreement.  Seller may establish programs of self insurance to the same minimum levels as set forth below, as allowed by law.

### All Risk»

.  Seller shall purchase and maintain insurance to the full replacement cost of the Equipment during the process of fabrication and in the factory until the Equipment is loaded on Purchaser’s transport, or, if the Purchaser elects deliver at an Optional Delivery Point, until delivery at the Optional Delivery Point, for physical loss and damage including but not limited to theft, vandalism, and malicious mischief, collapse, water damage and such other perils as Seller deems appropriate.  Seller may self insure work during the fabrication process.

### Workers Compensation and Employers Liability Insurance»

.  Seller agrees to comply with workers compensation laws of each jurisdiction where the Scope of Work is performed, and to maintain a Workers Compensation and Employers Liability policy.   This policy shall be endorsed, if applicable, to provide all state coverage, alternate employer, voluntary compensation coverage and occupational disease with the limits set forth below. If the work is to be performed  on or near navigable U.S. waters, the policy shall include coverage for United State Longshoreman’s and Harbor Worker’s Act, Death on the High Seas Act, Jones Act, or their equivalent as required by the applicable laws in the jurisdiction where such work is performed.

Workers Compensation	Statutory

Employers Liability		$1,000,000 Each Accident

$1,000,000 Disease

Each Employee (Minimum)

### Commercial General Liability Insurance»

.  Seller shall maintain Commercial General Liability Insurance, endorsed to provide coverage for: Explosion, Collapse and Underground Hazards; Contractual Liability (particularly applicable to the provisions of the “General Indemnity” section of this Agreement);  and Products and Completed Operations (for a minimum of one year after completion of the Scope of Work) with the following limits:

Bodily Injury and	$1,000,000 Combined Single Limit

Property Damage	Each Occurrence, (Minimum)

### Hull and Protection and Indemnity Insurance»

.  Seller shall ensure that if any owned or non-owned watercraft of any kind is used for performance of the Scope of Work, Hull and Protection and Indemnity Insurance shall be provided for the vessels in the amounts as follows:

Hull	Full replacement value of the watercraft

P&I	$1,000,000 Each Occurrence or the full value of the vessel, whichever is greater

Such insurance may be provided by the vessel operator, by the vessel charter agreement, or by Seller as Seller deems appropriate.

### Business Automobile Liability Insurance»

.  Seller shall provide Business Automobile Liability Insurance which shall include the following coverage for all owned, non-owned and hired vehicles:

Bodily Injury   	$1,000,000 Each Person  (Minimum)

$1,000,000 Each Occurrence (Minimum)

Property Damage 	$1,000,000 Each Occurrence (Minimum)

or

Bodily Injury and 	$1,000,000 Combined Single Limit

Property Damage 	Each Occurrence (Minimum)

### Aircraft Liability Insurance»

.  If the Scope of Work necessitates the use of Seller’s or Seller’s affiliate’s owned or leased aircraft, Seller shall provide Aircraft Liability Insurance which shall be endorsed to provide coverage for non-owned as well as Guest Voluntary Settlement, with limits of:

Bodily Injury and	$10,000,000 Combined Single Limit

Property Damage	Each Occurrence

Such insurance may be provided by the aircraft operator, by the aircraft charter agreement, or by Seller as Seller deems appropriate.

### Excess Umbrella Liability Coverage»

.  Seller shall provide Excess Umbrella Liability coverage with minimum limits of:

Bodily Injury and	$5,000,000 Combined Single Limit

Property Damage 	Each Occurrence

### Vendors»

.  Seller shall require its Vendors and others connected with the Scope of Work  to provide and maintain insurance at all times during the period that their agreement related to the Scope of Work under this Agreement is in force and effect at the Vendor’s, or other’s own cost, with insurance limits which at minimum meets levels as required for similar contracts and is customary for the applicable industry.

### Certificate of Insurance»

.  Within twenty (20) Days of execution of this Agreement, Seller shall submit to Purchaser a Certificate of Insurance, in form satisfactory to Purchaser, evidencing that satisfactory coverage of the type and limits set forth hereinabove are in effect.  Policies providing such coverage shall contain provisions that no cancellation or material changes in the policies shall become effective except on sixty (60) Days advance written Notice thereof to Purchaser.  Irrespective of the requirements as to insurance to be carried as provided for herein, the insolvency, bankruptcy or failure of any insurance company carrying insurance of Seller, the failure of any insurance company to pay claims accruing, shall not affect, negate or waive any of the provisions of this Agreement including, without exception, the indemnity obligations of Seller.

### Other Requirements»

.  Seller shall be responsible for the payment of all deductible and self insurance retention amounts with respect to the insurance required to be maintained by it pursuant hereto.  All Seller insurance shall:

##### Specify Purchaser and Lender, and such other parties as Purchaser may require as additional insured for all insurance coverage other than Worker’s Compensation Insurance, or its equivalent as required in jurisdictions other than the United States;

##### Provide that Purchaser shall have the right, but not any obligation, to pay any premiums if Seller shall fail to do so, and such payment of premiums by Purchaser shall be at Seller’s expense, either by direct charge or setoff;

##### For all insurance coverage related to Scope of Work, (i) endorse policies to apply as primary insurance without right of contribution from any similar coverage which may be maintained by the Purchaser Related Parties; (ii) waive any right of subrogation against the Purchaser Related Parties and all other named and additional insured and any other right of the insurer to any setoff or counterclaim or any other deduction, whether by attachment or otherwise, in respect of any liability of Purchaser Related Parties, or any other named or additional insured; and

##### For all other insurance other than as stated in (c) immediately above, waive any right of subrogation against Purchaser, Lender and all other named and additional insured and any other right of the insurer to any setoff or counterclaim or any other deduction, whether by attachment or otherwise, in respect of Purchaser, or any other named or additional insured.

### Vendor Waiver of Subrogation»

.  Seller agrees to require all policies of insurance which are in any way related to the Scope of Work and that are secured and maintained by Seller’s Major Component Vendors to include clauses providing that each underwriter shall waive its rights of recovery, under subrogation or otherwise, against Purchaser, and Lender, and their parent and affiliated companies and their directors, officers, employees and agents (the “Purchaser Related Parties”) or alternatively shall indemnify and defend Purchaser Related Parties against such action if such action arises out of or is in any way related to this Agreement.

### Compliance with Insurance»

.  Seller and its directors, officer, representatives, agents and employees shall comply with all the terms of the policies of insurance referred to in Section 19.2 and to the extent Seller is made aware of such terms, in any Delay in Start-Up and Business Interruption Insurance obtained by Purchaser.  Seller and its directors, officers, representatives, agents and employees shall comply with the procedures for claims, notification and administration under the aforesaid insurance policies and shall not do or omit to do anything which might  void policies of insurance or entitle insurers to avoid liabilities thereunder.  Seller shall ensure that all Major Component Vendors shall be subject to provisions identical to this Section 19.1.12.

### Limitation»

. In the event that Seller breaches its obligations under the first two sentences of Section 19.1.12 of the Agreement and such breach results in an insurer avoiding, in relation to Seller, any policy of insurance obtained by Purchaser pursuant to Section 19.2 of the Agreement, Seller shall not be regarded as an additional insured under such policy and any waiver of subrogation in favor of Seller included in that policy pursuant to Section 19.2 shall not apply.

In the event that any Vendor fails to comply with the procedures for claims notification and administration under any policy of insurance obtained by Purchaser pursuant to Section 19.2 of the Agreement or does anything which might render any such policy of insurance void or entitle insurers to avoid liability thereunder and as a result thereof an insurer avoids in relation to that Vendor any such policy of insurance, that Vendor shall not be regarded as an additional insured under such policy and any waiver of subrogation in favor of that Vendor included in that policy pursuant to Section 19.2 of the Agreement shall not apply.

## Purchaser’s Insurance.

### Cargo Insurance»

.  Purchaser shall provide or cause to be provided and maintained All Risk Marine Cargo Insurance for the period of transportation commencing upon transportation from factory where final assembly occurs prior to commencing delivery to Purchaser and ending upon delivery to the Site, unless Purchaser elects to have the Seller provide transportation services to the Optional Delivery Point, in which case Seller provides Marine Cargo Insurance as provided herein.  The maximum per occurrence deductible, shall be no more than $25,000.  Purchaser shall cause Seller to be an additional insured and provided a waiver of subrogation under such policy.

### Builder’s All Risk Insurance»

.  Purchaser shall provide or cause to be provided and maintained Builder’s All Risk Insurance policy covering activities at the Site for the period of time that Seller performs TD of I Services at the Site.  Seller, to the extent of its TD of I Services on the Site, shall be named as an additional insured and provided a waiver of subrogation under such policy.  Such additional insured status and waiver shall not apply to any loss arising out of Seller’s warranty obligations as described in ARTICLE XIV hereof.

Seller shall have an opportunity to review and make reasonable comments to the Purchaser’s proposed insurance policies in respect to the Cargo insurance and Builder’s All Risk insurance.  Upon request, Purchaser shall provide Seller one copy of the relevant portions of such final insurance policies as such policies become available.

# INDEMNIFICATION

## Third Party»

.  With respect to claims brought by third parties against either Seller or Purchaser relating to the property or facilities with respect to which this Agreement pertains or the Scope of Work performed under this Agreement, Seller and Purchaser agree as follows:

##### Seller agrees to indemnify, protect, defend, and hold harmless Purchaser its directors, Lenders, officers, employees, agents, and contractors, and the directors, officers employees, agents, and contractors of Purchaser’s parent and affiliated companies (collectively “Purchaser Indemnitees”), from and against any and all demands, claims, suits and causes of action and any and all liability, costs, expenses, and judgments incurred in connection therewith, including, without limitation, court costs and reasonable attorney’s fees (a “Claim”), whether arising in equity, at common law, or by statute, or under the law of contracts, torts (including, without limitation, negligence and strict liability without regard to fault) for personal injury or damage to property of third parties (excluding Purchaser Indemnitees) or arising in favor of or brought by any of Seller’s employees, agents, subcontractors, or representatives, or by any governmental agency or any other third party (the “Purchaser Claimant”), based upon, in connection with, relating to or arising out of or alleged to arise out of Seller’s, its agents’ affiliates’, subcontractors’ or vendors’ negligence, and even if due in whole or in part to Purchaser’s concurrent negligence or fault or other fault, breach of contract or warranty, or strict liability without regard to fault; provided, however, that Seller’s contractual obligation of indemnification shall extend only to the percentage of the Claim caused by Seller, it directors, officers, employees, agents and contractors and the directors, officers, employees, agents, and contractors of Seller’s parent and affiliated companies, and shall not extend to the percentage of the Purchaser Claimant’s Claim attributable to Purchaser’s negligence or other fault, breach of contract or warranty, or to strict liability imposed upon Purchaser as a matter of law.  This indemnification obligation shall apply regardless of the amount of insurance coverage held by Seller, including that under any worker’s compensation act, disability act, or other act or law which would limit the amount or type of damages, compensation, or benefits payable by or for Seller, and shall not be limited by any insurance carried or provided by Seller in accordance with this Agreement or otherwise.

##### Purchaser agrees to indemnify, protect, defend, and hold harmless Seller its directors,  officers, employees, agents, and contractors, and the directors, officers, employees, agents, and contractors of Seller’s parent and affiliated companies (collectively “Seller’s Indemnitees”) from and against any and all demands, claims, suits and causes of action and all liability, costs, expenses, and judgments incurred in connection therewith (including, without limitation, costs and reasonable attorney’s fees), whether arising in equity, at common law, or by statute, or under the law of contracts, torts (including, without limitation, negligence and strict liability without regard to fault) for personal injury or damage to property of third parties (excluding Seller’s Indemnitees) or arising in favor of or brought by any of Purchaser’s employees, agents, subcontractors, or representatives, or by any governmental agency or any other third party (the “Seller Claimant”), based upon, in connection with, relating to or arising out of or alleged to arise out of Purchaser’s, its agents’ affiliates’, subcontractors’ or vendors’ negligence, and even if due in whole or in part to Seller’s concurrent negligence or fault or other fault, breach of contract or warranty, or strict liability without regard to fault, breach of contract or warranty, or strict liability without regard to fault; provided, however, that Purchaser’s contractual obligation of indemnification shall extend only to the percentage of the Claim caused by Purchaser, it directors, officers, employees, agents and contractors and the directors, officers, employees, agents, and contractors of Purchaser’s parent and affiliated companies, and shall not extend to the percentage of the Seller Claimant’s Claim attributable to Seller’s negligence or other fault, breach of contract or warranty, or to strict liability imposed upon Seller as a matter of law.  This indemnification obligation shall apply regardless of the amount of insurance coverage held by Purchaser, including that under any worker’s compensation act, disability act, or other act or law which would limit the amount or type of damages, compensation, benefits payable by or for Purchaser in accordance with this Agreement or otherwise.

##### In the event that both Seller, its agents, affiliates, subcontractors or vendors, and Purchaser are adjudicated negligent or otherwise at fault or strictly liable without fault with respect to damage or injuries sustained by the Seller Claimant or Purchaser Claimant, this contractual obligation of indemnification shall continue but each of Seller and Purchaser shall indemnify the other only for the percentage of responsibility of the damage or injuries adjudicated to be attributed to the indemnitor.

##### It is a condition precedent to the indemnitor’s contractual obligation of indemnification under this Agreement that the party seeking indemnity shall provide written notice of the third party claim, demand or cause of action promptly after such third party claim, demand or cause of action is received by the party seeking indemnity.  Notice shall be served on the earlier of:

###### fifteen (15) business days prior to the last day for responding to such claim or, action; or

###### the date which is one-half of the period allowed for responding to such claim or action.

It is further a condition precedent to the indemnitor’s contractual obligation of indemnification under this Agreement that the indemnitor shall thereafter have the right to participate in the investigation, defense and resolution of such third party claim.

## Survival of Obligation»

.  The duty to indemnify under this Article XX will continue in full force and effect notwithstanding the expiration or termination of this Agreement.

# NON-DISCLOSURE OF INFORMATION

## Proprietary Information»

.  Without prejudice to Sections 21.1, 21.3 and 21.4, any information concerning the parties which is designated in writing as proprietary and/or confidential and disclosed to the other party incident to the performance of the Scope of Work pursuant to this Agreement in confidence shall not be published or otherwise disclosed to others without the written approval of the disclosing party, provided, however, that nothing herein shall limit either party’s rights to disclose data which:

##### was developed on its own or furnished to it prior to this Agreement without restriction;

##### becomes generally available to the public through no fault of either party; or

##### is received by either party from a third party without restriction and not in breach of this Agreement or without fault or wrongdoing of the recipient.

Proprietary and/or confidential information disclosed hereunder shall only be used by the transferee in the performance of its obligations hereunder or as expressly permitted under this Agreement.  Each party shall take such actions to protect proprietary and/or confidential information disclosed by the other party as are consistent with its practices to protect its own proprietary and/or confidential information.

Furthermore Purchaser or Seller may upon written Notice in advance to the other party  provide any such information to any governmental authority having jurisdiction and asserting a right to obtain such information, but only to the extent required to do so by law. This clause shall survive the termination of this Agreement.

## Press Releases»

.  Seller and Purchaser agree that it is in both parties’ interest to limit information of strategic value disseminated to the independent power industry regarding this Facility.  To the extent that a party desires to issue press releases, advertisements in the trade press, tombstones in the financial or trade press then that party must obtain the other party’s written release to do so.

## Confidentiality of Seller»

.  Seller acknowledges that Purchaser’s business is highly competitive and that Purchaser’s books, records, documents and technical information concerning its products, equipment, services, processes, procurement procedures, pricing techniques, the names of and other information (such as credit and financial data) concerning Purchaser’s customers and business affiliates, all comprise confidential business information and trade secrets of Purchaser which are valuable, special and unique proprietary assets.  Seller further acknowledges that protection of Purchaser’s confidential business information and trade secrets against unauthorized disclosure and use is of critical importance to Purchaser in maintaining its competitive position.  Accordingly, Seller hereby agrees that it will not, at any time during or after the term of this Agreement, make any unauthorized disclosure of any confidential business information or trade secrets of Purchaser or make any use thereof, except for the benefit of, and on behalf of Purchaser.  However, Seller’s obligation under this Section 21.3 shall not extend to information which is or becomes part of the public domain or is available to the public by publication or otherwise through no wrongful act or omission or noncompliance with this Section by Seller or its agents.  The provisions of this Section 21.3 shall survive the termination of this Agreement.  Seller agrees and acknowledges that money damages would not be sufficient to remedy  for any breach of this Section 21.3 by Seller, and Purchaser shall be entitled to specific performance and injunctive relief as remedies for such breach or any threatened breach.  Such remedies shall not be deemed the exclusive remedies for a breach of this Section 21.3 by Seller but shall be in addition to all remedies available at law or in equity to Purchaser including recovery of damages from Seller.  For the purposes of this paragraph, the term “Purchaser” shall also include Affiliates of Purchaser.

Seller shall deliver to Purchaser all Purchaser confidential information provided or disclosed to or used or acquired by Seller, including all information developed, derived, or created therefrom, or portions thereof, upon the earlier of:

###### the ending of the need for the information for performance of the Scope of Work;

###### Purchaser’s request;

###### the completion of the Scope of Work for which it was provided, disclosed used or acquired; or

###### cancellation, termination or suspension of this Agreement.

Seller may retain a single copy of all information upon which its Scope of Work is based for record purposes only.  In the event Seller, with Purchaser’s consent, releases Purchaser’s confidential information to a third party, Seller shall require such third party to enter into a confidentiality agreement similar to this Section 21.3 with Seller, and Seller shall retrieve all such released confidential information, including any and all copies of the confidential information and all information developed, derived, or created therefrom, upon the earlier of the events set forth above in this Section.

No documents, data, materials or information available to Seller as set forth in this Section 21.3 or produced in whole or in part under this Agreement shall be the subject of an application for copyright by or on behalf of Seller without the prior written consent of Purchaser.

Either party shall be entitled to disclose the terms and conditions of this Agreement and any data or information acquired by it under or pursuant to this Agreement without the prior consent of the other party:

##### to any Affiliate of such party;

##### to any outside consultants or advisers engaged by or on behalf of such party in connection with the Scope of Work or the financing or operation of the Facility and acting in that capacity;

##### to any operator of the Facility, permitted assignees and Lenders;

##### to the extent required by the rules of a relevant and recognized stock exchange;

##### to the extent required by law or pursuant to an order of any court of competent jurisdiction, provided that the original disclosing party is given Notice and adequate time to seek a protective order applicable to the information before it is disclosed;

##### to any insurer under a policy of insurance required to be taken out by either party under the Agreement; or

##### to directors, employees and officers of such party;

##### provided that:

##### the disclosing party determines in good faith that the recipient has a legitimate need to see such data or information; and

##### the recipient has been made aware of and has agreed to be bound by the requirements of this ARTICLE XXI.

## Confidentiality of Purchaser»

.  Purchaser acknowledges that Seller’s business is highly competitive and that Seller’s books, records, documents and technical information concerning its products, equipment, services, processes, procurement procedures, pricing techniques, the names of and other information (such as credit and financial data) concerning Seller’s customers and business affiliates, all comprise confidential business information and trade secrets of Seller which are valuable, special and unique proprietary assets.  Purchaser further acknowledges that protection of Seller’s confidential business information and trade secrets against unauthorized disclosure and use is of critical importance to Seller in maintaining its competitive position.  Accordingly, Purchaser hereby agrees that it will not, at any time during or after the term of this Agreement, make any unauthorized disclosure of any confidential business information or trade secrets of Seller or make any use thereof, except for the benefit of, and on behalf of Seller.  However, Purchaser’s obligation under this Section 21.4 shall not extend to information which is or becomes part of the public domain or is available to the public by publication or otherwise through no wrongful act or omission or noncompliance with this Section by Purchaser or its agents.  The provisions of this Section 21.4 shall survive the termination of this Agreement.  Purchaser agrees and acknowledges that money damages would not be sufficient to remedy  for any breach of this Section 21.4 by Purchaser, and Seller shall be entitled to specific performance and injunctive relief as remedies for such breach or any threatened breach.  Such remedies shall not be deemed the exclusive remedies for a breach of this Section 21.4 by Purchaser but shall be in addition to all remedies available at law or in equity to Seller including recovery of damages from Seller.  For the purposes of this paragraph, the term “Seller” shall also include Affiliates of Seller.

Purchaser shall deliver to Seller all Seller confidential information provided or disclosed to or used or acquired by Purchaser, including all information developed, derived, or created therefrom, or portions thereof, upon the earlier of:

###### the ending of the need for the information relating to the Scope of Work;

###### Seller’s request;

###### the completion of the Scope of Work for which it was provided, disclosed used or acquired; or

###### cancellation, termination or suspension of this Agreement.

Purchaser may retain a single copy of all information upon which its Scope of Work is based for record purposes only.  In the event Purchaser, with Seller’s consent, releases Seller’s confidential information to a third party, Purchaser shall require such third party to enter into a confidentiality agreement similar to this Section 21.4 with Purchaser, and Purchaser shall retrieve all such released confidential information, including any and all copies of the confidential information and all information developed, derived, or created therefrom, upon the earlier of the events set forth above in this Section.

No documents, data, materials or information available to Purchaser as set forth in this Section 21.4 or produced in whole or in part under this Agreement shall be the subject of an application for copyright by or on behalf of Purchaser without the prior written consent of Seller.

# ASSIGNMENT

## Assignment by Seller»

.  This Agreement may be assigned by Seller without Purchaser’s consent to a wholly owned subsidiary of Seller’s ultimate parent company subject to Section 3.7.  This Agreement may not be assigned by Seller to any other entity without the prior written consent of Purchaser, which shall not be unreasonably withheld.  Any assignment by Seller other than as permitted herein shall be void and without force or effect.

## Assignment by Purchaser»

.  This Agreement or any right or obligation contained herein may be assigned, from time to time, by Purchaser without Seller’s consent to the following:

###### an Affiliate of Purchaser;

###### a joint venture, partnership, limited liability company, or other similar entity in which Purchaser or any of its  Affiliates is a venturer, partner or participant with no less than a nineteen and one-half percent (19.5%) equity interest;

###### any Lender or financial institution providing financing to Purchaser, its Affiliates or any permitted assignee in connection with the Equipment or the Facility;

###### any party which is obligated or may be obligated to indemnify Seller from any claims or liabilities arising in connection with this Agreement;

###### any party (1) for which Purchaser or any of its Affiliates has agreed to construct or develop a Facility using the Equipment or (2) to which Purchaser or any of its Affiliates has agreed to convey a power plant project which it has under development; or

###### any contractor or developer which is retained by Purchaser or any of its Affiliates to construct or develop a Facility using the Equipment.

Except for (i) through (vi) above, this Agreement or any rights and/or obligations hereunder may not be assigned by Purchaser to other parties without the prior written consent of Seller which shall not be unreasonably withheld, conditioned or delayed.  Seller agrees to respond to any request for consent within thirty (30) Days following its receipt of such request.  Any failure to respond within the foregoing time period shall be deemed to be a grant by Seller of its consent to the proposed assignment. In the event of assignment to a party as described in (v) or (vi) above, Purchaser will receive a guaranty in a form substantially similar to that attached as Exhibit C-1. The guaranty shall be from a company with a credit rating of BBB+ or better.

In determining whether Purchaser shall be permitted to assign this Agreement, Seller shall only be deemed to be reasonable in withholding its consent if the proposed assignee: (i) does not have substantially the same or better credit quality than Purchaser unless (a) the proposed assignee provides appropriate guaranties, letters of credit or other assurances of payment issued by an entity or person with substantially the same or better credit quality than Purchaser or (b) the assignor agrees to remain liable for all future liability under this Agreement, (ii) is a direct competitor of Seller in the turbine manufacturing business, (iii) is an adverse party to Seller in any material litigation or (iv) if purchasing any Equipment (or its rights thereto), is not purchasing such Equipment (or rights thereto) as part of a transaction in which (x) Purchaser or any of its Affiliates is providing related goods and/or services to such assignee, and (y) Purchaser is not merely acting as a broker or market maker with respect to such Equipment (or rights thereto).  Purchaser shall have the right to assign or pledge, from time to time, all or any portion of its right, title and interest in, to and under the Agreement as collateral for financing of the Facility without Seller’s consent.

When duly assigned in accordance with this Section 22.2 (including, following any collateral assignment, upon foreclosure by any collateral assignee), (i) this Agreement or the rights and/or obligations so assigned shall be binding upon and shall inure to the benefit of the assignee (and all rights and/or obligations so assigned, including, without limitation, any and all warranty rights, shall be assigned to the assignee as if such assignee were an original party hereto), (ii) the assignor shall be irrevocably relieved of and forever discharged from all liability under this Agreement so long as the assignee executes an assumption of such liabilities, and (iii) the Seller shall look only to such assignee for the performance of the obligations so assigned.  Any assignment by Purchaser other than as permitted herein shall be void and without force or effect.

The parties hereto further agree and acknowledge that the foregoing provisions relating to this assignment will only control the assignment of Purchaser’s rights under this Agreement prior to the date upon which the Equipment achieves Takeover.  Following such date, Purchaser shall be permitted, without Seller’s consent, to: (i) assign its rights under this Agreement, (ii) convey any ownership interest that it may have in the Facility and/or (iii) convey any equity interest that it may have in the entity which owns the Facility.

# RELATIONSHIP OF THE PARTIES

## Independent Contractor»

.  Seller undertakes performance of this Agreement as an independent contractor.  Nothing herein shall create a relationship of employer and employee, joint venture, or partnership between Purchaser and Seller, its agents, representatives, employees, Affiliates, Vendors or subcontractors, for any purpose whatsoever.  Nothing herein shall create a relationship of principal and agent between Purchaser and Seller, its agents, employees, representatives or subcontractors.  Neither party shall have the authority to bind or obligate the other in any manner as a result of the relationship created hereby.  Purchaser shall not have the right to control the manner(s) or prescribe the method(s) by which Seller performs this Agreement.  Seller shall be wholly responsible for supervision and the methods of performance.  Seller is entirely and solely responsible for its acts and the acts of its agents, employees, representatives, Affiliates, and Vendors engaged in the performance of this Agreement.  Seller shall provide qualified personnel who shall be and remain solely the employees of Seller, and at no time or in any manner shall said personnel be considered as or deemed to be employees of Purchaser.  Purchaser’s general coordinative efforts, suggestions and procedures with respect to the Scope of Work and Purchaser’s right of inspection, review and observation of the performance of this Agreement shall not make Seller or its employees, employees of Purchaser.

## Responsibilities of Seller as Principal for its Employees»

.  Seller has complete and sole responsibility as a principal for its agents, Vendors and all other hires to perform or assist in performing the Scope of Work.

## Not Used.

# LIENS AND CLAIMS

Seller shall not directly or indirectly create, incur, assume or suffer to be created by it or any Vendors, employees, laborers, materialmen or other suppliers of goods or services any claim, lien, security interest, charge or other encumbrance on the Equipment or any part thereof or interest therein and Seller shall immediately notify Purchaser of the assertion of any lien, claim, security interest or other encumbrance against the Equipment or any part thereof.  Seller shall remove immediately any lien, claim, security interest or other encumbrances against Purchaser, Purchaser’s property, or Purchaser’s Affiliates’ property, or the Equipment arising in favor of Seller or its Vendors or other persons or entities by reason of having provided labor, materials or equipment related to performance of this Agreement and to pay any damages, costs, losses and expenses (including, without limitation, court costs and attorneys’ fees) of whatever kind which Purchaser may incur, be required to pay or be liable for as a result of, in connection with, arising out of, or related to any such lien, claim, security interest or other encumbrance.  In the event of a lien from a Vendor, supplier or subcontractor is levied, Seller shall immediately post a letter of credit, in form and substance acceptable to Purchaser, against such lien.  Upon the failure of Seller promptly to pay or discharge any lien claim, security interest or other encumbrance as required hereby within twenty (20) Days of Notice of the existence thereof from any source, Purchaser may, but shall not be obligated to, pay or discharge such lien claim, security interest or other encumbrance and, upon the payment or discharge thereof, shall be entitled to recover from Seller the amount thereof together with all expenses incurred by Purchaser in connection with such payment or discharge.

# NOTICES AND COMMUNICATIONS

## Notices»

.  Any Notice pursuant to the terms and conditions of this Agreement shall be in writing and either:

##### delivered personally;

##### sent by certified mail, (return receipt requested);

##### sent by a recognized overnight mail or courier service with delivery receipt required; or

##### sent by confirmed facsimile transfer.

| Such Notices shall be sent: If to Seller: | GE Packaged Power, Inc. 2707 North Loop West Houston, Texas 77008 Attn: Lee Johnson Fax: 713-803-0390 |
| --- | --- |
| cc: | Daniel Rowley, Esq. Fax: 713-803-0368 |
| cc: | Michael Storm 16415 Jacinto Port Blvd. Houston, Texas 77015 Fax: 281-864-2116 |
| If to Purchaser: | E-Next Generation LLC c/o Las Vegas Cogeneration II, L.L.C. 3WTC0306 121 SW Salmon Street Portland, Oregon 97204 Attn: Jody Blackburn Fax: 503-464-3740 |

Either party may change its address or the person to be notified by a Notice delivered in accordance with this section.

## Effectiveness of Notices»

.  Notices shall be effective when received  at the address or facsimile number specified.

## Technical Communications»

.  Notwithstanding communications and Notices addresses as set forth in Section 25.1, the parties will route routine and technical communications as follows:

| If to Seller: | GE Packaged Power, Inc. 2707 North Loop West Houston, Texas 77008 Attn: Lee Johnson Fax: 713-869-8365 |
| --- | --- |
| cc: | Michael Storm 16415 Jacinto Port Blvd. Houston, Texas 77015 Fax: 281-864-2116 |
| If to Purchaser: | E-Next Generation LLC c/o Las Vegas Cogeneration II, L.L.C. 3WTC0306 121 SW Salmon Street Portland, Oregon 97204 Attn: W. J. Williams, Jr. Fax: 503-464-3740 |

# ARBITRATION

## Negotiation of Disputes and Disagreements»

.  In the event of any dispute or disagreement arising out of or relating to the implementation or performance of this Agreement, which the parties hereto have been unable to settle or agree upon within a period of thirty (30) Days after the dispute or disagreement arises, each party shall nominate a senior officer of its management to meet at a mutually agreed time and place not later than forty-five (45) Days after the dispute or disagreement has arisen to attempt to resolve such dispute or disagreement.  Should a resolution of such dispute or disagreement not be obtained within fifteen (15) Days after the meeting of senior officers for such purpose, or if such meeting does not take place within sixty (60) Days after the dispute or disagreement has arisen, either party may then by Notice to the other submit the dispute to arbitration in accordance with the provisions of Section 26.2.

## Arbitration Resolution»

.  With respect to arbitration resolution, the parties agree that:

##### In the event of dispute between Purchaser and Seller concerning the interpretation of any provision of this Agreement or the performance of any of the terms of this Agreement such matter or matters in dispute shall be finally settled under the arbitration rules of the American Arbitration Association by three arbitrators, one appointed by each party, and the third, who shall be the chairman, will be selected by the two appointed arbitrators, and failing agreement, by the chairman of the American Arbitration Association.  The language of the arbitration shall be English and the place of the arbitration shall be New York, New York;

##### The decision of the arbitrators shall be final and binding upon the parties;

##### If any dispute to be referred to arbitration under this Agreement raises issues which are, as mutually agreed, substantially the same as or connected with issues raised in any other dispute between the parties (and their successor in title and assigns), then such latter dispute shall constitute a “Related Dispute”;

##### If a Related Dispute has already been referred to arbitration in accordance with arbitration provisions identical (mutatis mutandis) to this clause:

or, if the dispute under this agreement has already been referred to arbitration under this clause, then:

###### the dispute under this Agreement shall be referred to the arbitrators appointed to determine the Related Dispute; and

###### the arbitrators shall have power to join one or more defendants or third parties or consolidate actions as provided by Applicable Law.

## Continuation of Work»

.  Pending final resolution of any dispute, Purchaser and Seller shall continue to fulfill their respective obligations hereunder.

## Not Used.

## Not Used.

# LIMITATION OF LIABILITY

## Maximum Liability»

.  Seller’s maximum aggregate liability for claims by Purchaser arising out of Seller’s performance of this Agreement whether arising from tort (including negligence), breach of contract or any other cause of action, including Liquidated Damages, shall be one hundred percent (100%) of the Maximum Liability Amount; provided, however, that this limitation on liability shall not include any liability for or apply to any of the following categories of liability of Seller:

###### under Section 20.1 (Indemnification);

###### under ARTICLE XXIV (Liens and Claims);

###### under Section 15.2.2 (Intellectual Property Claims); and

###### resulting from the gross negligence or willful misconduct of Seller, its agents, employees or Vendors;

which liabilities shall not be limited.  All liability of Seller with respect to any Unit shall terminate six (6) years after delivery of the Unit to the Delivery Point as determined pursuant to Section 10.2, and all liability of Seller under this Agreement shall terminate six (6) years after the last Unit is made available at the Delivery Point as determined in accordance with Section 10.2.

## Consequential Losses»

.  Except for Liquidated Damages and cancellation fees specifically provided for herein, in no event, whether as a result of breach of contract, breach of warranty, tort liability (including negligence or strict liability), strict liability, or otherwise, and whether arising before or after completion of the Scope of Work, shall either party be liable to the other party for special, indirect, exemplary or consequential losses of any nature whatsoever, including losses or damages caused by reason of unavailability of the Equipment, shutdowns or service interruptions, loss of use, loss of profits or revenue, inventory or use charges, cost of purchased or replacement power, interest charges or cost of capital or claims of a party’s customers.

## Releases Valid in All Events»

.  Except as otherwise specifically set forth herein, releases, disclaimers and limitations on liability expressed herein shall apply even in the event of the negligence, strict liability, fault or breach of contract (including other legal bases of responsibility such as fundamental breach) of the party whose liability is released, disclaimed or limited.

## Seller’s Advice or Assistance»

.  If Seller furnishes Purchaser with advice or assistance which is not related to the Equipment nor required  by this Agreement, the furnishing of such advice or assistance will not subject Seller to any liability whether in contract, warranty, tort (including negligence), strict liability, indemnity or otherwise.

# DRUG AND ALCOHOL-FREE WORKPLACE

The parties desire to provide a safe and productive work environment.  The parties believe that the use, possession and/or distribution of illegal/unauthorized drugs and alcohol presents a serious threat to the safety of employees, visitors and others at the job site, or other premises owned, leased, or occupied by Purchaser.  All Seller’s and Seller’s Vendors’ employees associated with the Scope of Work under this Agreement must agree to compliance with Purchaser’s drug and alcohol policy Number 1200-2, dated September 11, 1995 including:

while on or entering the Site or other premises owned, leased, or occupied by Purchaser, search of personal and professional possessions, including but not limited to automobiles, trucks, briefcases, lunchboxes, and person for illegal drugs.  Failure to consent to such search shall be grounds for immediate removal from the Site or other premises owned, leased, or occupied by Purchaser;

drug testing at any time while on the Site or other premises owned, leased or occupied by Purchaser.  Failure to do so or failing any such test shall be grounds for immediate removal from the Site or other premises owned, leased, or occupied by Purchaser; and

failure of a Seller’s or Vendor’s employee to agree and abide by these requirements will be grounds for immediate removal from the job site or other premises owned, leased, or occupied by Purchaser from any work site or location under the control of Purchaser that is associated with the Scope of Work under this Agreement.

# PROJECT PLANNING AND CONTROLS

Exhibit K sets forth the Project Planning and Control system for tracking the progress of the Scope of Work.  Seller shall establish a program, submit reports and data as set forth therein.

# MISCELLANEOUS

## Validity and Enforceability»

.  The invalidity or unenforceability of any portion or provision of this Agreement shall not affect the validity or enforceability of any other portion or provision.  Any invalid or unenforceable portion or provision shall be deemed severed from this Agreement, and the balance of the Agreement shall be construed and enforced as if the Agreement did not contain such invalid or unenforceable portion or provision.  Notwithstanding the provisions of the preceding sentence, should any term or provision of this Agreement be found invalid by any governmental authority having jurisdiction thereof, the parties shall immediately renegotiate in good faith such term or provision of the Agreement to eliminate such invalidity.

## Governing Law»

.  This Agreement, its interpretation and any disputes relating to, arising out of or connected with this Agreement, shall be governed by the laws of the State of New York, without regard to its conflicts of law provisions (other than Section 5-1401 of the New York General Obligations Law).

## Entire Agreement»

.  This Agreement, and the Exhibits attached hereto constitute the entire agreement between the parties with respect to the subject matter hereof, and there are no oral or written understandings, representations or commitments of any kind, express or implied, not set forth herein.  This Agreement supersedes all prior agreements between the parties with respect to the subject matter hereof.

## Agreement Modification»

.  No oral or written modification of this Agreement either before or after its execution shall be of any force or effect unless such modification is in writing and signed by the party to be bound thereby.

## Waiver»

.  The waiver by any party of any breach or failure to enforce any of the terms, covenants or conditions of this Agreement shall not in any way affect, limit, modify or waive the future enforcement of such terms, covenants or conditions.

## Headings»

.  The headings contained herein are included solely for the convenience of the parties and are not to be used as a basis for interpreting the various sections of this Agreement.

## Third-Party Beneficiaries»

.  The provisions of this Agreement are intended for the sole benefit of Purchaser and Seller, and there are no third-party beneficiaries, other than assignees contemplated by the terms herein.

## Counterparts»

.  This Agreement may be executed in counterparts, each of which when so executed and delivered shall be an original, and all of which, when taken together, shall constitute one and the same instrument.

## Equal Employment Opportunity»

.  To the extent performance if any Scope of Work is performed in the United States, the parties hereto agree that the provisions of Executive Order 11246, as amended, and the Rehabilitation Act of 1973 (Section 503, Public Law 93-112, as amended), the Vietnam Era Veteran’s Readjustment Assistance Act of 1974, as amended (including the provisions of the “Equal Opportunity” clauses), and the regulations promulgated pursuant to the above, are hereby incorporated into this Agreement by reference as if fully set out.

## Cooperation on Site»

.  To the extent Seller is required to perform services on Site it shall cooperate with other contractors on Site so as to coordinate work and schedules.

## Nuclear Material»

.  The Equipment sold hereunder is not intended for application (and shall not be used) in connection with the use or handling of nuclear material or the construction or operation of a nuclear installation.  Purchaser warrants that it shall not use such Equipment for such purposes, or permit others to use such Equipment, while such Equipment is owned by Purchaser, for such purposes unless such use is agreed to in writing by the Seller.  If, in breach of the foregoing, any such use occurs, Seller disclaims all liability for any nuclear or other damage, injury or contamination, and Purchaser shall indemnify Seller against any such liability, whether arising as a result of breach of contract, warranty, tort (including negligence), strict liability, indemnity or otherwise.

[Remainder of page left intentionally blank]

IN WITNESS WHEREOF, the parties have caused this Agreement to be executed as of the date and the year first above written.

AGENT: ENRON NORTH AMERICA CORP. By: Name: Its: ACKNOWLEDGED AND AGREED PURCHASER: E-NEXT GENERATION LLC

By: Wilmington Trust Company, not in its individual capacity, but solely as Manager By: Name: Its:

ACKNOWLEDGED AND AGREED SELLER: GE PACKAGED POWER, INC. By: Name: Its:

EXHIBIT A  BASIS CONDITIONS

Performance Guarantee basis conditions for the Units shall be as set forth below:

| Fuel | Natural Gas | Units of Measure |
| --- | --- | --- |
| Fuel Composition | See Exhibit A-1 |  |
| Load | Base Load |  |
| Ambient Temperature | 75 | F |
| Inlet Air Chiller Status | ON Chilled to 50 | F |
| Elevation | 1920 | Ft. |
| Barometric pressure | 13.77 | psia |
| Ambient Relative Humidity | 22.8 | % |
| Fuel LHV | 20,804 | BTU/lb |
| Fuel Temperature | 77 | F |
| Exhaust Loss (Static) If not in Scope of Work | 13 | In. H20 |
| Inlet Loss (Static) | 5 | In. H20 |
| Generator Power Factor (Lagging) | 0.90 |  |
| Generator Frequency | 60 | Hertz |
| Water Injection (to 30 ppmNOX) | 18,652 | lbs/hr+/-20% |
| Chilled Water Flow Rate | 3,300 | Gpm |
| Chilled Water Glycol Temp* | 47* | F |

* Assumes 20% glycol/water mixture

EXHIBIT A-1 BASIS FUEL

A.	The Guaranteed Levels and Specific Performance Guarantees are based upon the Unit’s operating on natural gas having the following composition:

| Composition by vol. |  |
| --- | --- |
|  | Percent |
| Methane | 94.91 |
| Ethane | 2.90 |
| Propane | 0.38 |
| Butane | 0.11 |
| Pentane | 0.03 |
| Hexane | 0.02 |
| Carbon dioxide | 0.26 |
| Nitrogen | 1.40 |
| Oxygen | 0.00 |
| Total | 100.00 |

Delivery Pressure 		=	  610 psig (minimum)

Delivery Temperature		= 	77 F

The natural gas will contain not more than:

- 0.3 grains of hydrogen sulfide per 100 SCF.

- 20 grains of total sulfur (including the sulfur in any hydrogen sulfide and mercaptan) per 100 SCF.

- 7 pounds of water vapor per million SCF.

EXHIBIT A-2 NOT USED

EXHIBIT A-3  NOT USED

EXHIBIT B  SCOPE OF WORK/SPECIFICATION

1.	SCOPE OF SUPPLY

For a detailed description of the basic and optional scope of supply please refer to the accompanying Product Specification manual.

A.	BASIC SCOPE OF SUPPLY

The following equipment and services are included in the basic scope of supply:

1)	LM6000 gas turbine engine equipped with inlet bellmouth and screen.

2)	Gas fuel system, complete and self-contained on the unit, with connection on the baseplate for customer’s filtered, regulated fuel supply at 630 psig ± 20 psig.

3)	Brush Generator, 13,800 Volt, 60 Hz, 3600 RPM, 71,000 KVA @ 0.85 pf. Low maintenance brushless excitation system suitable for Class 1, Group D, Div 2 areas.  Neutral and line cubicles with CTs, surge protectors and lightning arrestors

4)	I-beam baseplates for turbine, generator and unit mounted accessories.  The baseplate will be drilled and doweled for field re-alignment.

5)	Acoustic enclosure for gas turbine and generator.  Redundant ventilation systems, AC internal lighting and DC emergency lighting.

6)	Multi stage air inlet filtration system for both gas turbine and generator, including weather hoods, inlet screen, pre-filter, final barrier filter, intake silencer, and standard ducting to plenum chamber.  Filterhouse ladders and platforms are included.  The inlet silencer shall be designed for noise attenuation to 85 dBA at 3 feet.

7)	Electro-hydraulic start system.

8)	Separate lube oil systems for gas turbine and generator, including duplex filters, duplex shell and tube coolers, stainless steel piping, and stainless steel reservoirs.

9)	Axial-exhaust system with discharge flange for customer connection.

10)	Unit control panel for indoor mounting in a controlled environment, including microprocessor fuel management and sequencing system, generator metering, Bentley Nevada vibration monitoring, CRT annunciation of alarms and shutdowns, and Ethernet connection for data output to customer’s control systems.  Beckwith integrated generator protection system.

11)	I/O cubicle mounted on gas turbine enclosure.

12)	24V DC control system battery with dual battery chargers.

13)	Fire and gas detection and extinguishing system, serving both turbine and generator compartments, complete with 24V DC battery and charger.

14)	“On-line” water wash system and “soak wash” system.

15)	Generator factory testing to IEEE or IEC standards.  Gas turbine performance test by SSEP at SSEP factory (Houston).

16)	Six sets of drawing and data packages, O & M manuals.  Six sets of drawing and data packages and O&M/Installation Manuals.

17)	Training course for up to 10 customer personnel.

18)	Inlet chiller coil

19)	Enchanced Sprint power augmentation system including main GT skid piping/tubing, injection pump and metering system.

20)	Winterization package to - 10F

21)	Nox water injection skid including main GT skid piping/tubing, injection pump and metering system.

22)	Special tools for installation and removal of the gas turbine.

23)	Technical Site Supervision - 240 man-hours per Unit

24)	Packing and crating for domestic shipment

25)	Special lifting devices for Unit installation (to be returned to Seller).

26)	Power system stabilizer (price includes field installation)

EXHIBIT B-1  SPECIFICATION FOR LM6000 SPRINT™
GAS TURBINE GENERATOR SET

- 1.0	GENERAL

This specification defines the details of the design, manufacture and testing of the LM6000 Enhanced SPRINT™ gas turbine generator set (Unit) including all accessories described herein.

The Unit will be designed to operate in combined cycle power plant facilities to be built by others, and will be capable of operating in an isochronous mode to satisfy plant electric loads or synchronized to the utility for power export.

- 1.1	Equipment and Services By Seller

1.1.1	Gas Turbine

1.1.2	Air Cooled Generator, brushless exciter and voltage regulator

1.1.3	Coupling and Coupling Guard

1.1.4	Structural steel baseplates for gas turbine, generator and unit mounted accessories.  Baseplates will be drilled and doweled for simplified field re-alignment.

1.1.5	Lube Oil System for Gas Turbine.

1.1.6	Lube Oil System for Generator

1.1.7	On-line and Crank Soak Waterwash System for Gas Turbine

1.1.8	Multi-Stage Inlet Air Filter System with Chiller Coil

1.1.9	Electrohydraulic Start System

1.1.10	Ladders, Stairs, and Platforms for Filter House Access

1.1.11	Acoustic Enclosure, Winterization and Ventilation System for Rotating Equipment Compartments

1.1.12	Inlet Silencer for Noise Attenuation to 85 dBA at 3 feet

1.1.13	Gaseous Fuel System

1.1.14	Water Injection Pumps and Metering Systems for NOx Control

1.1.15	Enhanced SPRINTTM power augmentation system including main GT skid piping/tubing, injection pump, and metering system

1.1.16	Unit Control Panel Designed for Indoor Installation

1.1.17	 Beckwith Integrated Generator Protection System

1.1.18	Bently Nevada 3500 Vibration Monitoring System

1.1.19	Fire and Gas Detection System

1.1.20	CO2 Fire Extinguishing System

1.1.21	Factory Testing of Turbine, Generator, and Generator Sets

1.1.22	Training

1.1.23	Operating and Maintenance Manuals

1.1.24	Installation Manuals

1.1.25	Special Tools for Installation and Removal of Gas Turbine

1.1.26	Packing and Crating for Domestic Shipment

1.1.27	Drawings

1.1.28	Special Lifting Devices for Unit Installation (to be returned to Seller)

1.2	Options Offered By Seller: The following equipment has been offered as optional and is not included with the basic Unit scope of supply.

1.2.1	Transport to the job site

1.2.2	Simple cycle exhaust stack with EPA ports, platforms and ladders

1.2.3	35’ X 14’ Modular Control Room

1.2.4	Inlet air chilling module

1.2.5	Fired, fuel gas, heating module

1.2.6	Unit 480 V Motor Control Center

1.2.7	NEMA 3R 15 kV Switchgear

1.2.8	Dual Fuel Option (transfer fuels at reduced load, non-cooled CDP)

1.2.9	O&M Manuals on CD ROM

1.2.10	Low ambient temperature anti-icing system

1.2.11	Generator inlet air cooling system

- 1.3	Equipment and Services by Purchaser

- The Purchaser will provide the following equipment, materials, and services.

1.3.1	Unloading, indoor and outdoor storage (as required) and installation labor.

1.3.2	Foundations, anchor bolt hardware, grouting forms, and grouting.

1.3.3	Fuel and water forwarding systems including piping to flange connections at Vendor's baseplate.

1.3.4	Lubricants and fluids (Operating and Commissioning)

1.3.5	High voltage cables and/or bus duct from the generator terminals.

1.3.6	Electric utility interconnect including the required circuit breakers and protective devices.

1.3.7	Interconnection piping, conduit, and wiring between the unit control panel, main unit termination boxes, auxiliary system modules, and motor control center.

1.3.8	Bolts, nuts, washers, and gaskets required at terminal points.

- 2.0	REFERENCED DOCUMENTS

The applicable sections of the following US and ISO Codes and Standards will be considered as relevant Standards for gas turbine equipment. The designs and procedures will be compliant with applicable sections of the following:

AGMA 421	Standard Practice for High Speed Helical and Herringbone Gear Units (Used for the accessory gear except for service factor.)

- ANSI/AFBMA

Std 9			Loading Ratings and Fatigue Life for Ball Bearings.

Std 11			Load Ratings and Fatigue Life for Roller Bearings.

ASCE-7	Minimum Design Loads for Buildings and Other Structures	(Used for Snow Loads)

ANSI B1.1	Unified Inch Screw Threads (S&S Energy Products complies at the customer's connection)

ANSI B1.20.1	Pipe Threads

ANSI B16.5		Steel Pipe Flanges and Flanged Fittings

ANSI B16.9		Factory - Made Wrought Steel Butt Welding Fittings

ANSI B16.21	Non-metallic Flat Gaskets for Pipe Flanges.  (Spiral-wound gaskets per API 601 may be used, particularly in turbine compartment piping.)

ANSI B31.1		Pressure Piping and gas turbine piping systems comply.

ANSI B133.2		Basic Gas Turbine. Complies, with the exception of paragraph:

8.5	Loose items such as jackscrews and eyebolts are not furnished.  Provisions for use of such items are not included in the design.

ANSI B133.3	Gas Turbine Auxiliary Equipment.  Auxiliary equipment will fully comply with design portions only.  The Seller’s recommended lube oil flushing procedure will be implemented.  Atomizing air receiver is not applicable.

ANSI B133.4			Gas Turbine Controls and Protection Systems

ANSI B133.5			Gas Turbine Electrical Equipment

ANSI B133.8			Gas Turbine Installation Sound Emissions

ANSI C37.90			Relays Associated with Electric Power Apparatus

ANSI C37.90.1		Guide for Surge Withstand Capability (SWS) Tests

ANSI C50.10			General Requirements for Synchronous Machines

ANSI C50.13			Requirements for Cylindrical Rotor Synchronous Generators

ANSI C50.14	Requirements for Combustion Gas Turbine Driven Cylindrical Rotor Synchronous Generators (The GTG does not provide a peak reserve rating.  Not all of the prototype tests indicated in Table 2 have necessarily been conducted.)

ANSI C57.94	American Standard, Guide for Installation and Maintenance of Dry Type Transformers

ANSI C83.16			Relays

ANSI S1.2			Method for the Physical Measurement of Sound

ANSI S1.4			Specification for Sound Level Meters

ANSI S1.13			Method for the Measurement of Sound Pressure Levels

ANSI/ASHRAE 52.1-1992	Gravimetric and Dust Spot Procedures for Testing Air-cleaning Devices Used in General Ventilation for Removing Particulate Matter

ANSI/IEEE C37.2	Electrical Power System Device Function Numbers (The Unit complies with respect to device designations except that in a few cases device numbers had to be modified or added for this application.)

ANSI/IEEE 100	IEEE Standard Dictionary of Electrical and Electronics Terms

ANSI/NEMA MG1		Motors and Generators

ANSI/NEMA MG2	Safety Standard for Construction and Guide for Selection, Installation and Use of Electric Motor and Generators

ANSI/NFPA 12		Carbon Dioxide Extinguishing Systems

ANSI/NFPA 70	National Electrical Code (Electrical components will be designed to meet the intent of this Code for Class 1, Group D, Div. 2, Hazardous area classification where appropriate.).

API 614	Lubrication, Shaft-Sealing, and Control - Oil Systems for Special - Purpose Applications

API 616	Gas Turbine for Refinery Services

API 650	Storage Tanks

API 670			Vibration Monitoring Systems

API 678			Accelerometer - Based Vibration Monitoring System

API RP11PGT			Packaged Combustion Gas Turbines

ASME PTC22			Gas Turbine Power Plants - Performance Test Codes

ASME Section VIII		ASME Boiler and Pressure Vessel Code

ASME Section IX		ASME Boiler and Pressure Vessel Code

AWS D1.1			American Welding Specification

EIA RS-232	Interface between Data Terminal Equipment and Data Communication Equipment Employing Serial Binary Interchange

IEC 34.1			Rotating Electrical Machines - Rating and Performance

IEC 34.3			Rotating Electrical Machines - Turbine Type Synchronous

Machines

IEEE Std. 421	IEEE Standard Criteria and Definitions for Excitation Systems for Synchronous Machines

JIC				Hydraulic Standards for Industrial Equipment

UBC	Uniform Building Code (Used for wind loads and seismic design)

3.0	TECHNICAL REQUIREMENTS

- 3.1	Operation

The Unit shall be capable of satisfactory operation from 0% load to 100% load at the Site Design Conditions.  During startup, the turbine shall be capable of idling unsynchronized for up to 60 minutes.  The Unit shall be capable of starting, synchronizing and loading within 10 minutes of dispatch from a ready to start condition.

- 3.2	Performance Data and Guarantees

The Seller guarantees the kW output, heat rate, NOx, CO, PM10 and UHC emissions, and noise emissions of the Unit according to the Agreement.

Seller shall provide additional performance data to show how changes in ambient temperature and inlet/exhaust losses affect heat rate, power output, exhaust mass flow, and exhaust gas temperature.

- 3.3	Site Design Conditions

- 3.3.1	Climatic Conditions

The Unit and related equipment furnished by the Seller shall be designed for proper operation with the following climatic conditions:

-	Maximum wind velocity of 100 mph

-	Ambient temperature range of 44 to +105F*

-	Relative humidity of 15% to 100%

*Lower-operating temperatures can be realized with the addition of an anti-ice system

- 3.3.2	Seismic Conditions

The gas turbine structure and attachments shall be designed in accordance with UBC 1997, Seismic Zone 4.

- 3.4	Surface Temperatures

Surface temperature of components that can be readily accessed during normal operation shall not exceed 140F without a barrier to protect personnel.  The engine compartment interior and roof are excluded from this requirement.

- 4.0	LM6000 SPRINT GAS TURBINE GENERATOR SET

- 4.1	Gas Turbine

Major Components of the LM6000 turbine are:

-	5-stage low pressure compressor (LPC)

-	14-stage variable geometry high pressure compressor (HPC)

-	Annular combustor

-	2-stage air cooled high pressure turbine (HPT)

-	5-stage low pressure turbine (LPT)

-	Accessory Drive Gear Box

The LPC will be driven through a concentric drive shaft by the 5-stage LPT, forming the low-pressure rotor.  The high-pressure rotor will be formed by the 14-stage HPC, driven by the 2-stage HPT.  The high pressure "core" will be formed by the HPC, combustor and HPT section.

The Unit uses the Low-Pressure Turbine (LPT) powers the output shaft.  Driving with the LPT improves fuel efficiency and allows the turbine to be directly coupled to the electrical generator rotating at 3600 RPM.  The gas turbine drives the generator through a flexible dry type coupling connected to the front, or "cold", end of the LPC shaft.

- 4.2	Turbine Cycle

The gas turbine cycle begins with air entering the inlet plenum, where it is directed through inlet guide vanes into the LPC.  The LPC compresses the air by a ratio of approximately 2.4:1.  Air leaving the LPC is directed into the HPC.  Variable bleed valves (VBV) in the flow passage between the two compressors regulate the airflow entering the HPC during idle, low power operation, and transient load conditions.  To further control the airflow, the HPC will be also equipped with variable pitch inlet guide vanes and stator vanes.

The HPC compresses the air by a ratio of approximately 12:1.  The HPC discharge will then be directed into the annular combustor section where it mixes with the fuel from the 30 fuel nozzles.  One igniter initially ignites the fuel/air mixture.  When combustion is self-sustaining, the igniter will then be turned off.  The hot combustion gases will then be directed into the HPT, which consequently drives the HPC.  The gas then expands further through the LPT, which drives the LPC.  The flanged LPC shaft drives the electric generator.

- 4.3	Inlet Section

The air intake section of the gas turbine consists of an annular flow section to direct the air stream into the low-pressure compressor.

- 4.4	Low Pressure Compressor

The low-pressure compressor (LPC) will be a 5-stage axial flow compressor with 2.4:1 pressure ratio.   At low power settings and during large power reduction transients modulating bleed ports control LPC bypass flow to assure adequate LPC stall margins.

- 4.5	High Pressure Compressor

The high-pressure compressor (HPC) will be a 14-stage design. Variable stators in stages  through 5 provide stall-free operation and high efficiency throughout the starting and operating range.  The stator geometry of stages 6-14 will be fixed.

The HP compressor casing will be split horizontally to allow ready access to the stator vanes and rotor blades for inspection or replacement.

- 4.6	Combustion System

The gas generator will be furnished with 30 externally mounted fuel nozzles for the natural gas fuel system requirements.  For NOx reduction, water will also be injected into the fuel nozzles through a separate manifold.

The Unit uses a high performance annular combustor with low exit temperature pattern, low-pressure loss and high combustion efficiency at all operating conditions.

- 4.7	High Pressure Turbine

The high-pressure turbine (HPT) will be an air cooled, 2-stage design with demonstrated high efficiency.

The HPT will be designed to be easily maintainable in service.  Significant maintainability features include:

-	Stage 1 nozzle assembly will be removable as a unit.

-	Stage 2 nozzle assembly will be removable as a unit.

-	Turbine blades will be individually replaceable.

Stage 1 and 2 shrouds will be segmented and designed for removal and 	replacement in the stator assembly.

The 2-stage high-pressure turbine will be assembled on the same shaft as the 14-stage high-pressure compressor.

Compressor discharge air will be used to cool the rotor structure and both blade stages.  The cooling air flows through the shaft and the bore of the stage 1 disk, where it separates to supply stage 1 and 2 blades.  Compressor discharge air and bleed air will be used to cool the HPT stator.

- 4.8	Low Pressure Turbine

A 5-stage low-pressure turbine receives the outlet flow from the HP turbine.  The LP turbine will be mounted on a common shaft with the 5-stage LP compressor.  This shaft will be concentric to the HP rotor.

- 4.9	Gas Turbine Support Structures

- Three frames provide support for the LP and HP rotors.

- Front Frame

The front frame will be a major engine structure that provides support for the LPC rotor and the forward end of the HPC rotor.  The frame also forms an airflow path between the outlet of the LPC and the inlet of the HPC.  Engine front mount provisions will be made off the front frame.

The front frame contains the engine "A" sump that includes a thrust and a radial bearing for support of the LPC rotor and a radial bearing which supports the forward end of the HPC rotor.  Lubrication oil, supply and scavenge, lines for the "A" sump will be routed inside the frame struts.  The engine inlet gearbox will be located in the "A" sump, with the radial drive shaft extending out through the strut located at the six o'clock position.

- Compressor Rear Frame

The compressor rear frame consists of an outer case, 10 struts and the "B-C" sump housing.  The outer case supports the combustor and 30 fuel nozzles.  The hub provides support for both a thrust bearing and a radial bearing to support the mid section of the HP rotor system.

- Turbine Rear Frame

The turbine rear frame provides the aft connection of the gas turbine to the base through the rear engine mounts and is the structure supporting the "D-E" sump, and the LPT stator case.

- 4.10	Accessory Drive System

The hydraulic starter, lube and scavenge pump, variable geometry hydraulic pump, and other accessories will be mounted and driven from the accessory gearbox.  The accessory gearbox, located below the front HPC casing at the six o'clock position on the air collector, will be driven from the transfer gearbox through a short horizontal shaft.  The transfer gearbox will be driven by the high-pressure rotor system.

- 4.11	Variable Geometry (VG) Control System

The variable geometry system consists of a positive displacement hydraulic pump, with torque motor positioned hydraulic servos for porting fluid at regulated pressure, two HPC variable stator vane actuators and six LPC bleed valve actuators.  Electrical inputs from the SSEP controls operate three separate servo valves mounted on the gas turbine.  The variable output pressures from these servos position the low-pressure compressor variables bleed valves (VBV) and the high-pressure compressor variable stator vanes (VSV).  Position feedback of the moving elements will be provided by linear variable differential transformers (LVDT) integral with the actuators.

- 4.12	Gas Generator Overall Features

Included are modular LPC assembly, fabricated compressor front frame and air collector, modular HPC and HPT, fabricated compressor rear frame and turbine mid-frame and modular LPT.  Each rotating mass will be supported by roller bearings, and rotor axial thrust loads are carried by ball bearings.  Labyrinth type, long-life seals will be used in the bearing sumps.  Each sump will be individually scavenged.  A common line to an air/oil separator vents the “A”, “B-C” and “D-E” sumps.

- 4.13	Starting Motor

A hydraulic motor will be installed on the accessory gearbox to provide starting torque to the gas turbine.  A 200 HP (150 kW) electric motor and hydraulic pump mounted on the auxiliary equipment module provide pressured hydraulic oil to power the hydraulic starter motor.  (See Section 9).

- 4.14	Fuel Systems

The Purchaser will supply fuel in accordance with GE M&IAD Spec MID-TD-0000-1 at the baseplate connection.  The components downstream of the baseplate connection are supplied by the Seller.

- 4.15	Lubrication System

A complete lubrication system for the gas turbine will be furnished as described in Section 10.  The lube oil system includes mechanical pump, duplex filters, pressure and temperature instrumentation, 304 stainless steel reservoir and a 304 stainless steel piping system.  The gas turbine uses rolling element dry sump bearings.  There will be no need for auxiliary lube oil pumps.  Bearing sumps will be sealed with knife-edge seals and pressurized with compressor bleed air.  Oil will be removed from the seal air by an air-oil coalescer mounted on the roof skid.

- 4.16	Ignition System

The ignition system includes one ignition unit, which converts the 115 V, 60 Hz power to high voltage, and includes  a high tension lead and igniter.  The ignition system will be used only during starting and will be turned off once the engine reaches idle speed.

- 4.17	Borescope Inspection Provisions

Ports and removable covers in the casing permit borescope inspection of the blades and vanes of the low pressure compressor, the high pressure compressor, the high pressure turbine, the low pressure turbine, combustor, frames, and accessory gearbox.

- 4.18	Turbine Mounted Instruments

These devices will be incorporated into an electronic control system furnished.  Details of the control system are described in Section 13.

The gas turbine will be equipped with the following sensors:

Qty					Sensor

2	Speed sensors (XN25) high-pressure rotor - magnetic pickup type - located on 	accessory gearbox.

2	Speed sensors (XNSD) LP turbine rotor - magnetic pickup type - 			located in the LP turbine rear frame. .

1	Low-pressure turbine inlet temperature (T48) sensor system - chromel alumel 	thermocouples - located on LPT case.

2	Accelerometers - located on the gas turbine, compressor rear frame, and LPT rear 	frame.

7	Resistance Temperature Detectors (RTD) will be provided to measure and 	monitor the temperature of lube oil in the Transfer Gearbox, the B-C sump, D-E 	sump scavenge lines, the accessory gearbox and the lube supply line to the gas 	turbine.

1	Low-pressure turbine inlet pressure probe (P48) - total pressure - located on the 	low-pressure turbine case. .

1	Low-pressure compressor inlet temperature and total pressure probe (T2, P2) - 		located on the IGV case.  The probe is a dual element RTD (two separate RTDs in 	one probe).  The probe also includes a P2 (total pressure) sensing port.

1	High-pressure compressor inlet temperature and total pressure probe (T25, P25) - 	located on front frame.  The probe will be a dual element RTD (two separate 	RTDs in one probe).  The probe also includes a P25 (total pressure) sensing port.

2	Variable stator vane (VSV) position sensors - linearly variable differential 	transformer (LVDT) - located on the actuators.

2	Variable bleed valve (VBV) position sensors - linearly variable differential 	transformer (LVDT) - located on the actuators.

1	High-pressure compressor discharge temperature (T3) sensor - A dual element 	chromel - alumel thermocouple mounted on the compressor rear frame.

3	Remote indicating chip detectors, located in scavenge oil return lines.

2	Liquid manifold temperature sensors will be provided.  Type K thermocouples 	(furnished on dual-fuel or gas-fuel-with-water-injection units only).

- 4.19     ENHANCED SPRINT System

The system will utilize demineralized water as a sprayed “inter-cooler in-between the low pressure and high pressure compressors.  This “inter-cooling” lowers the compressor discharge temperature (T3).  The T3 temperature will typically be the limiting engine control point at higher ambient temperatures.  Cooling the T3 allows the unit to operate at another controlling limit, which will allow more fuel to be injected into the engine at a given engine inlet temperature (T2).  The water flow rates will vary depending on the (T2) conditions.  The maximum flow rate should not exceed 30 GPM of demineralized water.  The system will be programmed to operate automatically after being enabled.  It will shut itself down if the load falls below a pre-determined minimum loading, and if the T2 conditions fall below the point where SPRINT is no longer useful.

- 4.20 	Water Injection System

The water injection system consists of inlet strainer, valves, piping controls and a duplex or two simplex boost pump skid(s) to boost water pressure to the required pressure.  Purchaser must supply demineralized water to the customer connection located on the water injection boost skid.  A minimum supply pressure of 5 psig will be available during gas fuel operation at a maximum rate of 55 gpm.  NOx water cleanliness will satisfy GE M&IAD Spec MID-TD-0000-3.

5.0	GENERATOR AND AUXILIARIES

- 5.1	Generator Design

The generator will be an air cooled, self-ventilated, cylindrical rotor machine.  It will be a two pole synchronous generator with a brushless excitation system and a permanent magnet pilot exciter.  The generator utilizes an open, drip-proof design and will be packaged in a housing which reduces average noise levels to 85 dB(A) at 3 feet from unit and 5 feet above grade.  The rotor will be supported by two split sleeve bearings, which will be lubricated with a pressurized mineral oil system.  The generator has a design life of 25-30 years, utilizes Class F insulation and will be sized to operate with Class B temperature rise.  The generator will be capable of absorbing the site rated power output of the gas turbine for baseload operation throughout the entire ambient temperature range of the application.

The generator will be capable of a 110% power overload for 2 hours out of every 24 hours of operation with no loss of operating life.  The generator will also be capable of withstanding a 30% overload current for 1 minute.

The generator and turbine shall be capable of operating at full output at plus/minus 3-percent frequency deviation continuously.

- 5.2	Brushless Excitation System

A brushless exciter will be furnished with each generator.  The brushless exciter will be the direct connected, rotating type, electrically and mechanically coordinated with the generator to insure a reliable generating unit.  The exciter will be powered by a Permanent-Magnet-Generator (PMG) mounted on the shaft of the main generator.

A rotating, full-wave bridge rectifier converts the AC output of the exciter to DC, which will be fed directly into the generator field.  The voltage regulator controls the output of the exciter.

- 5.3	Voltage Regulator System

The generator will be furnished with an auto-manual electronic voltage regulator system.  The voltage regulator system will be rack-mounted in the unit control panel and maintains generator output voltage within +0.5% under steady state operating conditions.  The voltage regulator utilizes single phase sensing circuitry and includes:

-	diode failure alarm			-	under excitation limiter

-	flux limiter				-	auto follower & null balance

-	over-excitation limiter			-	auto transfer to manual control

-	volts per Hz control

- 5.4	Neutral Cubicle and Line Side Cubicle

Separate terminal boxes are provided on opposite sides of the generator to house the neutral and line terminals.

- 5.4.1	Line Side Cubicle

The line side cubicle will be the Purchaser's connection point to the high voltage output of the generator.  The cubicle bolts to the right hand side of the generator enclosure, as viewed from the exciter end.  It contains 3-phase power lugs, lightning arrestors and surge protectors and bus work.  The cubicle will be adequately sized to accommodate stress cones supplied by others.  The line compartment, provided by the Seller as an option, shall contain 6 CTs for generator protective relaying in Public Utility applications.

- 5.4.2	Neutral Cubicle

The neutral cubicle will be the Purchaser's connection point for grounding the generator.  The cubicle bolts to the left-hand side of the generator enclosure, as viewed from the exciter end.  Within the cubicle the three phases will be brought together to a "Y" point with bus bar.  The "Y" point will be connected to a high impedance grounding system* furnished by the Seller.  The grounding system includes a transformer and a secondary grounding resistor in an enclosure mounted on the neutral cubicle.

The neutral cubicle contains 7 CTs supplied by the Seller; 3 for metering, 3 for protective relaying, and 1 for cross current compensation.

- 5.5	Generator Accessories

- 5.5.1	Stator Temperature Detectors

A minimum of six platinum resistance temperature detectors (two per phase) will be embedded in the stator windings.  The RTD's will be the 100-ohm at 32F type.

- 5.5.2	Bearing Temperature Detectors

An embedded RTD will be provided for each radial bearing.  In addition, an RTD and local thermometer will be furnished in the drain line of each bearing.  Monitoring and temperature indications will be provided at the unit control panel.

- 5.5.3	Space Heaters

The generator will be equipped with space heaters located inside of the generator enclosure.  The space heaters will have adequate capacity to prevent condensation of moisture within the generator enclosure when the unit is not operating.  The space heaters will be designed for operation on a three phase, 480 VAC, 60 Hz system.  The space heater will be automatically switched ON/OFF by the unit control panel and a contactor in the Unit motor control center.

- 5.5.4	Vibration Detectors

Two Bently Nevada vibration detectors will be mounted 90 degrees apart at each radial bearing (Total 4).  The proximeters and cables will be wired to the main termination box in the generator compartment.  Monitoring equipment will be provided in the unit control panel.

- 5.5.5	Ground Fault Monitoring

Continuous electronic monitoring of the generator rotor winding and its connections will be provided.  Indication of a ground fault will be provided at the unit control panel.

6.0	AIR INLET SYSTEM - MULTI STAGE DESIGN

The air inlet system:

1.	Maintains clean airflow required by the gas turbine, generator cooling, and 	enclosure ventilation.

2.	Minimizes frequency of high efficiency filter replacement.

3.	Permits the inclusion of optional equipment including inlet conditioning and anti-	ice protection.

- 6.1	Filtration Specifications

The Unit air inlet system has a three-stage filter which removes 99.9 percent of all particles 5.0 micron and above under the specified environmental conditions.  The filter is not designed to protect the gas turbine against salt laden air.

Total AirFlow:			335,000 SCFM

Engine Combustion Air 		230,000 SCFM

Ventilation Air for Turbine &		105,000 SCFM

Generator Compartments

- 6.2	Filter House Construction

6.2.1	General Arrangement

The filter house will be a three-section unit, assembled at the job-site.  The left side and right side filter house sections contain the filtering elements.  The center section will be a fabricated plenum with a bottom outlet for the filtered air flow.  Weather hoods shield the filter sections from driving rain or hail.  A pre-designed transition duct with expansion joint mates the filter to the engine enclosure.  Ladders and platforms will be furnished to provide access to the service doors at each filter section.  Internal walkways and lighting will be provided within each filter section to simplify operator changeout of filter elements.  The filtered airflow will be divided into two air streams by ducting within the filter assembly, providing:

-	Combustion air for the gas turbine

-	Generator Cooling Air

-	Ventilation air flow for the generator and turbine compartment

6.2.2	Material

The filter housing will be constructed of steel plate.  Two (2) coats of protective paint will be applied to the exterior and interior carbon steel surfaces.

6.3	Filtration System Details

- 6.3.1	Inlet Screen

The inlet air passes first through a wire mesh screen that removes trash, paper, and other loose objects.

6.3.2	Prefilter

Next, the air stream passes through a replaceable pre-filter.  The pre-filter removes coarse particles and extends the life of the high efficiency barrier filter.

6.3.3	Barrier Filter

The final filtration stage consists of a high efficiency barrier filter with an extended surface area.  The replaceable cylindrical canister filter elements will be rugged, provide high dirt-holding capacity and have low pressure drop.

6.3.4	Restriction Indication

A pressure switch will be provided for alarm and shutdown based on the filter system pressure drop:

- New and Clean (Typical)			4" H2O (9.9 mbar)

- Alarm					5" H2O (12.4 mbar)

- Shutdown					8" H2O (19.8 mbar)

- 6.4	Air Inlet Anti-Ice

Sixteen row heating/chilling coils will be installed in the combustion air stream located in the air filter house in which the customer can circulate a hot water/glycol solution to heat the inlet air of the gas turbine.  This protects against ice formation on the inlet bellmouth when temperatures drop below 45F with relatively high humidity.  Ice entering the inlet of the gas turbine has potential to cause catastrophic damage.  The heating coils will be built with copper tubes and aluminum fins. The piping and equipment external to the coils, including valves, drains and controls will be provided by others.

- 6.5	High Performance Chilling Coils

This coil will be sized to lower the temperature of the inlet combustion air to 50F, from a 95F dry bulb and 74F wet bulb.

Cold water supply, and piping, fittings, valves and controls exterior to the exchanger will be furnished by others unless the packaged chiller option is required as outlined in section 6.6 or heater package in section 6.7.

- 6.6	Turbine Inlet Air Chiller Package (Optional Feature)

The seller offers a 2200 Ton single lift inlet chiller module measuring 14’W x 45’L x 12’H with an estimated operating weight at 114,000 lbs. Redundant pumps for the condenser and evaporator will be included as well as controls, switchgear, valves, piping, and insulation. For further benefit, the seller can supply as an option, a Marley Cooling Tower designed around the chiller module.

A complete indoor motor control panel containing all the electrical switchgear, breakers, and power distribution system is located inside the acoustically treated module. The Purchaser will provide one 480 volt and one 4160 volt feed to the chiller package.

- 6.7	Anti-Ice Heater (Optional Feature)

Depending on site conditions, this module will house between five and nine, one million BTUH input Natural Gas Fired Boilers.  This option allows for the advantage of utilizing the chilled water pumps already located on the chiller module.  A small stream of water/glycol will be taken out of the chiller water loop, heated, and then mixed downstream to give a minimum five degree temperature rise in the heater coil, with a corresponding combustion air inlet temperature increase of 10 degrees. Materials for integration with the Chilling module include, pumping, control, and auto changeover from inlet cooling to heating.

Similar to the chiller module, the anti-ice heater includes the required electrical, lighting, starters, controls, and disconnects for a single point 480V, 3 phase, 60 hertz power connection.

7.0		ENCLOSURE, VENTILATION AND NOISE CONTROL

- 7.1	Enclosure

The unit enclosure will be designed for outdoor installation and wind loads of 100 mph.  It will be divided into turbine and generator compartments by a bulkhead.  The inlet volute will be an enclosed structure located in the turbine compartment.   The turbine exhaust flows axially, out a flanged connection at one end of the enclosure.  Access doors and air conditioning (ac) will be located in each compartment. The engine compartment contains an integral overhead bridge crane to facilitate engine removal.

The enclosure walls utilize a sandwich construction filled with high-density fiberglass insulation blankets.  The inner wall panel will be fabricated from perforated 18-gauge stainless steel.  The outer wall panel will be 14-gauge cold rolled carbon steel.  The turbine and generator compartment walls will be supported by a structural steel framework and will withstand the internal pressure developed by the fire extinguishing system.  The enclosure hinges, latches and mounting hardware are stainless steel or chrome plated.

- 7.2	Ventilation

The ventilation system removes heat from the turbine and generator compartments and reduces the hazards in the event of a fuel system failure.  Both the engine compartment and generator compartment will be fully ventilated by redundant fans.  Ventilation air will be filtered to the same quality as the combustion air for the gas turbine.

7.2.1	Gas Turbine Compartment Ventilation

Ventilation air enters the compartment at the bottom front center of the room.  The ventilation system maintains airflow of 60,000 SCFM through the gas turbine compartment.  During normal operation, 1 vent fan provides sufficient airflow for ventilation purposes.  If engine compartment temperatures reach 140 F, the standby fan will assist until temperatures are below the high temperature alarm conditions.  The ventilation system maintains a negative pressure in the turbine compartment.

7.2.2	Generator Compartment Ventilation

Duplex fans provide ventilation to generator compartment and cooling air to the generator.  During normal operation conditions, a single ventilation fan provides the 45,000 SCFM flow required for ventilation and cooling with the second fan on standby.  The generator compartment will be classified as a non-hazardous enclosure because a positive pressure is maintained.

7.2.3	Noise Control

The equipment enclosure and air inlet silencer reduce near field noise to 85 dB(A) at 3 ft. from the enclosure and 5 ft. above grade.

8.0		TURBINE EXHAUST SYSTEM (Optional Feature)

The Unit exhausts through an axial exhaust outlet at the end of the turbine enclosure to facilitate in-line mounting of an optional simple cycle exhaust stack.  The stack assembly will consist of expansion joint, 85 dBA silencer, 90° elbow and 45-ft. stack.  An optional 15’ extension may be available separately.  For requirements greater than 60’, a separate reinforced assembly will be required.

The stack shall include EPA emissions ports with access ladders and platforms per recognized “Good Engineering Practice” design.

9.0	STARTING & WATER WASH SYSTEMS AND AUXILIARY EQUIPMENT MODULE

The gas turbine will be started by an electro-hydraulic system that includes:

-	An electric motor-driven hydraulic pump mounted on the auxiliary equipment 	module.

-	A hydraulic motor mounted on the turbine auxiliary gearbox, which rotates the 	HPC.

-	Controls, valves, filters, interconnect hoses and heat exchanger.

- The same system cranks the turbine for purging, water washing, and cool down.

- 9.1	Starting System Operation

- To start the gas turbine, the hydraulic motor must

-	rotate the HPC to purge the engine

-	accelerate the HPC to ignition speed

-	continue acceleration to self-sustaining speed

The starter accelerates the HPC to 2,200 RPM, and cranks at this speed for two minutes to purge the exhaust stream for simple cycle applications.  The purge cycle is a safety measure performed at the onset of each start routine.

After completing the purge cycle, the HPC slows to a light-off speed of 1,700 RPM.  Once ignition is verified, the starter and the turbine then work together to accelerate the HPC to 4,500 RPM, where the starter disengages automatically.  The gas generator continues to accelerate until it reaches idle speed and is stabilized by the governor.  The turbine will then be self-sustaining and support a start time of ten minutes or less as defined in section 3.1.

- 9.2	Hydraulic System Description

The hydraulic starting system consists of:

Hydraulic cranking motor (mounted on turbine auxiliary gearbox)

And the following equipment mounted on the auxiliary equipment module:

-	200 HP (150 kW) electric motor

-	6000 psi hydraulic pump

-	40-gallon hydraulic reservoir

-	Air/Oil cooler with hydraulic fan motor

-	Duplex Filter

-	Control system

The hydraulic circuit will be a closed loop design with a 40-gallon reservoir.  The system requires an initial fill of approximately 35 gallons of ISO VG 46 premium, anti-wear petroleum based hydraulic fluid.  A small charge pump on the cover of the main pump draws fluid from the reservoir to prime the system during each start cycle.  The control system modulates pump flow from zero to approximately 55 GPM during the starting cycle.  This flow regulation permits accurate control of gas generator speed for purging, ignition and acceleration.  The Air/Oil cooler prevents overheating of the hydraulic oil and permits extended cranking for cool down or water wash.

- 9.3	Water Washing Equipment

The following equipment will be mounted on the auxiliary equipment module:

-	304 Stainless steel water wash reservoir

-	Manual fill connection for washing chemicals

-	Manual water fill valve

-	Solenoid valves for water wash sequencing

-	Interconnect hoses between auxiliary skid and main unit

The following equipment will be mounted in the turbine enclosure:

-	"On-line" spray nozzles

-	"Crank-soak" spray nozzles

-	 Stainless steel piping

Purchaser will supply compressed air,  between 80-120 psig filtered to 20 microns, cleaning solution, and demineralized water for the water wash system.

- 9.3.1	Cleaning Solution Specifications

The LPC and HPC sections of the engine will be cleaned with a water/detergent mixture followed by a thorough rinsing.  Rochem solvent and B&B Chemical Company compound 3100 are recommended cleaning agents.  Other cleaning agents must conform to GE standard MID-TD-0000-5.  Water will be used to dilute the solvent and also for rinsing after completion of the cleaning process.  A water/anti-freeze mixture must be used for dilution and rinsing in ambient temperatures of 50F, or below.  See above specifications for suitable anti-freeze recommendations.

- 9.3.2	Water Quality Standards

Please refer to the attached GE Spec MID-TD-0000-4 for compressor cleaning water requirements.

10.0	LUBE OIL SYSTEMS

The gas turbine will be lubricated with synthetic lube oil.  A separate lube oil system using mineral oil will be provided for the electric generator.

Fin fan coolers or water to oil coolers will be used for lube oil cooling.  Coolers will be built to the same specifications as the other auxiliary equipment supplied with the Unit including paint specification, weld specification, seismic design, and wind loading.  Coolers will be designed to operate in ambient conditions up to 95F.  Coolers will be carbon steel with 304 stainless tubes and aluminum fins.  Fans will be aluminum with 7-½ hp Marathon motors.

10.1	Gas Turbine Lube Oil System

1.	Supply System - Provides clean, cool oil to the turbine bearings at the proper 			pressure.

2.	Scavenge System - Recovers (scavenges) the lube oil from the bearing drain 			sumps, then 	filters and cools the oil and returns it to the reservoir.

These sub-systems combine to provide dependable and efficient lubrication for the gas turbine.

- 10.1.1	Gas Turbine Lube Supply System

Approximately 130 U.S. gallons of lube oil are stored in the 150 U.S. gallon capacity stainless steel reservoir mounted on the auxiliary equipment module.  The reservoir will be fitted with a low level alarm switch, a level gauge, a filler connection, and a vent demister.  An electric heater with thermostatic control will be included.

A positive displacement lube oil pump, mounted on the gas turbine accessory drive gearbox, takes suction from the lube oil reservoir.  The pump provides approximately 17 GPM of cooled, filtered lube oil to the turbine bearings.

Oil from the pump discharge will be filtered by a duplex, full-flow filter (6 microns absolute) located on the auxiliary equipment module for ease of replacement.  Filter elements can be serviced during turbine operation. A local differential pressure indicator will be provided to monitor the lube oil filter condition.  A high differential pressure alarm will be provided to indicate that filter service is required.

Lube oil supply temperature will be measured by an RTD.  The temperature will be shown on the control panel CRT, and controls provide high temperature alarm and shutdown.  The lube oil supply passes through an anti-siphon check valve and will then be distributed to the bearing chambers where oil is sprayed onto each engine bearing.  Pressure switches provide low-pressure alarm and shutdown signals to protect the turbine.

- 10.1.2	Gas Turbine Lube Scavenge System

Lube oil is removed from the bearing sumps by a 5 element scavenge pump.   RTDs measure scavenged oil temperature at sumps B, C, D, and E.  Scavenge oil temperature will also be measured via RTD at the accessory gearbox and transfer gearbox discharge.  , with readout, alarm and shutdown at the unit control panel.  A check valve on the pump discharge prevents siphoning of oil back into the engine during shutdown.

The scavenged oil will be filtered through a duplex full-flow filter (6 microns absolute) located on the auxiliary equipment module.  A local pressure indicator and pressure instrumentation will be provided to indicate when filter service is required.

- 10.1.3	Air/Oil Separator Operation

To prevent excessive oil consumption, the bearing sumps will be vented to an air/oil separator rated to minimize oil carryover to the environment per accepted “Good Engineering Practice”.  The air/oil separator is mounted on the ventilation module on top of the generator set enclosure.  The recovered oil will be returned to the reservoir by gravity flow.  The air removed from the mixture will be de-misted and vented to the atmosphere.

- 10.2	Generator Lube Oil System

The generator lubrication system provides approximately 30 GPM of cooled and filtered oil to the generator bearings.  The generator lube oil reservoir, pumps and filters will be located in the generator compartment.  Two doors provide easy access to these components, and the operator can check the lube oil gauges without entering the generator compartment.  The lube oil filters may be changed while the unit is operating.

10.2.1	Generator Lube Oil Supply

The stainless steel reservoir includes a sight level gauge, fill connection and drain valve.  A switch provides a low-level alarm at the unit control panel.  A thermostatically controlled immersion heater will be provided to maintain adequate lube oil temperature in the reservoir.

The main oil pump will be a gear type and mechanically coupled to the generator shaft outboard of the exciter.  An AC motor-driven auxiliary lube oil pump will be used during the start/stop sequencing and as a backup to the main pump.  Rundown tanks provide lubrication during coast down, if the AC lube oil pump should fail or if AC power is lost.

Oil flow will be regulated at each bearing housing by an orifice plate.  The oil flows through the orifice and into the bearings and forms a film that cools and lubricates the journal.  Pressure switches at the bearing supply header provide low pressure alarm and shutdown signals to the unit control panel.

If the supply pressure drops, a low lube oil pressure switch automatically starts the auxiliary lube oil pump. If the lube oil pressure falls to a lower level, the turbine generator set shuts down and special “run-down” oil tanks slowly feed the generator bearings during coast down.

The primary and auxiliary lube oil pumps can each supply 100% of the generator lube oil requirements.  Each pump will be equipped with a pressure relief valve piped to the reservoir.  Lube oil pressure at the supply header will be controlled by a pressure-regulating valve, which bypasses excessive oil flow to the reservoir.

A local pressure indicator and pressure instrumentation will be provided to indicate when filter service should be required. Filters may be serviced during operation.

10.2.2	Generator Lube Oil Return

Each bearing will have a gravity drain and sight glass, which permits the operator to visually verify oil flow.  A dual element RTD will be embedded in each bearing to measure the actual metal temperature.  These RTDs will be continuously monitored at the unit control panel and provide alarm and trip signals.  In addition, an RTD and a temperature gauge will be provided in each drainpipe to monitor bearing discharge oil temperatures.

11.0	FUEL SYSTEM AND WATER INJECTION SYSTEM

The base gas turbine will be configured for gaseous fuel operation.

- 11.1	Gaseous Fuel System

The gaseous fuel system contains the following major components that are to be mounted in the turbine compartment, adjacent to the engine:

-	Duplex gas strainer, pressure switches and local gauges

-	Primary shut-off valve

-	Fuel metering valve

-	Secondary shut-off valve

-	Fuel flow meter

-	Fuel gas manifold

-	30 Fuel gas nozzles

Gaseous fuel will be supplied to the baseplate connection at 675-psig ± 20 psi for full power operation.  A Purchaser supplied filter, pressure regulator, pressure relief valve and manually operated shut-off valve will be installed in the purchaser fuel supply system adjacent to the Unit baseplate.

To protect the turbine against both high and low pressure conditions, the gaseous fuel system will be provided with pressure switches located upstream of the fuel control valve.  The fuel control valve will be an electrically actuated Woodward design.  The fuel control valve provides an accurate, non-pulsating flow of fuel to the engine for initial light off, acceleration and on-line operation.

- 11.2	Gaseous Fuel Specification

The minimum temperature of gas fuel supplied to the gas turbine shall be either 50F greater than the saturated vapor temperature of the gas at the supply pressure or the hydrate temperature, whichever is greater.  The temperature of the gas fuel should not exceed 300F at the gas fuel manifold inlet.  Gas fuel temperatures above 300F will result in a shutdown procedure.  The gas fuel will be defined for each application by the Purchaser and should comply with the attached GE Spec MID-TD-000-1.

- 11.3	Water Injection

The water injection metering system is added to reduce NOx emissions.  Demineralized water will be injected into the combustor through ports in the fuel nozzles to produce NOx suppression.  Water will be supplied to the nozzles by a special water manifold.  The Seller will supply the complete metering system, controls, and boost pump skid.

11.3.1	Water Quality Specifications

Purchaser will supply demineralized water to the Seller defined connection on the water injection boost skid.  A minimum 5-psig, supply pressure will be available to the Seller at a flowrate of 55 GPM per GE Spec MID-TD-0000-3 for NOx water requirements.

12.0	FIRE AND GAS DETECTION AND EXTINGUISHING SYSTEM

- 12.1	General

The gas turbine generator set includes an extensive safety system to detect fire, unsafe temperatures or explosive atmospheres in the equipment enclosure.  The system releases CO2 should a fire be detected.

The enclosures will be designed to reduce the hazard of fire and explosion.  A wall separates the turbine and generator/gearbox compartments to provide isolation.  Individual ventilation systems, with redundant fans, create a positive pressure in the generator/gearbox compartment and a negative pressure in the turbine compartment to maintain separation.  In addition to this fundamental safeguard, gas detectors, thermal detectors, optical flame detectors and an extinguishing system that conforms to NFPA will protect the enclosures.

- 12.2	Unit Mounted Equipment

- 12.2.1	Gas Detectors

Two (2) hydrocarbon gas detectors will be provided in the turbine compartment near the ceiling.  A third detector will be located in the front of the generator compartment.  If any gas detector senses a gas concentration of 15% LEL, a warning will be initiated.  If a sensor detects a gas concentration of 60% LEL, an emergency shutdown will be initiated.

12.2.2	Optical Flame Detectors

Four (4) optical flame detectors will be provided. Three (3) are mounted in the front of the engine compartment and operate with 2-out-of-3 voting logic.  One (1) optical flame detector will be mounted in the generator compartment.  A flame indication by the generator room sensor or any two (2) engine room sensors initiates an emergency shutdown and extinguishing agent release.

- 12.2.3	Thermal Detectors

Thermal detectors monitor the enclosure temperatures as follows:

- GAS TURBINE ENCLOSURE:

-	Two (2) RTDs.  Alarm at 140oF and shutdown at 150oF.

-	Two (2) spot temperature detectors.  Shutdown at 450oF.

- GENERATOR ENCLOSURE:

-	One (1) RTD.  Alarm at 115oF and Shutdown at 150oF.

-	Two (2) spot temperature detectors.  Shutdown at 225oF.

In addition to alarm and shutdown functions, the RTDs provide enclosure temperature signals for the unit control panel CRT.  The spot temperature detectors will be a bimetallic design and respond to both rate-of-rise and compartment temperature.  They cause a unit shutdown and release of the extinguishing agent when tripped.

12.2.4	Manual System Trip

Three (3) manual trip stations will be located on the rotating equipment module; one (1) on each side, near the center of the package, and the third at the exciter end of the generator.

- 12.2.5	Extinguishing System

A CO2 extinguishing system will be provided with the Unit package.  The system components include:

-	Main extinguishing agent storage cylinder(s)

-	Reserve extinguishing agent storage cylinder(s)

-	Necessary valves, piping and wiring

The extinguishing agent will be stored in pressurized cylinders in a mounting, complete with rack and clamps to hold the cylinders and piping to connect the cylinders to the distribution header and nozzles.  The reserve cylinders will be an "automatic backup", and will be released if detectors still indicate a hazard ninety (90) seconds after release of the main cylinders.

The piping within the equipment package, from the pressure connection to the nozzles in the turbine and generator compartment, will be installed.  The fire system control panel controls release of the extinguishing agent.

12.3	Fire System Controls

12.3.1 	General

The fire and gas detection system will be controlled by solid-state modules, which are to be rack-mounted in an enclosure on the front of the unit control panel.  These modules monitor signals from the detectors mounted on the equipment.  Other panel-mounted modules provide logic, memory and output functions to complete the system.

12.3.2	Power Supply

In accordance with NFPA, the fire and gas detection controls will be powered by a dedicated 24V DC battery system.

12.3.3 	Sensor Monitoring

Each equipment mounted sensor will be monitored by the fire and gas detection system control panel.  Solid state modules compare each signal to alarm and shutdown set points.    Readout of gas detector signals will be provided in the HMI.  An alarm from any gas detector provides a contact closure in the alarm summary channel and sounds the panel alarm horn.  A shutdown signal from a gas detector, optical detector, thermal detector, or manual station provides a contact closure in the shutdown summary bus.  This closure initiates an emergency shutdown.

12.3.4 	Defective Sensor Protection

Each sensor will be connected with closed loop circuitry to verify its readiness.  Should the sensor or its wiring become defective, a "fault" condition will be indicated on the fire and gas detection control panel.  A faulty sensor will not trip the unit nor initiate an extinguishing agent release.

12.3.5	Extinguishing Agent Release Logic

When a CO2 release situation may be imminent, ventilation fans will be turned off and a horn will sound.  After a time delay, the extinguishing agent will be released into both generator and turbine compartments.  Fire dampers will be closed the instant CO2 should be released.

A concentration level sufficient to extinguish flames will be established in approximately thirty (30) seconds.  If the primary cylinders fail to discharge within four (4) seconds, the reserve cylinders will be discharged.  If flames are still detected ninety (90) seconds after the primary extinguishing agent cylinders have been discharged, the reserve cylinders will be discharged.

13.0	CONTROL AND MONITORING SYSTEM

General Description

The control and monitoring system for the gas turbine generator set will provide a highly reliable, operator friendly package.  System components will include:

-	Turbine Generator Unit Control Panel

-	Control Batteries and Charger Assembly

-	Gas turbine wet gauge panel and water wash panel (local)

-	Generator wet gauge panel (local)

The unit control panel will be the primary control point for the system.  The gas turbine wet gauge panel will be mounted on the turbine enclosure and provides process readouts and safety devices necessary for maintenance.  Switchgear cubicles containing circuit breakers, protective relays, transformers and motor control center equipment may be available as optional equipment, as described in Section 16.

13.1	Unit Control Panel

13.1.1 	General

The unit control panel will be the focal point for operating the gas turbine generator system.  The panel uses state of the art electronics and is suitable for installation in a non-hazardous local control room near the gas turbine generator.  The control panel includes digital meters for key parameters control switches and HMI for operator commands, a programmable, microprocessor based sequencer, a CRT display, and Ethernet port to export data to a customer DCS, remote terminal or printer.

13.1.2 	Remote Panel Interface

The Unit Control Panel will have a built-in interface for easy connection of a Purchaser's Remote Control Panel or Distributed Control System.

The Unit Control Panel will accept Start/Stop and other operating commands from "dry" relay contacts in the Purchaser's system.  This allows the Gas Turbine/Generator to be integrated into the Purchaser's overall plant control system.

To provide information at a remote location, the Unit Control Panel transmits status information (Stopped, Starting, Running, etc.), Alarms and Shutdowns, and operating parameters (Pressure, Temperature, Flow, etc.) via an Ethernet port in the sequencer.  The Purchaser may use this information on a remote CRT to monitor the operation of the unit.

13.1.3 	Cabinet Construction

The unit control panel will be housed in a freestanding cabinet.  The cabinet will be constructed of welded cold rolled steel.  Approximate dimensions are 90"H x 114"L x 30"D.

Special care will be given to panel appearance and finish.  A high quality corrosion protection, primary painting and finish painting process will be employed.  The standard finish will be textured semi-gloss ANSI gray color paint.

13.2	GE Mark VI Fuel Control/9070 Sequencer

A GE Mark VI Fuel Control/9070 Sequencer in the unit control panel provides sequencing, monitoring and fuel management control for the system.  The Mark VI uses a 32-bit processor and high-speed digital circuitry to control the turbine and generator.  A front-mounted HMI will permit tuning of selected system variables while in operation.  Plug-in modules provide flexibility of operation and permit future system expansion.

The Mark VI controls turbine speed with an electrically actuated fuel valve mounted in the engine room adjacent to the turbine.

13.2.1 	Fuel Management System

The Fuel Management System provides the following:

- 13.2.1.1	Light Off Fuel Control

- This function accurately controls minimum fuel flow for reliable engine light off.

13.2.1.2	Acceleration Control

This function controls the rate of increase of fuel flow to the engine.  While increasing the gas generator speed, the acceleration control continuously checks the rate of speed increase to prevent over fueling conditions which could damage the engine.

- 13.2.1.3	Deceleration Control

This function prevents flameout by controlling the rate of reduction of fuel flow to the engine.  The deceleration schedule will be a function of HPC minimum speed, corrected by compressor inlet temperature, which will be set to prevent flameout.

13.2.1.4	Temperature Control

The gas generator LP turbine inlet temperature (T48) will be monitored at all times.  During start-up and acceleration the temperature limits will be lower than the steady state, full-power limit.  After the engine has accelerated to operating speed, the engine will be allowed to operate at its base load T48 temperature to produce full power.

- 13.2.1.5	Speed Governing

The Fuel Management Systems varies the speed of the high-pressure compressor by controlling the rate of fuel flow.  For maximum safety and stability, the fuel management system incorporates "low select" circuitry.  This circuit uses the lowest of the following signals to control the high-pressure compressor speed:

.	High-pressure compressor speed control

.	Low-pressure compressor/output shaft speed control

.	Maximum temperature control

.	Acceleration control

.	Deceleration control

13.2.2 	Programmable Sequencer

The programmable sequencer controls automatic starting, running and stopping of the turbine generator set.  Programmed time delays will be used to ensure that the sequence will be orderly and that permissive conditions exist before starting the next event.  This careful sequencing provides dependable control and permits the unit to be started and stopped, either locally or remotely, with a single pushbutton.

13.2.2.1	Starting Sequence

A "ready to start" indication shows that the required trips have been reset, the start permissive sequence has been accomplished, the oil and bearing temperatures meet minimum start temps, and the unit stands ready to be restarted.

From a "ready to start" condition, the following automatic start and load sequence will occur when the operator turns the "start" switch:

-	The GE 9070 PLC turns on the primary ventilation fans;

-	The generator AC lube oil pump system activates and output pressure will be 	verified;

-	The starter motor switches on, and the engine begins cranking at 2,200 RPM to purge the system for a minimum of two minutes, depending on exhaust configuration;

-	Engine slows to 1,700 RPM;

-	The fuel system shutoff valves open;

-	The ignition system starts;

-	The turbine fires and accelerates to 4,500 RPM;

-	The starter disengages, and the turbine accelerates under its own power to idle speed;

-	The ignition system de-energizes.

-	The turbine warms-up at idle speed for a pre-set time before automatically 	ramping to synchronous speed;

-	Generator voltage builds;

-	The automatic synchronizer matches generator speed, phase and voltage to the 	electrical bus;

-	The synchronizer issues a "breaker-close" command (verified by two "synch-check" relays) and the breaker closes;

-	The "ready to load" indicator turns on and the operator can begin loading the 	generator manually.  (Optional automatic loading can also be supplied).

Sequence events must be completed within preset times, or the start will be aborted.  The sequencer provides similar automatic shutdown sequence when the Stop button is pushed.

13.3	Additional Control System Functions

The control system also includes the following equipment and control functions:

13.3.1 	Engine Temperature

Eight chromel-alumel dual element thermocouple probes measure the LP turbine inlet temperature.  A connecting harness permits individual readout of the eight input signals, which will be transmitted to the unit control panel and used by the fuel management system.

13.3.2	Low Pressure Compressor (LPC) Speed

Two eddy-current type speed sensors will measure the low-pressure shaft speed .  These sensors detect the blade-passing frequency and provide an electrical signal to the fuel management system.  This signal will be used to control acceleration and output shaft speed, and to actuate overspeed and underspeed switches.  The LPC speed will be indicated on the unit control panel.

13.3.3 	High Pressure Compressor (HPC) Speed

Two magnetic pickups in the accessory gearbox sense HPC speed.  The speed signals will be used by the fuel management system to control acceleration/ deceleration and to activate switches in the control sequence, including overspeed alarm and shutdown.  The HPC speed will be indicated on the HMI.

13.3.4 	Alarm and Shutdown System

A comprehensive alarm and shutdown system will be provided for the turbine generator set and its auxiliaries.  Field-mounted sensing devices (level, pressure, temperature, etc.) provide signals to input modules of the programmable sequencer and fuel management system.  If an abnormal condition should be detected on any sensor, then an alarm and/or shutdown will be initiated.  A HMI display indicates system malfunctions sequentially.  An optional hard copy printer provides a sequential history of alarm and shutdown conditions.

An “acknowledge” push button on the unit control panel HMI silences the audible alarm.  Pressing the Reset button clears the HMI display if the system faults have been corrected.

For additional safety following a shutdown, the operator must acknowledge and reset the alarms before restarting the turbine.

13.3.5 	Vibration Monitor

Vibration monitoring will be provided for the gas turbine and electric generator.  Two accelerometers on the Gas Turbine casing will be monitored in accordance with the General Electric Aircraft standards.  Two (2) Bently Nevada proximity probes will be located at each generator bearing (total four (4) probes).

A Bently Nevada vibration module mounted in the unit control panel continuously monitors each vibration channel.  Vibration levels will be indicated on the HMI.  Excessive vibration causes alarm or shutdown.

13.3.7 	Automatic Synchronizer

Synchronization may be accomplished manually with the synchroscope in the unit panel, or by selecting an automatic synchronizer included in panel.  The auto synchronizer matches the generator's frequency, phase and voltage with the bus and then issues a "breaker close" command signal.  The "breaker close" signal (auto or manual) will be monitored by two (2) independent "synch check relays" to prove synchronization before breaker closure will be permitted.

13.3.8 	Control Batteries and Charger Assembly

A 24-volt DC lead calcium battery system, complete with dual chargers and integral protection equipment will be furnished.  The battery system will be capable of supplying the control loads for at least three (3) hours without recharging.  The battery rack will be made of steel, properly insulated and painted with two (2) coats of acid resistant paint.

The two (2), 100% battery chargers have 208 volt, 60 Hz, 1 phase power supply.  The chargers will be the static rectifier type.  Either charger, operating alone, can maintain the battery fully charged.

13.3.9 	Fire and Gas Detection System

The Seller will provide an independent control rack dedicated to the monitoring of optical flame detectors, thermal detectors and gas detectors as part of the unit control panel.  The rack will be as described in detail in Section 13.  The fire and gas detection system will have it own independent 24V DC battery system with charger.

13.3.10 	Gas Turbine Wet Gauge and Water Wash Panel (Local)

Gauges showing system temperatures and pressures will be mounted in a panel on the side of the main enclosure.  Controls to "water wash" the turbine will be conveniently located in a small panel, near the water wash equipment.  The water wash controls will be interlocked with the turbine control panel for safe operation.

13.3.11 	Generator Wet Gauge Panel (Local)

Gauges for the generator lube oil system will be located on a small panel adjacent to the generator lube oil reservoir.  The gauges may be monitored without entering the generator compartment.

14.0	TESTING

- 14.1	Gas Turbine Test

The gas turbine will be full-load tested at the factory to verify power capability, fuel efficiency and mechanical integrity.  A copy of the factory test report is included in the documentation package.

14.2	Generator Test

The generator will be built in accordance with ANSI C50.14 or IEC 34-3 and tested to IEEE 115 standards.  The factory tests include high voltage, cold resistances, bearing insulation and vibration levels, open and short circuit losses, voltage and current balance and phase rotation. These tests will be performed at the generators manufacturers works.

- 14.3	Generator Set Package Testing

A full load string test will be performed on six of the twenty-four gas turbine generator sets at the Seller’s factory.  The proper operation of the selected entire units will be tested and confirmed, including the gas turbine, generator, fuel management system, alarm and shutdown devices, auxiliary systems and unit vibration.  Electrical loads will be picked up and rejected.  Water injection valves and piping will be checked for completeness and operation.  The water injection system will not be tested during the full-load string test.

The remaining generator sets will undergo an Unfired Test Procedure that includes functional check-out of the generator set without firing the turbine and generator together.  This procedure includes oil-flushing, verification of piping connections, and calibration of instruments- the same steps taken for a fired test.

Electrically, each individual control panel will be powered up, loaded with software, and fully simulated in our test lab to test the safeties and alarms.  Furthermore, the Bently Nevada system will be calibrated and the Integrated Generator Protection System programmed.  As a final check, the Seller connects the control panel up to available diesel generators on the test facility to certify the synchronizer circuits.  The Unfired Test results will be measured, recorded and included in the Test Report for submittal to the Purchaser.

14.4	Field Performance Testing

Performance and Sound Level Tests shall be performed in accordance with the Agreement and Exhibits F, F1 and F2 thereof.

15.0	ELECTRICAL EQUIPMENT

- 15.1	Purchaser’s Electrical Interface

The package will be arranged to simplify the Purchaser’s field connections.  Electrical devices on the rotating equipment module will be wired to junction boxes in the turbine and generator compartments.  Neutral and line-side cubicles will be bolted onto the outside of the generator enclosure for the Purchaser's power connections.

15.2	Area Classification

Electrical components located inside the turbine compartment will be suitable for Class I, Group D, Division 2 areas.  This applies primarily to switches, sensors and electrically actuated valves.  Engine mounted instruments and the 115-volt AC ignition system used during start-up will be constructed to aircraft standards, and, in general, meet the requirements of Class I, Group D, Div. 2, but need not be so qualified or stamped.  The filter house, roof-mounted fans, generator compartment, auxiliary equipment module and optional control house will be classified as non-hazardous areas.

- 15.3	Electric Motors

The AC electric motors 5 HP (3.7 kW) and larger are 460V AC TEFC or explosion proof motors with a 1.15 service factor. Continuously running motors will be the "high efficiency" type.  Nameplate ratings and normal operating loads for each motor will be selected based on system requirements, which have been proven through the Seller’s experience on numerous successful installations.  .

15.4	CTs, Lightning Arrestors, Surge Capacitors

Seller shall furnish seven CTs, mounted in the neutral cubicle; three (3) for metering, three (3) for generator protection and one (1) for cross current compensation.  Three (3) lightning arrestors and three (3) surge capacitors will also be mounted in the line-side cubicle.  Optional line-side CTs for redundant protective relaying may also be provided.

- 15.5	Generator Metering

The unit control panel supplied includes a synchroscope and a front mounted digital meter for frequency, voltage, amperage, power factor and vars.  A rack mounted microprocessor based electronic voltage regulator, with both VAR and PF control, will also be included in the unit control panel, along with the rotor ground-fault detection equipment.

15.6	Lighting

The scope-of-supply includes AC lighting for the interior of the gas turbine compartment, filter house and generator compartment.  Turbine and generator compartments will be fitted with high-pressure sodium fixtures.

- 15.7	Modular Control Room (Optional Feature)

The Seller may supply an optional control room as required by the Purchaser.  When required, the control rooms will be designed to accommodate GT control panels, motor control centers, and unit battery/charger systems.  The control room will be a single lift module using a steel I beam base.

15.7.1 	Structural Design

The modular control room base will be fabricated with 8" wide flange beams welded into a rigid baseplate.  The control room walls will be a "sandwich construction,” consisting of an 18-gauge carbon steel outer panel, 3” of fiberglass insulation and an inner panel of 18-gauge galvanized steel.  The floor-plate will be 1/4" carbon steel.

15.7.2 	Air Conditioning/Heating

The modular control module will be equipped with redundant air conditioning units.  For colder climates, heat pumps may be substituted, or the control module may be arranged with supply/return flanges for Purchaser-supplied heating and cooling fluids.

15.7.3 	Lighting

The modular control room will be complete with ceiling-mounted fluorescent lighting fixtures and switches at each entrance door.

15.7.4 	Equipment in Modular Control Room

Seller will mount the unit control panel, batteries and chargers and Purchaser-selected optional equipment in the modular control room.  Optional items often include:

-	Switchgear (See 15.8 )

-	Unit Motor Control Center (See 15.10 )

15.7.6	Battery Room

The modular control room contains a separate area for battery racks and charger assemblies.  The basic scope-of-supply includes a 24V DC battery pack with a capacity of 300 AMP hours, redundant 208VAC chargers for the unit control system, a 24V DC battery pack with a capacity of 55 AMP hours and a single 120V AC charger for the unit fire protection system.  A separate 125V DC battery/charger assembly to power the switchgear may be provided as an option.  The chargers will be wall-mounted near the battery room and wired to the rack-mounted batteries.

- 15.8	Switchgear (Optional Feature)

The metal clad switchgear, includes a generator circuit breaker, draw out potential transformers and high-voltage current transformers for generator protective relaying.  The switchgear may be supplied as ship-loose cubicles, for installation by others at the job site, or as part of an integrated modular control room as described in Section 15.7.

The main generator breaker and auxiliaries will be mounted in a cubicle approximately 36"W x 94 "D x 95 "H, containing the following components:

-	1 - 3000 AMP, 3 phase, 3 wire, main bus system, copper, fully insulated for 15 kV

-	1 - 1/4" x 2" copper ground bus

-	1 - Set (3) 3000 AMP insulated copper bus bars.

-	1 - 3000 AMP, 3 pole, 15 kV, 1000 MVA - electrically operated drawout type, 	vacuum  circuit breaker, 125V DC close and trip (GE type VBB-1-15-1000-30 or 	equal)

-	4 - Drawout type PTs (for synchronization, protection and metering)

-	3 - CT's (for generator differential protection)

15.9	Generator Protection

The generation protection module will be rack mounted in the gas turbine control panel and contains the following protective functions:

-	#59N – Neutral Overvoltage

-	#51V AC Time Overcurrent – Voltage Restrained

-	#87 Phase differential current

-	#46 Reverse phase current

-	#27 Undervoltage

-	#59 Overvoltage

-	#40 Field failure

-	#81 Over/under frequency

-	#24 Overexitation

-	#60 Balanced voltage supervision

-	#21 Directional impedance

-	#xx Inadvertent energization

- 15.10	Unit Motor Control Center (MCC) (Optional Feature)

The MCC will be built in accordance with NEMA 1, Class 1, with Type B wiring.  The MCC will be a freestanding unit, and may be incorporated into the modular control room as described in Section 15.7.

The standard MCC includes:

-	Modular, plug-in starters or contactors for each motor or 480-volt load in the Unit 	package.

-	Lighting transformer, 15 to 45 kVA, 3 Phase, dry type, 480/208 /120 volt.

-	Lighting distribution panel with circuit breakers for individual /120 volt loads in the Unit package, Integrated into the MCC with the transformer.

16.0	MAINTENANCE, SPECIAL TOOLS AND SPARE PARTS

- 16.1	Special Tools and Fixtures

Special tools and fixtures are required to provide Level 1, maintenance activities.  These are as listed below and offered at a separate price.  The Seller will provide the bridge crane required for removing and installing the turbine from the engine compartment in the basic scope of supply.

The items listed in the fixtures group designated with (*) are required at initial start-up and shall be furnished by the Seller without charge if returned undamaged within 60 days (freight prepaid).

Fixtures Group					Quantity

-	*Main Baseplate lifting pins			      1

-	*Main Baseplate rigging cables		      1

-	*Alignment tool				      1

-	*Alignment axial gauge			      1

-	*Alignment spreader tool			      1

- Level I Maintenance Tools**(optional)

Nomenclature					Tool Number

-	Engine Handling Support			Tool # Not Assigned

-	Dolly, Engine Transfer			TC9025

-	Gage, Immersion Depth Igniter		1C9096/2C6613

-	Borescope Set					2C6388/GE-CTF-120-5

-	Wrench Set					2C6352/1C6344

-	Kit, Mechanics Hand Tool			9448M18G01/GE-CTF-106-80C

-	Tool Set, Engine Rigging			1C5714G05

-	Actuator Unit					2C6395/1C3569

-	Tool Set, Radial Drive Shaft			1C6361

-	Wrench, Speed Sensor - S.V.			1C8062

-	VSV Transmitter				2C6451

-	VSV Indicator					2C14232

-	Installation/Removal Tools			Tool # Not Assigned

-	Adapters					Tool # Not Assigned

-	Gages						Tool # Not Assigned

**This list is preliminary.  Please consult S&S Energy Products for current details.

- 16.2	Spare Parts

Two spare parts lists will be presented as follows:

- Start-up Spares and Consumables

- Operating Spares and Consumables

The gas turbine spares considered as a minimum start-up spares are listed below and shall beincluded in the Seller’s basic equipment price.  Operating spares for the gas turbine, generator and major systems will be offered separately.

An operating spare parts list will be prepared on a project-specific basis after the unit details have been designed.  The list will reflect the fuel type, water injection provisions, air inlet filter type, and Purchaser specified requirements.  Additions and deletions will be made as appropriate for multiple unit sites or remote sites.

- Start-Up Spares

Start-up spares will be provided in accordance with the recommended quantities below:

Nomenclature				Recommended Quantity

1. Filter Elements - Fuel				1 Set

2. Filter Elements - Lube Oil				1 Set

3. Filter Elements - Hydraulic Oil			1 Set

4. Flexitalic Gaskets for Raised-Face			1 Set

Connection Flanges

- 5. "O" Rings and Mating Flanges for			1 Set

High Pressure Hydraulic Connections

6. Fasteners?

17.0	DRAWINGS, DOCUMENTATION AND TRAINING

- 17.1	General

A comprehensive drawing package will be provided for the gas turbine generator set on a Facility basis, which includes simplified flow diagrams of the fuel system, starting system and lube oil systems. Mutually agreeable corrections will be made and the final drawing reissued by Seller.  Certified drawings will be provided only for anchor bolt locations, foundation design and Purchaser’s piping connection locations.

In addition to the approval drawing package, general arrangement drawings of skid mounted auxiliary equipment and the unit control panel will be presented for the Purchaser’s information to complete the site layout plans and establish interface locations.  To assist the operator in checkout and trouble shooting, complete internal system wiring diagrams will be provided in the operation and maintenance manuals.  A typical list of drawings will be is provided in Section 17.5.

- 17.1.1	Drawing Quantities and Format

Four sets of drawings to support each Facility shall be provided within the Purchase Amount.  Each set contains six copies of the package drawings. The drawings shall be 11" x 17" and shall be reproducible on most photocopy machines.  Electronic format submittals of final drawings will be provided in AutoCad, version 14.

- 17.2	Drawings Available

- The Seller will furnish the following documents and drawings.

- 17.2.1 	General Arrangement Drawings

These drawings define the orientation of the major Seller’s modules to be installed by the Purchaser.  A main unit, general arrangement drawing, showing plan and elevation views, will be issued for the Purchaser’s approval.

The general arrangement drawings include the following information:

-	Overall dimensions of the equipment

-	Direction of rotation of equipment

-	Access space required for removal or maintenance of major components

-	Foundation bolt hole locations and sizes, plus any special requirements (Main unit 	foundation information will be shown on a separate drawing)

-	Static and dynamic foundation loads

-	Lifting lug locations

-	Center of gravity information

-	Layout of Purchaser piping and electrical connections, complete with dimensions 	and locations.

- 17.2.2 	One-Line and Three-Line Electrical Drawings

These drawings provide electrical description of the power system from the generator terminals to the purchaser's high voltage bus and ground.  Included will be protective relaying, the excitation system and the synchronizing system.  Also shown on these drawings will be auxiliary power systems, with a simplified display of distribution panels.

If the Seller’s equipment will be interfaced with an existing facility or with customer supplied protective devices, Purchaser will supply facility one-line drawing to Seller for preparation of the Seller’s one-line electrical diagram.

- 17.3	Drawings for Information

The following drawings provide the Purchaser a reference for field construction purposes.  The drawings will be submitted for "information only" and will not be subject to approval.

17.3.1	Electrical System Interconnection Plan

This drawing contains information for recommended interconnecting cables and conduit between Seller supplied modules, and, if applicable, the Purchaser’s control room.  The drawing includes information to assist the Purchaser in purchasing wire and cable for interconnection and in planning the site layout.  Point-to-point interconnection wiring diagrams will also be provided.  These drawings will be completed when other system approval drawings have been finalized.

17.3.2 	Auxiliary General Arrangement Drawings

The following drawings show physical layout and interconnection details required for proper installation of auxiliary equipment.

-	Auxiliary equipment module

-	Water Injection Module

-	Enhanced Sprint Skid

17.3.3 	Flow and Instrument Diagrams (F & ID)

F & IDs will be issued for each of the fluid systems in the Seller’s scope of work.  This includes:

- Natural gas fuel system

- Fuel Oil System, if required

- Water injection system (Enhanced Sprint and NOx Injection)

-	Water wash system

-	Hydraulic starting system

-	Gas turbine lube oil system

-	Generator lube oil system

-	Fire protection system

-	Air inlet and ventilation system

-	Inlet Air Refrigeration System, if required

-	Turbine auxiliary instrumentation

Each F & ID drawing shows the equipment components, piping, valves and instruments in the system, complete with piping line sizes.  The manufacturer and model number of items on the F & ID will be shown on a Bill of Material, which will be a part of each F & ID drawing.  The F & IDs also show the pressure, temperature and volume limitations of the system, including set points for alarms & shutdowns.  Each working fluid in the system will be identified, and initial fill quantities for fluid reservoirs will be shown.  For clarity, the F & ID drawings will be considered schematic in nature.  Therefore, pipe elbows, fittings and similar details will be omitted.

- 17.3.4 	Unit Control Panel Plan & Elevation

This drawing provides installation details for operator information.  The drawing shows the front of the unit control panel as viewed by the operator, including meters, HMI and switches which initiate start/stop and other events.  Cable entry locations and overall dimensions will be shown on this drawing.

17.3.6 	Documentation List

Seller provides a list of procedures and specifications used in our plant during manufacturing.  The following specifications will be included:

.	Factory welding and inspection procedures

.	Application of paint & protective coatings

.	Drafting symbols for contract drawings

.	Factory testing procedures

.	Quality control inspection point program

17.4	Drawings With Manuals

In addition to the above drawings, a complete set of system wiring diagrams will be included in the operation and maintenance manuals to serve as a reference for field check-out and troubleshooting.

17.5	Typical Drawing List

Submittal

Title						Code		Time (Weeks)

| General Arrangement, Main Unit | CA | 8 |
| --- | --- | --- |
| Foundation Loading Diagram, Main Unit | C1 | 8 |
| Installation Foot Print, Main Unit | C1 | 8 |
| Anchor Bolt & Jack Screw Detail, Main Unit | C1 | 8 |
| Lift Plan | C1 | 12 |
| Shipping Plan | C1 | 12 |
| Flow & Equipment Symbols | C1 | 10 |
| Flow & Instrument Diagram, Turbine Fuel System | C1 | 10 |
| Flow & Instrument Diagram, Turbine Lube Oil System | C1 | 10 |
| Flow & Instrument Diagram, Generator Lube Oil system | C1 | 10 |
| Flow & Instrument Diagram, Water Wash System | C1 | 10 |
| Flow & Instrument Diagram, Ventilation System | C1 | 10 |
| Flow & Instrument Diagram, Fire Protection System | C1 | 10 |
| Flow & Instrument Diagram, Turbine Hydraulic System | C1 | 10 |
| Instrument Diagram, Auxiliary System | C1 | 10 |
| General Arrangement, Hydraulic Start Module | C1 | 8 |
| General Arrangement, Air Filter, Ladder & Platforms | C1 | 8 |
| Electrical Abbreviations Symbols & Reference Data | C1 | 8 |
| One Line Diagram, Generator 13.8 kV | CA | 8 |
| Three Line Diagram, Generator Metering | CA | 12 |
| System Schematic, Generator Excitation | C1 | 12 |
| Schedule, Motor Control Center | C1 | 8 |
| Interconnect Plan, Electrical | C1 | 12 |
| Interconnection Wiring Diagram Customer | C1 | 16 |
| Plan & Elevation, 24V DC Battery System | C1 | 12 |
| Plan & Elevation, Turbine Control Panel | C1 | 12 |
| Schematic Diagram, Discrete Control System | C1 | 12 |
| Logic Diagram, Fire & Gas Protection System | C1 | 12 |

Title								  Code

| Interconnect Cable Schedule | C1 |
| --- | --- |
| System Schematic, Communication | C1 |
| System Wiring Diagram, Auxiliary Skid | M |
| System Wiring Diagram, Air Inlet Filter | M |
| System Wiring Diagram, Turbine Vibration | M |
| Schematic Diagram. Circuit Breaker Control | C1 |
| System Wiring Diagram, Turbine Skid | M |
| Plan & Elevation, Lineside Cubicle | C1 |
| Plan & Elevation, Neutral Cubicle | C1 |
| System Wiring Diagram, Fire & Gas Protection | M |
| Wiring Diagram, Lineside Cubicle | M |
| Wiring Diagram, Neutral Cubicle | M |
| Wiring Diagram, Turbine Control Panel Control Cubicle | M |
| Wiring Diagram, Turbine Control Panel Termination Cubicle | M |
| Wiring Diagram, Turbine Auxiliary | M |
| System Schematic, Lighting & Distribution | M |
| Wiring Diagram, Sprint Skid | M |
| Switch Development Control Panel | M |

- NOTES:

1)	CA	= Customer Approval

CI	= Customer Information, Only, Not An Approval Drawing

M	= Drawings Supplied With Operation And Maintenance Manuals

2)	Submittal time shown will be in three weeks after the "Design Finalization Meeting (DFM).

- 17.6	Training - General

Operator training will be provided by Seller to instruct Purchaser to enable proper and safe operation of Seller’s equipment.

Seller’s scope of training includes the supply of experienced teachers, materials and training aids for Operator Training to be conducted at four sites with the Purchase Amount.  Operator training will be available for up to 10 students.  Purchaser must supply facility for training course.

- 17.7	LM6000 Familiarization

A total of four three-day courses for up to 10 Customer's operators will be available during the general training course.  This course familiarizes operators with the major structures, systems and characteristics of the gas turbine engine.

Topics include:

-	Introduction to the Gas Turbine Engine (Classroom)

- Application, size, weight, horsepower, temperatures, pressures, RPM

-	Gas Turbine Orientation (Classroom)

Basic components, air flow, bearings, sumps, seals, parameter designations, piping identification, general system description.

-	Basic Engine - (Classroom)

Frames, stators, compressor, combustor, high-pressure turbine, power turbine, accessory gearbox, air oil separator.

-	Systems - (Classroom and Shop)

Fuel system and components, lube system and components, compressor controls, variable stator vanes, starter system, electrical systems, instrumentation.

-	Operation - (Classroom)

General operation, emergency shutdowns, starting procedures, operation to maximum power, performance and trend monitoring, troubleshooting, engine log records.

-	Borescope Equipment and Maintenance - (Classroom)

- Equipment operation procedures, inspection procedures, typical limits

-	Hardware Review - (Shop - Observation)

Visit manufacturing area to provide close study and physical examination of engine components and accessories, with emphasis upon the latest configurations and further explanatory illustration of areas or points questioned during classroom discussions.

17.8	Turbine-Generator Operations

A total of four five -day courses for up to 10 Customer's operators will be provided at Seller’s plant or Purchaser’s facility site.  The course provides detailed classroom and "hands-on" training on operation of the turbine, generator and auxiliary equipment systems.  Students T & L expenses will not be included.

Topics include:

- Generator:

- Fundamentals of Electric Generation.

-	Generator Construction Details..

-	Generator Cooling System.

-	Generator Lube Oil System.

-	Generator Excitation.

-	Synchronization.

-	Generator Protective Relay System.

- Turbine:

-	Fundamentals of Gas Turbine Operation.

-	Gas Turbine Construction and Operation Details.

-	Inlet Air Filter and Ventilation System.

-	Hydraulic Starting System.

-	Turbine Lube Oil System.

-	Turbine Fuel System.

-	Fire Protection System.

- Controls:

-	Basic Control System Concepts.

-	Sensors, Valves and Actuators.

-	Sequencer.

-	Fuel Management System.

-	Alarms, Shutdowns and Annunciation.

-	Operating Sequences.

-	Troubleshooting.

Progressive examinations will be provided throughout this course to gauge student progress and identify areas where additional instruction may be required.

- 18.0	QUALITY ASSURANCE AND CUSTOMER WITNESS PLAN

- 18.1	Quality Assurance/Quality Control

- Seller’s maintains an ISO 9001 Quality Assurance/Quality Control program.

18.2	Quality Assurance

The Quality Assurance staff, whose Manager reports directly to the Division Vice-President, writes procedures, specifications and test standards.  Quality Assurance also conducts audits of sub-vendors to assure that their quality programs are in place and that their equipment and procedures meet Seller’s standards.

- 18.3	Quality Control

A staff of trained inspectors performs the following:

.	Qualify Welders

.	Inspect Shop Weld Quality

.	Review Radiographic Test Reports

.	Inspect Sub-Vendor's Workmanship

.	Witness Sub-Vendor's Testing, when required

.	Monitor Shop Fabrication, Alignment and Testing procedures

- Inspection Point Program Scope

Attached is a spreadsheet that outlines the inspection and testing required by the quality control, production and test departments.  The quality plan spreadsheet is used as a checklist during the fabrication, assembly and testing of the gas turbine generator packages designed, assembled, and tested at the Seller’s facility.

- Inspection Point Program Objective

This program will be developed as the minimum requirement for both production and quality control.  This program provided written objective evidence that this gas turbine package has been manufactured, assembled, and tested in accordance with the applicable drawing, specifications and Purchaser’s requirements.

- 18.5	Factory Test

The Seller shall perform either a “full load string test” or an unfired test on all new gas turbine generator sets.  Using a special test line at the Seller’s facility, the Seller will perform a functional check-out of the generator set and related control system

- 18.6	Shop Visits

The Seller shall extend an open invitation for Purchaser’s visits to the manufacturing works during normal business hours.  These facility visits should be scheduled in advance to insure proper staffing for plan tours, inspections, meetings, test witnessing and other similarly scheduled activities.

EXHIBIT B-2  NOT USED

EXHIBIT B-3  NOT USED

EXHIBIT B-4  APPROVED VENDORS

AIR FILTERS

Altair

Donaldson

Stewart & Stevenson

Universal

BALL VALVES

Apollo

Kitz

Orbit

Rockwell

Watts

WKM

BATTERY CHARGERS

Lamarche

Sens

BEACON LIGHTS

Whelen

Tomar

CABLE

Alpha

Belden

Consolidated

Okonite

Pirrelli

Tensolite

Thermo-Electric

CHECK VALVES

Check-All

Circle Seal

Durabala

Emco

Gulf Valve

Hoke

Kepner

Kitz

Ladish

Mueller

OIC

TRW Mission

Valtek

Vogt

CENTRIFUGE

Centrico

Alpha Laval

CENTRIFUGAL CHILLERS

Trane

COUPLINGS

Falk

Kopflex

Lovejoy/Centiflex

Lucas Aerospace

Magnalloy

Thomas

Waldron (Garrett)

Zurn

DAMPERS

American Warming

DIFFERENTIAL PRESSURE SWITCHES

Dwyer

Neo-Dyn

Orange Research

DIFFUSER

American Warming

ELECTRIC GENERATORS

Brush Electric

GEC Alsthom

General Electric

Kato

EMERGENCY LIGHTS

Crouse Hinds

EXHAUST STACK

Braden

EXPANSION JOINTS

Expansion-Joint Systems

JM Clipper

Pathway

Power Dynamics

RM Engineered Projects

Hyspan

FANS

Aerovent

FIRE SYSTEMS/COMPONENTS

Alestec

Detronics

Kidde

Rexnord

Wilson

FLAME DETECTORS (UV)

G.E.

Honeywell

FLOW METERS

Cal-O-Flow

EG&G Flow Technology

Foxboro

Yokogawa

FLOW SWITCHES

Delta Controls

Fluid Components

FUEL CONTROL VALVES

EGT

Whittaker

Woodward

RECIPROCATING GAS COMPRESSORS

Ariel

Dresser-Rand

GAS FUEL FILTERS

Texas Systems & Controls

GATE VALVES

Bonney Forge

Kitz

Stockham

Vogt

GEARBOXES

Lufkin Industries

Maag

Koe Milwaukee

GLOBE VALVES

Stockham

HEAT EXCHANGERS

Air Coolers

American Technology

Air-X-Changer

GEA Rainey

Hayden

Oil Coolers

Basco

HEAT TRACE

Thermon

Wyegland

HEATERS

Fuel Oil

Texas Systems & Controls

Compartment

Ruffneck

Lube Oil Tank

Chromalox

CO2 Enclosure

Caloritech

INLET SILENCERS

Donaldson

Farr

IAC

Spitzer & Assoc.

INSTRUMENT VALVES

Dragon

INSULATORS

Victor

JUNCTION BOXES

Hoffman

Stewart & Stevenson

Tanco

LEVEL SWITCHES

IMO

Jobell

Link

Murphy

LIGHTNING ARRESTORS

GE

LUBE OIL FILTERS

Donaldson

Pall

Parker

MIST COLLECTORS/AIR OIL SEPARATORS

Aercology

Altair

Dollinger

Monsanto

Stewart & Stevenson

MOTOR CONTROL CENTERS

Allen Bradly

General Electric

MOTORS

GE

Marathon

ORIFICE

Meriam

LPC

GE

Allen Bradley

Xycom

PRESSURE CONTROL VALVES

Fisher

PRESSURE GAUGES

Ashcroft

Dwyer

Orange Research

PRESSURE SWITCHES

Dwyer

Neo-Dyn

United Electric

PRESSURE TRANSMITTERS

Honeywell

Rosemount

Schlumberger

Statham

PUMPS

Barnes

EGT

Gould

IMO

Rexroth

Roper

Roto-Jet

Sundstrand

Tuthill

Voith-Eckerle

Whitton

Woodward

REGULATORS

Fisher

RELIEF VALVES

Anerson Greenwood

Circle Seal

Crosby

Fisher

Hycon

Kepner

Parker

RTD’S

Brush

Rosemount

Weed Instrument

SEQUENCER

Woodward

SIGHT GLASS/FLOW INDICATORS

Cyclops

Jacoby-Tarbox

OPW

SNUBBERS

Ashcroft

SOLENOID VALVES

Asco

Atkomatic

Denison

Versa (Stig)

SPEED SENSORS

GE

STARTER

Rexroth

Starter Clutch

Hillard

STRAINERS

Hayward

Marvel

Mueller

SURGE CAPACITORS

GE

TANK THERMOMETERS

Ashcroft

TANKS

Brunner Mfg.

Gulf Coast Alloy Welding

Jerryco

Stewart & Stevenson

TEMPERATURE INDICATORS

Ashcroft

TEMPERATURE SENSORS

Rosemount

Weed

Woodward

TEMPERATURE SWITCHES

Neo-Dyn

United Electric

TERMINAL BOARDS

Buchanan

Entrelec

Phoenix

THERMOSTATIC CONTROL VALVES

Amot

THERMOSTATIC SWITCHES

Amot

Neo-Dyn

United Electric

VANEAXIAL FANS

Aerovent

Hartzell

VIBRATION MONITORING

Bentley Nevada Corp.

VIBRATION SYSTEMS

Bentley Nevada Corp.

EXHIBIT B-5  DOCUMENT REVIEW STATUS CRITERIA

DRAWING PROCESSING

A copy of each drawing reviewed will be returned to Seller as stipulated herein.  Copies of drawings returned to Seller will be in the form of a print with Purchaser’s marking.

A.	DEFINITION OF SELLER DOCUMENT REVIEW STATUS

The guidelines listed below are followed in assigning the document status number to Seller prints.  These status numbers serve as hold points for starting or continuing manufacture of the covered commodity.  The document and its transmittal letter indicate the reason for the status.

Status 1: Work may proceed.

The document conforms to Agreement requirements.  The document requires no changes or additions.  Matters remaining to be resolved do not require document change and will be handled by correspondence.  Where it is known that the design information on a supplier document is not complete and resubmittals will be made, such as “hold” areas, the document is assigned another status number.

Status 2: Revise and resubmit.  Work may proceed subject to resolution of indicated comments.

The document is in basic conformance with Agreement requirements.  Minor deviations from Agreement requirements (not including minor changes for Purchaser’s convenience) have been noted or other minor technical or physical changes in the equipment are required.  Such changes may include those affecting dimensions, material, colors, etc.  Administrative type changes such as inclusion or equipment or tag numbers and shipping notes may be combined with technical changes in this status.  Seller shall resolve comments and resubmit documents prior to shipment of commodity.

Status 3:  Not Used.

Status 4: Review not required.  Work may proceed.

Document is not subject to Purchaser review.  Typical uses for this status are in the review of items that are supplier standard products, small internal parts of major equipment, or Seller standardized data.

Permission to proceed does not constitute acceptance or approval of design details, calculation analysis, test methods, or materials developed or selected by the supplier from full compliance with contractual obligations.

FINAL DRAWINGS

Upon receipt from Purchaser of drawings marked Status 1 or Status 4, Seller drawing shall be considered acceptable and no further corrective action shall be required.  After completion of fabrication and release for shipment, all drawings shall be resubmitted showing the “as installed” configuration of the Equipment.

EXHIBIT C-1  SELLER PARENT GUARANTEE

GUARANTEE

THIS GUARANTEE, dated the ______ of ____________________, 200___, is from [Seller's Parent Company], a [           ] corporation ("XXX"), to [                ]. ("RECIPIENT").

WHEREAS, [Seller] is an affiliate of [Seller's Parent Company] ("XXXX"); and

WHEREAS, RECIPIENT and [Seller] entered into the attached Agreement dated [------] (the "Agreement"); and

WHEREAS, Seller desires to assign all or part of its rights and benefits and delegate its duties and obligations under the Agreement to [Assignee] (the “Assignee”); and

WHEREAS, [Seller's Parent Company] has agreed to guarantee the performance of Assignee under the Agreement in order to induce RECIPIENT to consent to Seller’s assignment of the Agreement;

NOW THEREFORE, [Seller's Parent Company] hereby irrevocably and unconditionally guarantees to RECIPIENT the performance by Assignee of all of Seller’s undertakings, covenants, indemnities and obligations under the Agreement to the extent and under the terms and conditions and subject to the limitations set forth in the Agreement.  [Seller's Parent Company] hereby consents that at any time and from time to time without notice to [Seller's Parent Company], the performance or observance by Assignee of any term or covenant of the Agreement may be waived, the time of performance thereof extended, any provisions thereof amended and the rights of RECIPIENT hereunder assigned, without affecting the liability of [Seller's Parent Company] hereunder.  [Seller's Parent Company] may assert any and all defenses and limitations of liability possessed by Assignee, but excluding any defenses based upon invalid execution of the Agreement.

This guarantee shall be governed by, and construed, interpreted and enforced in accordance with the substantive law of the State of Texas, excluding any conflict of laws or principles which would result in a choice of law for this Guarantee other than Texas law.  Further, the parties stipulate that this Guarantee is deemed to have been made and entered into by them in the State of Texas.  With respect to any suit, action or proceedings relating to this Guarantee (the "Proceedings"), each party irrevocably submits to the exclusive jurisdiction of the courts of the State of Texas and the United States District Court located in Harris County, Texas, and irrevocably waives any objection which it may have at any time to the laying of venue of any Proceeding brought in any such court, waives any claim that such Proceedings have been brought in an inconvenient forum and further waives the right to object, with respect to such proceedings, that any court does not have jurisdiction of such party.  Nothing in this Guarantee precludes either party from enforcing in any jurisdiction any judgement, order or award obtained in any such court.

[Seller’s Parent Company] waives any rights to subrogation/security and agrees to be bound by any findings of fact or final award or judgement made in an arbitration against Assignee under the Agreement.

This Guarantee and any liability or obligation created hereunder shall expire upon the expiration of all liability and obligations of [Assignee] under the Agreement.

IN WITNESS WHEREOF, [Seller's Parent Company] has caused this Guarantee to be executed as of the date first written above.

[SELLER'S PARENT COMPANY] By: Printed Name: Title:

EXHIBIT C-2  NOT USED

# EXHIBIT D  SAMPLE LETTER OF CREDIT

Applicant:   [-------] (“Seller”)

Beneficiary: [-------] (“Beneficiary”)

Bank: [------- ] (“Bank”)

Expiry Date:

Amount:       US ($--------)

I.	Funds under this irrevocable standby Letter of Credit are available to Beneficiary against presentation to us of Beneficiary’s draft drawn at sight on _____________, marked thereon “Drawn under standby Letter of Credit number ________, and accompanied by the following documents:

1.	Original Beneficiary’s statement purportedly signed by an authorized officers of Beneficiary (as determined at Beneficiary’s sole and absolute judgement) stating:  “Seller is in default of its obligation to perform in accordance with Section(s) [-------] of Agreement No. [------------] (the “Agreement”), dated _________.  This statement is a demand for payment under irrevocable standby Letter of Credit number _______ notwithstanding any objection by Seller or any other person or entity whatsoever.”

2.	A copy of the written Notice to Seller sent pursuant to Article 25 of the Agreement (a copy of the conformation of receipt shall be attached thereto) , dated at least thirty (30) Days prior to presentation of any claim under this irrevocable standby Letter of Credit evidencing that Beneficiary gave the requisite written notification to Seller stating therein that Seller was in breach of a specified obligation under the Agreement and that it is [beneficiary] intent to drawdown [specify amount] in the event Seller fails to cure or commence to cure such default within thirty (30) Days from the date of this Notice.

II.	Special Conditions:

1.	Payment under this irrevocable standby Letter of Credit will be made to an account in Beneficiary’s name at such bank as Beneficiary shall stipulate.  The amount or amounts demanded shall not exceed, in the aggregate, the amount of this Letter of Credit.

2.	Any payment made hereunder shall be made free and clear of and without deduction for, or on account of, any present or future taxes, levies, imposts, duties, charges, fees, commissions, deductions or withholdings of any nature whatsoever and by whomever imposed.

3.	Any reference to Agreement/Bid item is for information purposes only and is not incorporated in nor made a part of this irrevocable standby Letter of Credit.

4.	Bank agrees and consents that this irrevocable standby Letter of Credit may be modified, adjusted, amended, extended, suspended or shortened pursuant to Article VI of the Agreement, and that this irrevocable standby Letter of Credit, subject to agreement of Beneficiary, Seller and Bank, may be modified to comply with any such changed requirements of the Agreement.

5.	Seller’s liability under this irrevocable standby Letter of Credit is limited to ([-------] United States Dollars [$-------]).  This irrevocable standby Letter of Credit shall expire at our counters [-------]     , 20[---].

6.	Demands may be made against this irrevocable standby Letter of Credit in one or more increments; however, the aggregate of such demands shall not exceed the amount set forth in Paragraph 5 of this irrevocable standby Letter of Credit.

We hereby engage with the Beneficiary that draft(s) accompanied by documents drawn in strict compliance with the terms and conditions of this irrevocable standby Letter of Credit shall be duly honored by us if presented to us at our office located at _______________________on or before the expiration date.

This irrevocable standby Letter of Credit is subject to the uniform customs and practice for documentary credits (1993 revision), International Chamber of Commerce, Publication No. 500.  This irrevocable standby Letter of Credit shall be governed by, and construed in accordance with the laws of the State of New York.

EXHIBIT E NOT USED

EXHIBIT F  PERFORMANCE TEST GUIDELINES

A.	TEST PHILOSOPHY

I.	General.

The performance guarantees for the Unit include the Specific Performance guarantees of the Specific Performance Levels and performance guarantees of the Guaranteed Levels.  The performance test procedure will include three (3) one (1) hour input/output test runs for each Unit utilizing a combination of installed station instrumentation and special test instruments to (i) observe and record of the parameters required to demonstrate or calculate performance and (ii) enable correction of the demonstrated or calculated performance to Basis Conditions (individually a “Test Run”).  All instruments used to measure parameters used to calculate the results of the Test shall meet the accuracy and calibration requirements of the Codes and Standards or as specified in this Exhibit F, if station instrumentation does not meet accuracy, Purchaser shall install temporary equipment to meet accuracy.

If the test run results and uncertainty bands calculated from the post-test uncertainty analysis demonstrate “complete overlap”, as described in PTC 19.1-1998 Section 8.5 and Figure 8.3, the Seller may choose two (2) of the three (3) Test Runs for the basis of test acceptance.  The results of the same two test runs shall be used to evaluate all of the performance guarantees.

The Performance Test will be performed by the Purchaser.  Seller will supply gas turbine correction curves and calculations, while Purchaser will prepare a detailed Test Procedure, based on PTC 1-1999, PTC 22-1997, PTC 4.4-1981, PTC 19.1-1998, PTC 46-1996 and appropriate related ASME Performance Test Codes and ASME Standards (the “Codes and Standards”), Purchaser will perform calculations to determine Unit performance relative to Guaranteed Levels and Specific Performance Levels and will prepare test result certificates in the form as set forth in Exhibits G-1 and G-2 for submittal to Seller’s Representative.

Performance Tests should be conducted as soon as possible (within 200 site fired hours) after first fire.

II.	Procedure

The gas turbine generator will be operated at Base Load as defined in the Agreement.  The Test Procedures will include a demonstration of power capability, heat rate, exhaust energy (when applicable) and exhaust temperature (when applicable).  The Unit’s auxiliary equipment power consumption data will be measured to enable determination of net Electrical Output of the Unit.

The Performance Test Procedures will establish the methodology, based on the Codes and Standards, for calculating the Unit performance and for correcting the Unit’s measured Electrical Output (gross), Heat Rate (gross), and Exhaust Gas Temperature and Exhaust Gas Energy, as applicable to plant cycle design, from existing Site conditions to Basis Conditions, and subsequently deducting Unit auxiliary loads for the purpose of comparing the Adjusted Electrical Output, Adjusted Heat Rate, Adjusted Exhaust Gas Temperature and Adjusted Exhaust Gas Energy values against Guaranteed Levels and Specific Performance Levels as applicable.  Unit specific correction curves needed to correct from Site conditions to Basis Conditions will be developed by Seller and included in the Performance Test Procedures.

A Facility specific Facility Agreement Performance Test Guideline will be prepared for each Site.  The specific guideline will include a means of verifying that the Unit is at base load during each performance test run by comparison of operating data with control variables.  It is the Seller’s responsibility to ensure that the Unit is operating on its control curve that defines Base Load at the time of the test.  A test run will not be valid if the Unit control mode changes during that run.  The GE cycle deck will be used to determine the performance corrections for determination of the Test Result, however, the performance guarantee margins and test uncertainty will be taken into account.   Since the Unit has multiple control modes it is necessary to make corrections of the Unit performance for inlet conditions to evaluate the corrected control mode.  The uncertainty analysis shall include control element uncertainty as noted in PTC 22-1997.  Seller will supply all necessary correction curves for the purpose of the calculating the Test Results.

B.	STANDARD FIELD PERFORMANCE TESTING PROCEDURE

I.	Scope

The Test Procedure will follow ASME PTC 22-1997 and ASME PTC 46-1996.  Whenever deviations from ASME PTC 22-1997 and/or ASME PTC 46-1996 are required the performance test procedure will clearly identify the deviations, the reasons for the deviations, and the alternative proposed method to be used during testing for agreement among the parties involved in the testing.  Any deviation from the ASME PTC codes is required to maintain the high accuracy criteria of the codes and of this Exhibit F.

II.	Machine Condition

In accordance with Section 12.4.1 of the Agreement, Seller’s representative shall certify that the Unit is ready to test.

The Unit shall be tested when in new and clean condition subject to Section 10.12.4 of the Agreement.  The Seller’s representative shall determine, in its sole and reasonable discretion, based on the terms of this Agreement and the Test Procedures, whether the subject Equipment is in new and clean condition and ready to be tested.  For testing conducted after new and clean period as defined in Section 10.12.4.2 of the Agreement, Seller’s degradation curves, as set forth in this Agreement, shall be utilized.

If the Seller’s representative, in its sole reasonable discretion, determines that the subject Equipment is not in new and clean condition prior to the conduct of the Performance Test, the Equipment shall be cleaned in accordance with Seller’s recommendations set forth in Exhibit A-2, Attachment 3 (Seller reference).

III.	PTC 22-1997 Modifications and Clarifications

A.	A valid Test Run will consist of a minimum of thirteen (13) sets of instrument reading taken at five (5) minute intervals over a sixty (60) minute time span after steady state conditions have been established as listed in PTC 22.

B.	Speed measurements are required and must be measured by an electronic tachometer or equal, and averaged for the Test Run.  Any corrections for frequency variation shall be applied to the calculation.

C.	Unit Electrical Output is to be measured by polyphase calibrated watthour meters (of revenue meter quality) at the generator terminals.  Revenue quality metering shall be provided by Purchaser.

D.	Gas Turbine exhaust temperature will be measured in control thermocouples mounted in the exhaust plenum (supplied by Purchaser).

E.	It is essential that the temperature indicating system be adjusted and calibrated in place with a known millivolt source prior to the test so that it reports reliable data.

F.	Barometric Pressure at the test site shall be measured with a mercury or aneroid barometer with an accuracy in accordance with PTC 22.  A minimum reading accuracy of 0.01 inches of Hg is required.

G.	Fuel Consumption: Gas fuel is to be measured with a flat plate orifice or venturi installed in accordance with ASME MFC-3M or a turbine meter installed according to ASME MFC-4M standards.  Calculation of gas flow will be done in accordance with either ASME MFC-3M or MFC-4M as appropriate.  The upstream pressure will be measured with a precision test gage, the pressure drop with a manometer, the gas temperature with a thermometer or thermocouple.  The above flow will be verified with the Unit mounted fuel flow meter.

H.	Four (4) gas samples shall be taken from the fuel system during the test for laboratory analysis of composition according to ASTM D1945.

I.	The higher and lower heating values will be determined according to ASTM D 3588.

J.	Ambient air condition will be measured with at least two (2) (preferably 4) RTD’s with an uncertainty meeting PTC 22.

K.	Turbine exhaust static pressure at or near the turbine exhaust flange or other convenient location must be measured using at least two (2) disc type static pressure probes.

L.	All instruments to be used in the performance test shall be calibrated immediately prior to the performance test and checked immediately after the performance test.  The Parties to the Test will witness the calibrations and inspections.

IV.	Evaluation

The Performance Test Procedure will include the tolerance due to measurement uncertainties associated with each particular test result in accordance with Section 10.12.10 (iii) of the Agreement.

The Parties will agree on a method of determining the sufficiency of the inlet chiller coils to provide the desired inlet air cooling.  The results of this determination will be included in the calculation of the Test results and in the Performance Test report.

# AUXILIARY POWER LOAD

| GT Package Equipment | Quantity in Operation |
| --- | --- |
| Turbine Vent Fans | 1 |
| Generator Vent Fans | 1 |
| Hydraulic Start Pump | 0 |
| Gen. Aux. L.O. Pump | 0 |
| Gen. Jacking Oil Pump | 0 |
| Turbine L.O. Heater | 0 |
| Gen. L.O. Heater | 0 |
| Turbine Air/Oil Separator | 1 |
| Lighting and Low Voltage Distribution System | 1 |
| Sprint Water Pump | 1 |
| Water Inj. Pump-Gas Fuel | 1 |

EXHIBIT F-1  SOUND LEVEL TEST GUIDELINES

PERFORMANCE TEST GUIDELINES FOR NEAR SOURCE SOUND LEVELS

- Testing methodology shall be based on the latest version of ANSI/ASME PTC 36.  The final result shall be the arithmetic average of the sound power levels (“SPLs”) measured around the equipment after background and other corrections have been applied.  The equipment shall be in compliance if the final result does not exceed the noise limit(s) specified in Section 10.5 of the Agreement.

- Equipment shall be operated in a new and clean condition as intended by the designers when measurements are taken.  All access compartments, doors, panels and other temporary openings shall be fully closed; all silencing hardware shall be fully installed; all systems designed to be airtight shall be sealed.

- Corrections to the measured SPLs shall be made per ANSI/ASME PTC 36 procedures.  Background noise is defined as the noise measured with all Seller supplied equipment off and all other plant equipment on.

- Intermittent noises such as steam safety blow off valves and filter pulse noise are not included in the above guarantee.

- Measurements shall be taken 3.28 feet (1 meter) away from the outermost surfaces of equipment, including piping, conduit, framework, barriers, Equipment enclosures and personnel protection devices if provided.

- Measurements shall not be taken in any location where there is an airflow velocity greater than 4.9 feet per second (1.5 meters per second), including nearby air intakes or exhausts.

- Free field conditions must be prevalent at measurement locations.  Testing and corrections to a free field shall be per ANSI/ASME PTC 36.

- Testing shall be done according to a test plan agreed to by both the Purchaser and Seller.  Such a plan shall be submitted to both the Purchaser and Seller at least 30 Days prior to noise compliance testing.  The test results shall be submitted in the form of a test report that shall be made available to both the Purchaser and Seller.

Measurement responsibility shall be stated in the Agreement.  Seller reserves the right to audit or parallel these measurements.

PERFORMANCE TEST GUIDELINES FOR FAR FIELD SOUND LEVELS

- Testing methodology shall be based on the latest version of ANSI B133.8.  The final result shall be the arithmetic average of the SPL’s at the 8 measurement locations after background and other corrections have been applied.  The equipment shall be in compliance if the final result does not exceed the noise limit(s) specified above.

- Equipment shall be operated in a new and clean condition as intended by the designers when measurements are taken.  All access compartments, doors, panels and other temporary openings shall be fully closed; all silencing hardware shall be fully installed; all systems designed to be airtight shall be sealed.

- Corrections to the measured SPL shall be made per ANSI B133.8 procedures.  Background noise is defined as the noise measured with all Seller supplied equipment off and all other plant equipment on.

- Intermittent noises such as steam safety blow of valves and filter pulse noised are not included in the above guarantee.

- Measurements shall be taken 4.9 feet +/- 2.5 feet (1.5  meters +/- .75 meters) above the ground.  Such measurement locations shall be on a flat elevation no more than 16 feet (5 meters) above or below the plant base elevation.

- Measurements shall not be taken in any location where there is an airflow velocity greater than 5 feet per second (1.5 meters per second), including nearby air intakes or exhausts.

- Measurement locations shall be chosen such that free field conditions exist at those locations.  Measurement locations shall not be closer than 12 feet (3.5 meters) to any nearby reflecting surfaces.

- Testing shall be done according to a test plan agreed to by bother the Purchaser and Seller.  Such a plan shall be submitted to both the Purchaser and Seller at least 30 Days prior to noise compliance testing.  The test results shall be submitted in the form of a test report that shall be made available to both the Purchaser and Seller.

Measurement responsibility shall be Purchaser’s.  Seller reserves the right to audit or parallel these measurements.

EXHIBIT F-2  EMISSIONS TEST GUIDELINES

# GE POWER SYSTEMS
U.S. Standard Field Testing Procedure for Emission Compliance

Test Philosophy

Testing to demonstrate emission guarantees and for adjustment of the NOx reduction system (if required) will be performed using procedures which are mutually agreed between Seller and the Purchaser.  Seller engineers and/or technical advisors may be present at the tests for procedural direction.  Test methods chosen are EPA methods which yield data on site immediately, wherever possible.

Emission Testing

A.	General

Emission testing identified herein shall be within Purchaser’s scope of supply using procedures which are mutually agreed.  Sampling for inlet pollutant concentrations may be required, at the sole discretion of GE, in order to demonstrate compliance with emission guarantees.  Seller’s guarantees apply to the net increase of these pollutant emissions.

B.	Nitrogen Oxides Emissions

Before the official compliance testing is begun, the NOx reduction system will be adjusted to verify compliance with  NOx emission limits.  The gas turbine control system contains a pre-programmed schedule for either water or steam injection, this schedule may be adjusted to achieve an appropriate emission level approximately 5% to 10% below emission limits, and minimize the supply requirements.  Once the proper injection schedule has been established, this schedule is maintained throughout the testing, and it is programmed into the control system.

The NOx emission testing and related oxygen testing will be in accordance with U.S. EPA Method 2 presented in the Code of Federal Regulations.  Title 40, Part 60 (40CFR60 Appendix A and 40CFR60 Subpart GG -- Standards of Performance for Stationary Gas Turbines), with the following modifications, limitations and additions:

a.	The NOx instrument will be limited to a chemiluminescent type which meets 40CFR60 Appendix A, Method 7E.

b.	The span of the NOx analyzer will be set for appropriate spread of the expected NOx readings, rather than the specified 300 ppm.

c.	Oxygen will be sampled simultaneously with all NOx readings since Subpart GG of 40CFR60 requires correction to 15% O2.  Method 3A from 40CFR60 Appendix A is used for the oxygen analysis.

d.	Section 60.33(c)  (i)of Subpart GG has been replaced by U.S. EPA Memorandum dated June 2, 1997 for GE gas turbines using either water or steam for NOx reduction.  The EPA memorandum approves the Seller injection control algorithm in lieu of the Subpart GG ISO correction equation.

e.	Section 60.335(c) (i) is not applicable to gas turbines with dry low NOx combustors.

C.	Carbon Monoxide Emissions (If Required)

Sampling is the same as for NOx normally with the same line feeding the different instruments.  Method 10 per 40CFR60 appendix A is used, but only the continuous sample method per Section 5.1 is acceptable to Seller.  A recorder is mandatory, not optional as per 5.3.9, with a span which gives an appropriate spread of the expected readings.

D.	Unburned Hydrocarbon Emissions (If Required)

Sampling and analysis must be on a wet basis to avoid condensing out the higher hydrocarbons.  Moisture determination by Method 4 (or Method 5) is necessary to convert results to dry basis.  Method 25A per 40CFR60 Appendix A is used for unburned hydrocarbons.  Results are presented as methane (CH4).  This method uses a flame ionization detector or analyzer.

E.	Volatile Organic Emissions (If Required)

When volatile organic emissions (non-methane, non-ethane hydrocarbons) are required, Method 18 per Section 7.2 is used.  This requires a gas chromatograph at the site.  Seller requires calibration of the measurement train at the sampling probe.

F.	Sulfur Emissions (If Required)

Sulfur emissions will be determined by use of fuel flow data and fuel analysis for sulfur content.

G.	Particulate Matter Emissions (If Required)

Particulate matter emissions are determined by sampling, analysis and calculation in accordance with U.S. EPA Methods 5 and 5B with traversing per Methods 1 and 2 all from 40CFR60 Appendix A.  The following modifications and limitations on choices within the methods apply:

a.	Sampling probe internal surfaces must be made of chemically inert and non-catalytic material such as quartz.

b.	The filter material shall be quartz.

c.	Nozzle, probe and filter must be heated to 248 to 273F per Method 5, or at last 10F higher than the dew point of sulfuric acid in the exhaust duct.  Use of Method 5B requires nozzle, probe and filter to be heated to 320 to 345F.

d.	Probe wash shall be acetone per Method 5.

e.	Sampling technique shall provide a fairly large exhaust gas sample, with an objective of 100 SCF.

f.	Sulfates are excluded from the Seller guarantees for particulates.

H.	PM10 Emissions (If Required)

PM10 emissions are determined by sampling, analysis and calculation in accordance with U.S. EPA Methods 5 for front half filterable particulate matter and Method 202 for back half condensible particulate matter with traversing per Methods 1 and 2, all from 40CFR60, Appendix A except for Method 202.  Method 202 is from 40CFR51, Appendix M.  The following modifications and limitations within the methods apply:

a.	Sampling probe internal surfaces must be made of chemically inert and non-catalytic material such as quartz.

b.	The filter material shall be quartz.

c.	Nozzle, probe and filter must be heated to 248 to 273F per Method 5, or at least 10F higher than the dew point of sulfuric acid in the exhaust duct.

d.	Probe wash shall be acetone per Method 5.

e.	Sampling technique shall provide a fairly large exhaust gas sample, with an objective of 100 SCF.

f.	Impinger solution shall be extracted with ACS grade methylene chloride per Method 202.

I.	Opacity (If Required)

Opacity shall be measured in accordance with EPA Method 9 from 40CFR60, appendix A.

J.	Ammonia Slip (If Required)

Required EPA methods for measuring ammonia slip have not been published.  GE has established in the interim a preference for the determination of ammonia slip.  The ammonia slip emissions will be determined by on-site sampling and analysis plus calculations in accordance with the on-site industry procedure of Indophenol Absorptiometrics.  This procedures requires the use of reactant solutions and a photoelectric spectrophotometer at the plant site.

Sample collection procedures should include Item G(a)-(e) above (Particulate Matter Emissions - Front - Half Filterable Solids Only).

K.	Certification of Calibration Gases

All gases used in certification of instruments or performance of emissions guarantee demonstrations shall be analyzed and certified in a manner and by a laboratory mutually agreeable to GE and Purchaser.  Examples of acceptable certification are:

- U.S. EPA Standard Methods

- U.S. EPA Protocols

- U.S. National Bureau of Standards Certification Procedures

L.	Exhaust Gas Flow Determination (Not required for this Agreement)

Seller has established preferences for the determination of exhaust flow based on accuracy of the determination.  GE prefers the following:

The primary exhaust flow determination shall be by the F - factor method per 40CFR60, appendix A, Method 19 (as specified in Method 20 for gas turbine emissions).  The F - factor constants from Table 19-1 shall be applied in all cases where possible per Paragraph 3.1.

Where available, the compressor inlet air flow signal shall also be used to compute exhaust flow.  Exhaust flow on a dry basis is the turbine inlet air flow minus the water vapor plus the fuel flow minus the water formed from the combustion of hydrogen in the fuel.  Gas turbine inlet air is measured using the compressor inlet air scroll as a flow element.  The inlet scroll is calibrated during the factory tests of the gas turbine.

Flow measurements by Velocity Traverse, per 40CFR60, Appendix A, Methods 1 and 2, can result in errors of 25% or more in this application, and is not acceptable.

M.	Fuel Bound Nitrogen Determination

Prior to emission testing, analysis for fuel bound nitrogen must be determined in accordance with ASTM D4629 which is based on a combustion/chemiluminescence method.

EXHIBIT G-1  PERFORMANCE TEST CERTIFICATE

# PERFORMANCE TEST CERTIFICATE

The undersigned duly authorized representative of (Name of Purchaser’s Company), under the provisions of the Agreement between [-------------] and [--------------], dated (_______) the “Agreement” hereby certifies that:

1.	Performance Tests have been conducted pertaining to Electrical Output, Heat Rate, Sound Levels and  Emissions [and in the case of combined cycle operations, Exhaust Gas Energy and Exhaust Gas Temperature] of the combustion turbine generator units referred to in the Agreement (each a “Unit” and collectively the “Units”) as set forth therein.

2.	During the most recent Performance Test, completed [date] the [turbine SNs] Units tested produced [-------] kW as the Adjusted Electrical Output for the [   ] Units when consuming [---] for fuel.

3.	During the most recent Performance Test, completed [date] the [turbine SNs] Units tested produced [-------] BTU/kWh as the Adjusted Heat Rate for the [    ] Units.

4.	During the most recent Sound Level Test, completed [date] the [turbine SNs] Units tested produced a Near Field Sound Level of [----] d(B)A.

5.	During the most recent Performance Test, completed [date] the [turbine SNs] Units tested produced as the Adjusted Emissions for the [    ] Units as set forth in the attached table.

6.	During the most recent Far Field Sound Level Test, completed [date] the [turbine SNs] Units tested produced a Far Field Sound Level of [----] d(B)A.

7.	During the most recent Performance Test, completed [date] the [turbine Sns], combined cycle Units tested produced Exhaust Gas Energy the for the [    ] Units as set forth in the attached table.

8.	During the most recent Performance Test, completed [date] the [turbine Sns], combined cycle Units produced Exhaust Gas Temperature as set forth in the attached table.

19.	Capitalized terms used herein and not defined herein shall have the respective meanings assigned to them in the Agreement.

IN WITNESS WHEREOF, has executed and delivered this Certificate as of the       day of        , 200  .

By:

Title:

From and on Behalf of

[Name of Purchaser’s Company]

EXHIBIT G-2  PERFORMANCE TEST COMPLETION CERTIFICATE

# PERFORMANCE TEST COMPLETION CERTIFICATE

The undersigned duly authorized representative of (Name of Purchaser’s Company), under the provisions of the Agreement hereby certifies that:

1.	Performance Tests pertaining to Electrical Output and Heat Rate on the combustion turbine generator units referred to in the Agreement have been conducted (each a “Unit” and collectively the “Units”).

2.	As set forth in the Agreement, Seller guaranteed that (i) the Adjusted Electrical Output of each of the Units will be at least [-----] kW when consuming natural gas for fuel, and that in any event Seller guaranteed that the Units shall produce no less than [------] kW Adjusted Electrical Output when the Electrical Output is measured and adjusted in accordance with the Test Procedures and the Agreement and (ii) if six (6) or more Units are installed at the Facility, the average Adjusted Electrical Output of all such Units will be at least [-----] kW.

The results of the Performance Tests show that the Units produced an average Adjusted Electrical Output of ________, and that each Unit individually produced the Adjusted Electric Output set forth below:

| Unit | Adjusted Electrical Output |
| --- | --- |
| Unit No_____ [turbine SN] | ________ kW |
| Unit No_____ [turbine SN] | ________ kW |
| Unit No_____ [turbine SN] | ________ kW |

# [USE A, B, and C BELOW AS APPROPRIATE]

A.	The Adjusted Electrical Output of the Units as set forth above, individually and, if applicable, collectively on average, are greater than or equal to the Electrical Output Guarantee and, if applicable, the Optional Electric Output Guarantee, and therefore, Seller is not liable for Performance Liquidated Damages associated with Electrical Output.

B.	The Adjusted Electrical Output of [turbine SNs] Units set forth above is/are less than the Electrical Output Guarantee of [___________], but greater than the Specific Performance Electrical Output Guarantee of [____________]; therefore, the undersigned has determined that the amount of Unit Output Liquidated Damages to be assessed against the Seller for failure to meet the Electrical Output Guarantee is U.S. $_____________.

C.	The average of the Adjusted Electrical Output of the Units is less than the Optional Electrical Output Guarantee of [             ]; therefore, the undersigned has determined that the amount of Optional Output Liquidated Damages to be assessed against the Seller for failure to meet the Optional Electrical Output Guarantee is US $              .

3.	As set forth in the Agreement, Seller guaranteed that the Adjusted Heat Rate of the [turbine SNs] Units will be at least [-----] BTU/kWh(LHV) when consuming natural gas for fuel, and that in any event Seller guaranteed that the Units shall demonstrate no less than a [------] BTU/kWh(LHV) Adjusted Heat Rate when the Heat Rate is calculated and adjusted in accordance with the Test Procedures and the Agreement.  The results of the Performance Tests show that each of the [turbine SNs] Units produced the Adjusted Heat Rate set forth below:

| Unit | Adjusted Heat Rate |
| --- | --- |
| Unit No_____ [turbine SN] | ________ BTU/kWh (LHV) |
| Unit No_____ [turbine SN] | ________ BTU/kWh (LHV) |
| Unit No_____ [turbine SN] | ________ BTU/kWh (LHV) |

# [USE EITHER A OR B BELOW AS APPROPRIATE]

A.	The Adjusted Heat Rate of each of the Units as set forth above is less than or equal to the Heat Rate Guarantee and therefore, Seller is not liable for Performance Liquidated Damages associated with Heat Rate.

B.	The Adjusted Heat Rate of [turbine SNs] Units set forth above is greater than the Heat Rate Guarantee [-------------], but less than the Specific Performance Heat Rate Guarantee of [-------------]; therefore, the undersigned has determined that the amount of Heat Rate Liquidated Damages to be assessed against the Seller for failure to meet the Heat Rate Guarantee is U.S. $[----------------].

EXHIBIT H-1  TECHNICAL DIRECTION OF INSTALLATION

1.0	General.  The parties agree that as part of this Scope of Work Seller shall provide the requisite technical direction of installation (the “Technical Direction of Installation” or “TD of I”) support at the Site required for installation, start-up and correction of problems related to waived shop testing and commissioning of the Equipment.

2.0	Schedule.  Seller and Purchaser’s Representative shall coordinate the start and finish schedules of each of the TD of I personnel.  Seller shall provide a maximum two hundred forty (240) man-hours per Unit installed (straight time 40 hrs/week TD of I advisors as required to support Purchaser’s receipt of Equipment, installation, startup, commissioning and correction of problems related to waived shop testing until certified ready for testing in accordance with the Agreement. Seller shall provide a bar chart for its manpower staffing in support of the construction schedule, which shall be adjusted from time to time by Seller and Purchaser as the work progresses.  Hours worked by Seller’s TD of I personnel in excess of 40 hours straight time hours each week shall be deducted from the 240 manhour count, at the equivalent rate of one and one half straight time hours pursuant to Section 8 below.  Seller’s 40 hour work week is 8 hours per Day, Monday through Friday

3.0	Cost.  Seller shall bear each and every expense for services provided by its TD of I personnel including, but not limited to, international and local transportation, salary, lodging, per diem, taxes, work permits and expenses which costs are included within the Purchase Amount.  Any TD of I activities associated with field testing and correction of the Units which would normally be performed in the factory is included in Seller’s Scope of Work and is not counted against the 240 manhour count.

4.0	Supervision of Craft Labor.  Seller’s TD of I personnel shall not be responsible for the productivity or quality of work performed by Purchaser’s contractors and shall not have direct supervision responsibility over craft labor.

5.0	Seller Technical Direction Office Facilities.  Purchaser shall provide:

(a)	A secure, furnished private jobsite office facility of sufficient size (near the Equipment) that can accommodate 3 to 4 field engineers per Unit, where drawings, special tools, and other Seller proprietary materials and equipment can be kept and referred to or worked upon.

(b)	Purchaser shall coordinate installation of four (4) direct phone lines to Seller’s jobsite office facility and Seller shall be responsible for payment of the monthly local and long distance service and usage charges to the telephone company.

(c)	Seller’s jobsite office facility shall have HVAC and contain furnishing equivalent to that in use by Purchaser and its other subcontractor’s suitable for supporting Seller’s work.  The facility shall have adequate lighting, electrically outlets and sanitary facilities shall be accessible.  Seller shall be required to comply with the Site security and safety requirements at all times including control, use and parking restrictions relevant to Seller’s personnel’s privately owned vehicles.

6.0	Staffing Levels.

Seller shall provide biographical data and other qualifications as requested by Purchaser’s project manager for review and approval of Seller’s lead advisor (such approval not to be unreasonably withheld).

Staffing shall include:

(a)	Site manager not part of contract except in the case of large sites with 6 turbines, a site manager may be requested by the Purchaser.

(b)	Turbine Generator Installation team comprised of technical advisors skilled in mechanical erection of gas turbines and related equipment, electrical equipment installation and testing, Control System checkout, calibration and unit startup, and shall be capable of providing guidance and counsel for the following:

-	The inspection and unloading of the major components at the installation site and their placement on the foundations.

-	The setting of necessary shims between sole plates and the turbines.

-	The removal of shipping supports on the turbine and generator packages.

-	The installation of the turbine units to the proper center line and elevation.

-	The alignment of the accessory equipment and generators to the turbines.

-	The installation and checkout of conduit, piping, control wiring and instrumentation between the turbines and Seller supplied auxiliary equipment and generators.

-	Checkout and initial operation of the turbine starting equipment.

-	The sequencing and checkout of the turbine Milennium Control Panels.

-	The installation and checkout of the generator excitation/electric systems.

-	The startup of the turbine units with the Purchaser’s operating personnel.

-	Mark up two (2) sets of drawings to reflect the “as-built” condition of the equipment.  One (1) set for site records and one (1) set to be returned to GE Customer Service.

-	Installation and check out of all auxiliary and ancillary equipment provided under this Agreement.

-	Electrical checkout and powering of the control consoles.

7.0	Additional Services

In addition to providing the expertise outlined above, Seller’s personnel shall be relied upon to answer questions and provide or obtain interpretation of manufacturer supplied instructions and drawings during the execution of work (construction, erection, commissioning, etc.).  Included in this category of support are:

(a)	Confirmation that specifications and instructions to be applied during construction, erection and commissioning by the different Vendors are met and that the specified results of tests and examinations are obtained;

(b)	Corrections of construction/erection/commissioning software, if necessary, as far as design and engineering tasks are not concerned;

(c)	Confirmation that the necessary standard of quality has been sustained in all areas which could affect facts and information provided by Seller to Purchaser;

(d)	Immediate written objections to Purchaser’s representative if the standard of quality is jeopardized, and advise Purchaser’s representative in a timely manner on the implications where any work procedure may impair the Equipment warranty;

(e)	Troubleshooting, technical guidance and expertise during instrumentation and control systems loop and function checks;

(f)	Technical expertise for energization and synchronization activities performed during commissioning; and

(g)	Provide impromptu training to Facility operators during start up and commissioning.

8.0	Expected Work Week.  Purchaser anticipates that the normal work week on Site will consist of working six (6) Days per week (Monday through Saturday) for ten (10) hours per shift each work Day; however, such work hours and Days shall be adjusted to accommodate Purchaser’s general Site work schedule.  It is the intent of the parties that Purchaser shall have the flexibility to require Seller’s personnel to work more or less hours per Day than the standard work Day in support of certain construction activities.  All time worked, except for those hours worked in support of the waived shop tests, shall be subtracted from the total of Seller’s obligation set forth in Section 1.0 above.  Total TD of I hours worked in excess of the 240 manhours, subject to Sections 2 and 3 above, shall be reimbursed to Seller pursuant to a Change Order, at the following rates:

| Straight time (8hrs/Day) | = $135.00/hour (US & Canada) |
| --- | --- |
|  | $165.00/hour (International) |
| Overtime (excess of 8 hrs/Day Sundays and Holidays) = |  |
|  | $165.00/hour (US & Canada) |
|  | $248.00/hour (International) |

Additional manhours and other service rate classifications purchased will be subject to:

-	GE Aeroderivative and Package Services published rate sheet for technical assistance.

-	Required travel will be reimbursed at cost or in accordance with IRS mileage rates;

-	Travel time will be invoiced at the applicable straight time or overtime rate; and

-	Per diem will be applicable at the rate of $196.00 during all Days commencing on departure from point of origin through return or its equivalent.

9.0	Replacement of Unsatisfactory Personnel.  If any of Seller’s personnel provided under this Agreement fail, in Purchaser’s reasonable judgement, to fulfill his duties as assigned by Seller, Seller shall cause such personnel to properly perform such duties, or at the request of Purchaser replace the personnel. In the event of a replacement:

-	The replacement must be of equivalent qualifications to the person being replaced;

-	Seller shall provide Purchaser a resume of the recommended replacement;

-	The replacement must be approved by Purchaser, prior to the replacement’s   commencement of work, such approval, not to be unreasonably withheld; and

-	Seller shall bear all additional travel, living or other costs associated with removing the unsatisfactory individual and furnishing the replacement.

10.0	Supplemental Seller Personnel.  Seller’s personnel shall be direct employees of Seller, or Seller may elect to hire supplemental third party Sellers screened and trained by Seller.  In addition to any such screening and training, such personnel must have verifiable and demonstrable prior hands-on experience in installation or training as applicable to the work to be performed by such person. Seller shall provide Purchaser’s Representative resumes of all individuals selected by Seller as supplemental personnel pursuant to this Paragraph 9, and obtain Purchaser’s Representative’s prior approval of each individual’s assignment, such approval not to be unreasonably withheld.

11.0	Change of Seller’s Personnel.  Seller and Purchaser recognize that changing of personnel during the performance of the Scope of Work can be disruptive and adversely affect the timely and proper performance of the Scope of Work; however, both Seller and Purchaser realize that under certain circumstances, Seller may, on an exception basis, need to substitute personnel in the course of performance of the Scope of Work.  Seller may, on an exception basis, substitute personnel; provided that the following shall apply:

-	The replacement must be of equivalent capabilities to the person being replaced;

-	Seller shall provide Purchaser a resume of the recommended replacement;

-	Such change is for a compelling personal reason, or by mutual agreement the existing individual does not have the required skill;

-	The replacement must be approved by Purchaser prior to the replacement’s   commencement of work, such approval not to be unreasonably withheld, and,

-	Seller shall bear all additional travel, living or other costs associated with such change.

12.0	Debugging.  Seller shall provide with respect to TD of I, normal debugging of problems encountered during installation, start-up and commissioning of the equipment.  In the event debugging reveals a factory defect, Seller shall provide Purchaser written observations regarding such defect.

13.0	Release of Seller’s Personnel.  If Technical Direction of Installation Representative is/are released from site by Purchaser while the installation is in progress, the same Technical Direction of Installation Representative may not be available to return but will be replaced with a qualified Technical Direction of Installation Representative within two weeks after Company’s receipt of written request from the Purchaser for Technical Direction of Installation Representative.

14.0	Purchaser’s Responsibilities.  Purchaser will take all necessary precautions, at all times, for the safety of Company personnel at site.  This includes, but is not limited to, indoctrination of Purchaser’s safety practices, energization/de-energization of all power systems (electrical, mechanical and hydraulic) using a lock-out tag procedure, and conducting periodic safety meetings during construction and start-up.

EXHIBIT H-2  TRAINING

EXHIBIT I  CANCELLATION CHARGE

In the event Purchaser cancels this Agreement with respect to a Unit, Purchaser’s liability for cancellation charges shall not exceed the values set forth below for each Unit canceled:

| Receipt of Cancellation Notice Days After September 23, 1999 | Cancellation Charge/Fee (expressed as % of the Unit Liability Amount for the cancelled Unit) |
| --- | --- |
| 0-26 | 0 |
| 27-60 | 5 |
| 61-90 | 12 |
| 91-120 | 15 |
| 121-150 | 20 |
| 151-180 | 25 |
| 181-210 | 30 |
| 211-240 | 40 |
| 241-270 | 50 |
| 271-300 | 60 |
| 301-330 | 70 |
| 331-360 | 75 |
| 361-390 | 80 |
| 391-420 | 85 |
| 421-450 | 90 |
| 451-480 | 95 |
| After Day 481 | 100 |

Notes:

- Seller shall maintain title to the Unit when cancellation occurs prior to shipment.

- Cancellation exposure is 100% of the pro rata value of each Unit after shipment.

- The pro rata value of each Unit shall increase or decrease as applicable as a result of increases or decreases to the Unit Liability Amount due to executed Change Orders.

EXHIBIT J  QUALITY

1.0	QUALITY ASSURANCE AND CONTROL

1.1	Quality Assurance Arrangements

Seller, and its nominated Vendors shall work to defined quality assurance arrangements compliant with ISO 9001.  Seller shall indicate the results of any recent audits.

In addition to requirements detailed in ISO 9001, Seller shall:

- Ensure that all quality related activities are planned and that adequate resources are made available for these activities.

- Establish means by which all materials and components are identified through each stage of performance of the Scope of Work.  These measures will facilitate the traceability of materials as identified in the agreed quality plans.

- Arrange for the protection of the quality of the product to include delivery to the specified destination.

1.2	Vendors

Seller shall specify all quality assurance requirements to its Vendor and shall ensure that all Vendors comply with these requirements.

Seller shall undertake in respect of its nominated Vendors, where no such acceptable information is available or where the Vendor has not been subject to a quality audit within the previous 12 months, to carry out an audit of that Vendor in order to ensure that completion of works will be compliant with contract requirements.

Seller and its nominated Vendors maybe subject to a quality audit by Purchaser.

1.3	Quality Plans

Quality plans shall be prepared by Seller for all areas of activity.  These quality plans shall be submitted to Purchaser for review.

The format of the quality plans shall be agreed with Purchaser.  Seller shall ensure that all activity is carried out in accordance with the quality plans and will notify Purchaser of any deviations as they occur.

1.4	Review of Documents

Seller shall submit for review all quality plans and design documentation as may reasonably be required by Purchaser.  A schedule of drawings and documentation shall be maintained by Seller to show the current status and revision of each document.

1.5	Records

Seller shall maintain records as required by the quality plans.  All records including audit reports shall be made available for inspection by Purchaser, as required.

Seller shall generate records in a manner coincidental with the activities to which they refer, such that the quality status of each item can be readily verified.

All records shall be concisely compiled and coded.  They shall, in addition be clearly cross referenced to the parts or assemblies to which they refer.

Records shall in general, be available at the time of equipment delivery.  Such records shall include relevant certifications and build documentation together with any information which would facilitate the general traceability of component items or materials.

All records generated during the course of performance of the Scope of Work shall be retained by Seller for a minimum period of ten years from the date of Acceptance or supplied to Purchaser for its retention.

1.6	Seller’s Responsibility

Review and comment by Purchaser of the quality assurance procedures, quality plans, inspection and test arrangements operated by either Seller or his Vendors, will not relieve Seller of its obligation to provide Equipment which complies with the requirements of the Agreement.

2.0	QUALITY SURVEILLANCE

2.1	Quality Surveillance Requirements

Seller shall define the items which it proposes to Vendor together with all items for which quality plans (inspection and test plans) will be submitted.  Seller shall provide Purchaser’s Quality Assurance Manager the name of his representative authorized as having responsibility for resolving or obtaining resolution, of any problems arising in respect of the acceptability of raw materials, components, and assemblies.

Seller shall establish and maintain a documented inspection system capable of producing objective evidence that all material manufactured parts and assemblies comply with the quality requirements of the Agreement.

General information on the type of system in use by Seller shall be provided.

Seller’s inspection system shall include procedures used for controlling the following functions:

- Availability at inspection points of applicable drawings, instructions, etc and prompt removal of obsolete documents.

- Maintenance and calibration of suitable inspection and test equipment, which should comply with requirements set out in ISO 9001

- Inclusion (or referencing) on purchase orders of the necessary technical inspection and test details to meet the specified requirements and of Purchaser’s possible involvement at the Vendor’s facilities.

- Incoming, in process and final inspection and inspection of packing and marking.

- Means of identifying inspection status throughout manufacture.

- Provisions of complete inspection and test records.

Seller shall submit for review within 30 days after the execution of this Agreement, a quality plan, excluding testing and inspection on work already completed as of such submission date, in which case test records will be provided, (inspection and test plan) defining the program of quality control and inspection activities which it or its Vendors will perform in order to ensure that the manufacture and completion of the plant complies with the specified requirements.  The quality plan may be of any form to suit Seller’s system, but it shall as a minimum:

- Indicate each inspection and test point and its relative location in the production cycle including incoming, packing and site inspections.

- Indicate mandatory Seller Factory hold points for an item or process before the work can proceed.

Seller shall include in all its orders to Vendors, a note advising that all materials and equipment are subject to inspection by Purchaser.

In order to verify compliance with engineering, procurement, manufacturing requirements and program, Purchaser shall have access at all times as arranged by Seller, to all places where materials or equipment are being prepared or manufactured, including the works of Vendor’s raw materials.

Inspection of the Equipment may be by Purchaser and may include the following activities:

- Evaluation of Seller’s system and quality plans.

- Periodic monitoring to confirm the effectiveness of and Seller’s compliance with the established system procedures, quality plan and inspection and test instructions.

- Witnessing of inspections and test and/or verification of inspection records including:

a.	Compliance of raw material with specified requirements.

b.	Compliance of manufactured parts, assemblies and final items with specifications, drawings, standards and good engineering practice.

c.	Periodic inspection of Seller’s design manufacturing, installation work and the production of progress reports.

d.	Witnessing of inspections and tests.

e.	Packing for shipment including check for completeness of shipment, handling requirements, and identification.

Seller’s compliance with equipment documentation, drawing, delivery and commissioning schedules shall be monitored by Purchaser.

Raw materials, components, shop assemblies and the installation thereof, shall be subject to inspection and test by Purchaser as required by the specification and the extent practicable at all times and places during the period of manufacture.

Seller shall keep Purchaser informed, in advance, of the time of starting and of the progress of the Scope of Work in its various stages so that arrangements can be made for inspection and for test.  He shall also provide without additional charge, all reasonable facilities and assistance for the safety and convenience of Purchaser in the performance of his duties.  All of the required tests shall be made to Seller’s expense, including the cost of all samples used.

In the event of the unreasonable postponement, by Seller, of tests previously scheduled, or of the necessity tests due to unsatisfactory results of the original tests, or other reasons attributable to Seller, Seller will bear the costs incurred by Purchaser of his nominated representative in re-inspecting the non-conforming item or its replacement.

Seller’s and nominated Vendor’s quality assurance program shall identify and shall isolate items not conforming to the technical specification.  All such items shall be reported to Purchaser via a non-conformance report which shall identify:

- The identification of the item.

- The relevant specification, drawing etc including revision number.

- A sketch of the non-conformance.

- The method by which the non-conformance was identified.

- The cause of the non-conformance.

- The proposal for resolution the con-conformance.

- A concession application including the technical justification and the appropriate supporting documents if applicable.

- The proposed action to prevent re-occurrence.

Seller shall not offer, unless otherwise agreed, any item of equipment for inspection to Purchaser until all planned inspections and tests to date have been completed to the satisfaction of Seller.

Any non-conformance identified by Purchaser may be notified by issue of Purchaser’s non-conformance report to Seller.  Notification of re-inspection shall not be made until the completed non-conformance report together with any applicable concession application have been submitted to Purchaser.

The inspection and tests by Purchaser of any components or lots thereof does not relieve Seller of any responsibility whatever regarding defects or other failures which maybe found before the end of the Primary Warranty Period.

Seller shall provide a quality release certificate confirming compliance with the contract requirements and a data book containing relevant manufacturing and quality records.

Seller shall furnish Purchaser with 4 copies of the data book.

The parties agree that, in light of the fast-track nature of the project for which these Units are being supplied, and the advanced stage of manufacturing, Purchaser and Seller shall review the requirements, obligations and responsibilities set forth in this Exhibit J during two pre-inspection/quality meetings (one for the gas turbine, one for the generator). Seller shall coordinate and schedule a mutually agreed date for both meetings at Seller’s factory, with the goal of having them within two months after the Order Definition Meeting.  Seller shall document all mutually agreed adjustments to Exhibit J, issue the notes in letter form for review and agreement, and issue a final conformed letter  for subsequent endorsement by the parties and use as quality assurance guidelines.

EXHIBIT K  PROJECT PLANNING

1.	PURPOSE AND OBJECTIVES

1.1	Seller shall provide information and data required for development of a Project Schedule for the Work in accordance with the requirements of this Exhibit.  Seller’s information and data shall be provided electronically in a software which can be readily used in “Primavera Project Planner” software which will be used by Purchaser to develop the Project Schedule.  The purpose of the Project Schedule shall be to:

(1)	assure adequate planning, scheduling and reporting during the prosecution and progress of the Scope of Work by Seller in order to complete the Scope of Work in accordance with any and all milestones;

(2)	assure coordination of the efforts of Seller, his various Vendors and Purchaser furnished equipment and materials, if any;

(3)	assist Seller, and Purchaser, in monitoring the progress of the Scope of Work and in evaluating proposed changes to the Agreement and the Project Schedule.

2.	PROGRESS UPDATES

2.1	The Project Schedule shall be updated on a monthly basis and on a periodic basis throughout the duration of the Scope of Work, and until Agreement Completion.  Seller shall meet with Purchaser at the completion of each agreed upon period to review actual progress made through the date of the Project Schedule update, including dates for activities actually started and/or completed, and to review the overall percentage of the Scope of Work actually completed.  The data date of each Project Schedule update shall be the last Day of the month, or some other Day previously designated by Purchaser.  In case of disagreements at the Project Schedule update meeting concerning actual progress to date, Purchaser’s determination shall govern.

2.2	In addition to the Project Schedule updates, Seller shall submit a Monthly Contractor’s Progress Report containing the following minimum information as follows:

# MONTHLY CONTRACTOR’S PROGRESS REPORT

Timing:	Submitted 4 copies (4th of each Calendar month)

Contractor Name:

Reporting Month:

(1)	Management Summary (One Page)

-  Overall Project Situation

-  Major Activity

-  Significant Problems

(2)	Progress Review

-  Milestone Report

-  Updated Bar Chart Schedule (Current vs. Target)

-  Problems Affecting Progress

-  Decisions and Actions

-  Actions and Orientations required from Purchaser

(3)	Commercial Situation

-  Payment Status

-  Change Order Register

-  Notice of Claims

3.	RECOVERY SCHEDULE

3.1	Should the updated Project Schedule show at any time during Seller’s performance, in the sole opinion of Purchaser, that Seller is fourteen (14) or more days behind schedule for any Specific Date, Seller shall prepare a Recovery Schedule at no additional cost to Purchaser (unless Purchaser is solely responsible for the event or occurrence which has caused the schedule slippage) explaining and displaying how Seller intends to reschedule his work in order to regain compliance with the Project Schedule.

4.0 PROJECT SCHEDULE REVISIONS

4.1	If, as a result of the monthly and periodic Project Schedule update, it appears the Project Schedule no longer represents the actual prosecution and progress of the Scope of Work, Purchaser will request, and Seller shall submit, a revision to the Project Schedule.

4.2	Seller may also request revisions to the Project Schedule in the event Seller’s planning for the work is revised.  If Seller desires to make changes in the Project Schedule to reflect revisions in its method of operation and scheduling of the Scope of Work, Seller shall notify Purchaser in writing, stating the reason for the proposed revision.  In no case will Notice to Purchaser of a request for schedule revision relieve Seller of any of his obligations under this Agreement.  All Project Schedule revisions and updates shall conform to all provisions of the Agreement documents contained herein.

EXHIBIT L EQUIPMENT REQUIRING INSURABILITY CERTIFICATE

Seller shall provide assistance as necessary in order to ensure that the following Equipment is inspected by Purchaser’s Insurance Representative in attainment of an insurability certificate:

(a)	Generator

(b)	Generator Module

(c)	Gas Turbine Module

(d)	Control Room Module

(e)	Lube Oil Module

(f)		Auxiliary Module

EXHIBIT M-1  NOT USED

EXHIBIT M-2 NOT USED

EXHIBIT N-1  NOT USED

EXHIBIT N-2  OPTIONS

| Item | Notification Required to Secure Option | Quantity | Price in U.S. Dollars |
| --- | --- | --- | --- |
| Transportation Option A | 6 months | Per Unit | 5% + Seller’s Cost |
| Transportation Option B | > 3 or < 6 months | Per Unit | 7% + Seller’s Cost |
| Transportation Option C | < 3 months | Per Unit | 10% + Seller’s Cost |
| Option H - Dual Fuel System | 10 months | Per Unit | $280,000 |
| Option J - Upgrade to Dual Water Injection Skids w/Enclosures | 7 months | Per Unit | $57,000 |
| Option P1 - Exhaust Assembly (45 ft. 85 dBA) (Standard Base) | 7 months | Per Unit | $198,000 |
| Option P2 - Exhaust Assembly (60 ft. 85 dBA) (Standard Base) | 7 months | Per Unit | $236,000 |
| Option P3 - Exhaust Assembly (45 ft. 85 dBA) (Heavy Base) | 7 months | Per Unit | $233,000 |
| Option R - LM6000 Engine Level 1 Maintenance and Borescope Training | 6 months | Per Class | $28,000 |
| Option S - Modular Control Room (for up to 2 units) | 7 months | 1 | $125,000 |
| Option T - Switchgear, Generator Circuit Breaker in NEMA 3R enclosure (as described in Seller’s Published Product Specification Manual) | 7 months | Per Unit | $130,000 |
| Option U - Unit Motor Control Center | 7 months | Per Unit | $45,000 |
| Option V - Chiller Module (2200 Tons) | 7 months | Per Unit | $950,000 |
| Option W - Cooling Tower for Chiller Module | 7 months | Per Unit | $150,000 |
| Option X - O&M Manuals on CD-ROM w/Browser and Bookmarks | 6 months | Per Config. | $25,000 |
| Option Y - 3 Extra CT’s Terminated in MGTB for Redundant Relay Protection | 6 months | 1 Lot Per Unit | $23,000 |
| Storage Cost - Per Unit | Putting into storage |  | $10,800 per move |
|  | Taking out of storage |  | $8,300 per move |
|  | No charge for first 90 days |  |  |
|  | For months 4, 5 & 6 |  | $3,800 per month |
|  | Per month after month 7 |  | $4,800 per month |
| Power System Stabilizer | 6 months | Per Unit | $31,675 |

NOTE: This Agreement may be amended by Change Order to add other balance of plant equipment modules to Seller’s Scope of Work.

EXHIBIT O  HAZARDOUS MATERIAL NOTIFICATION

# HAZARDOUS AND TOXIC SUBSTANCES
DISCLOSURE REQUIREMENTS
AGREEMENT NUMBER

# Show the order identification 
on all correspondence

Seller:

Attention:

Address:                                      ZIP:

Phone Number: (     )

HAZARDOUS AND TOXIC SUBSTANCES DISCLOSURE REQUIREMENTS

The Occupational and Health Act (OSHA) of 1970, and OSHA regulation 29CFR 1910 contain hazardous and toxic substances reporting requirements.

Seller shall be required to provide the following documents, as applicable to Purchaser at the time of Agreement, if possible, but not later than ten (10) days thereafter. A copy of the Material Safety Data Sheet, (Form OSHA-20), or equivalent, must accompany each shipment of hazardous or toxic substances to Purchaser.  The following documents may be required for more than one item within the Agreement.

MATERIAL SAFETY DATA SHEET

The Material Safety Data Sheet (Form OSHA-20), or equivalent is required for each material containing a chemical substance which: (i) is regulated by any Federal law or rule, (ii) is listed in the latest edition of the National Institute for Occupational Safety and Health Registry of Toxic Effects of Chemical Substances. (iii) testing has yielded positive evidence of an acute or chronic health hazard, or (iv) has a Material Safety Data Sheet available to Seller indicating that the material may pose a hazard to human health.

# -AND/OR-

SELLER DISCLAIMER STATEMENT

Seller may alternatively submit a disclaimer statement set forth below:

# HAZARDOUS AND TOXIC SUBSTANCES DISCLAIMER

Seller hereby swears or affirms that the material furnished on this Purchase Order does not, to its best knowledge, contain any toxic substances or harmful physical agents as defined under 29CFR 1910.  In the event Seller discovers that such hazardous and toxic substances or agents are to be supplied, an appropriate Material Safety Data Sheet (Form OSHA-20), or equivalent shall be immediately supplied to Purchaser.

| ________________________ Signature of Company Officer | Date: _______________________________ |
| --- | --- |
| ________________________ Title |  |

NONCOMPLIANCE

Seller assumes all responsibility for its failure to supply Purchaser a completed Material Safety Data Sheet (Form OSHA-20), or equivalent or a Seller Disclaimer Statement as applicable.

EXHIBIT P  UNIT SERIAL NUMBER

UNIT SERIAL NUMBERS:

| Unit 19 : 310889 |  |
| --- | --- |
| Unit 20 : 310890 |  |
| Unit 23 : 309994 |  |
| Unit 24 : 310891 |  |

EXHIBIT Q SAMPLE PACKING LIST

| PKG. # | DESCRIPTION | GROSS WT. | L | W | H | CFT. |
| --- | --- | --- | --- | --- | --- | --- |
| PC 1 | LM6000 Generator Base | 68000 | 337 | 172 | 178 | 5971 |
| PC 2 | Turbine Base | 120000 | 371 | 172 | 178 | 6573 |
| PC 3 | Brush Generator | 176000 | 301 | 150 | 130 | 3397 |
| PC 4 | Roof Skid | 44000 | 470 | 172 | 149 | 6971 |
| Box 5 | V.B.V. Silencer | 17500 | 174 | 75 | 148 | 1118 |
| Box 6 | V.B.V. Duct | 15600 | 158 | 150 | 106 | 1454 |
| Box 7 | V.B.V. Hood | 3480 | 140 | 103 | 60 | 501 |
| PC 8 | L.H. Coil Module “A” | 42000 | 400 | 129 | 149 | 4449 |
| PC 9 | R.H. Coil Module “B” | 42000 | 400 | 129 | 149 | 4449 |
| PC 10 | Plenum | 24400 | 394 | 146 | 149 | 4960 |
| Box 11 | Raincap | 1320 | 82 | 82 | 54 | 210 |
| Box 12 | Raincap | 1320 | 82 | 82 | 54 | 210 |
| Box 13 | Roof Skid silencer | 2290 | 80 | 80 | 76 | 281 |
| Box 14 | Roof Skid Silencer | 2290 | 80 | 80 | 76 | 281 |
| Box 15 | Electrical Shiploose | 1105 | 96 | 48 | 38 | 101 |
| Box 16 | Generator Exhaust Hood | 9070 | 174 | 160 | 87 | 1314 |
| Box 17 | Neutral Cubicle | 4400 | 96 | 68 | 120 | 453 |
| Box 18 | Lineside Cubicle | 2800 | 68 | 68 | 124 | 332 |
| Box 19 | Mechanical shiploose | 2785 | 170 | 48 | 43 | 203 |
| Box 20 | Exhaust Flashing | 725 | 62 | 62 | 17 | 38 |
| Box 21 | Zurn Coupling | 1225 | 120 | 31 | 33 | 71 |
| Box 22 | Demister | 720 | 36 | 36 | 74 | 56 |
| Box 23 | Roof Skid Transition | 1710 | 148 | 78 | 34 | 227 |
| Box 24 | Nuts & Bolts Shiploose | 1245 | 48 | 48 | 36 | 48 |
| Box 25 | Paint (1-5 Gal.) | 130 | 24 | 18 | 23 | 6 |
| Box 26 | Generator Transition Throat | 1800 | 125 | 125 | 39 | 353 |
| Skid 27 | CO2 Bracket | 600 | 91 | 24 | 35 | 44 |
| Box 28 | Run Down Tanks (4) | 1455 | 106 | 46 | 30 | 85 |
| Box 29 | Water Injection Skid | 7620 | 195 | 62 | 64 | 448 |
| Box 30 | Shear Lugs (8) | 1020 | 45 | 25 | 17 | 11 |
| Box 31 | Pressure Balance Pipe | 500 | 54 | 48 | 24 | 36 |
| Box 32 | Walkways & Handrails | 3640 | 152 | 60 | 44 | 232 |
| Box 33 | Coil Module Parts | 1225 | 44 | 44 | 38 | 43 |
| Skid 34 | Support Structure & Ladder | 5620 | 312 | 81 | 62 | 907 |
| Box 35 | H-Frame | 2085 | 174 | 35 | 39 | 137 |
| Box 36 | Auxiliary Skid | 17000 | 180 | 140 | 100 | 1458 |
| Box 37 | CO2 Enclosure | 2535 | 106 | 34 | 106 | 280 |
| Box 38 | Sprint Skid | 2560 | 84 | 73 | 67 | 238 |
| Box 39 | Batteries & Racks | 1210 | 65 | 37 | 37 | 51 |
| Box 40 | Battery Chargers (2) | 610 | 44 | 33 | 49 | 41 |
| Box 41 | Generator Fan Expansion Joints | 450 | 51 | 51 | 24 | 36 |
| Box 42 | Ruffneck Heaters (2) | 615 | 66 | 35 | 38 | 51 |
| Box 43 | Cold Weather Enclosure/Gauge Panel | 1180 | 118 | 111 | 17 | 129 |
| Box 44 | CO2 Bottles (8) | 2700 | 37 | 37 | 72 | 57 |
| Box 45 | Flex Hoses | 260 | 64 | 19 | 14 | 10 |
| Box 46 | Misc. Shiploose | 145 | 34 | 26 | 17 | 9 |
| Box 47 | Acid (45 GALS.) | 640 | 48 | 19 | 36 | 19 |
| Box 48 | Control Panel | 4125 | 128 | 44 | 102 | 332 |
| Box 49 | Engine Lift Fixture | 1440 | 128 | 76 | 17 | 96 |
| Box 50 | Alignment Tool | 505 | 104 | 29 | 31 | 54 |
| Box 51 | Discharge Heads | 125 | 27 | 27 | 14 | 6 |
| Box 52 | Hood for Aux. Skid | 1290 | 77 | 52 | 83 | 192 |
| Box 53 | Pre-Filter Doors (16) | 2090 | 128 | 58 | 52 | 223 |
| Box 54 | Pre-Filter Doors (16) | 2015 | 128 | 58 | 52 | 223 |
| Box 55 | TCP Shiploose | 80 | 27 | 27 | 14 | 6 |
| Box 56 | CO2 Bottles (4) | 1405 | 26 | 26 | 72 | 28 |
| Box 57 | LG. Lift Pins (4) SM. Lift Pins (4) | 7260 | 114 | 86 | 30 | 170 |
| PC 58 | Donaldson Spreader Bar | 4650 | 440 | 33 | 12 | 101 |
| PC 59 | Main Unit Spreader Bar | 1800 | 211 | 26 | 12 | 116 |
| PC 60 | Generator Spreader Bar | 1400 | 133 | 126 | 12 | 116 |
| Box 61 | Slings & Shackles | 10000 | 136 | 96 | 42 | 317 |
| PC 62 | Vertical Stack Duct | 13110 | 180 | 131 | 132 | 1801 |
| PC 63 | Vertical Stack Duct | 23350 | 361 | 131 | 132 | 3613 |
| PC 64 | Vertical Duct | 33250 | 361 | 150 | 150 | 4701 |
| PC 65 | Breech Duct | 37750 | 181 | 197 | 151 | 3116 |
| Lot 66 | Ladder & Platforms | 10000 | 480 | 110 | 60 | 2933 |

EXHIBIT R  NOT USED

EXHIBIT S  FINAL WAIVER  OF LIENS FORM

AFFIDAVIT AND RELEASE OF LIEN

THE STATE OF ________	§

COUNTY OF ___________	§

[Seller Name] (the “Seller”) hereby acknowledges that it has been paid in full for all design, labor, materials, equipment, supplies and services, for the supply of GTG packages for the [            project name                  ], (“the Project”) pursuant to the Purchase Agreement No. [           ] dated [--------] , between [Seller Name] and [--------](the “Purchaser”).

[Seller Name] hereby acknowledges and certifies that it has been paid all sums owing and that it has no further claims against [-------], or any subsidiary, affiliate or parent of [-------] except for the outstanding unresolved Change Order listed in Appendix A to this Affidavit.  [if none, delete all of paragraph after “except for...”]

[Seller Name] further covenants and warrants that the Project is free from all liens and claims for payment by any subcontractor, materialman or employee.

In consideration for such full payment, [Seller Name], on behalf of itself and its predecessors, employees, agents, officers, directors, shareholders, representatives, attorneys, successors, insurers and assigns, subcontractors and on behalf of any other persons claiming by, through or under [Seller Name], does hereby waive, release, and relinquish its rights to and discharge, release and acquit [-------], its subsidiaries, affiliates and parent and its employees, agents, officers, directors, shareholders, representatives, attorneys, successors, insurers, assigns and subcontractors, from any and all causes of action, claims, demands, debts, liabilities, expenses or costs of any kind and every character and nature whatsoever, including but not limited to any lien claims or rights, whether known or unknown, contingent or fixed, either in or arising out of the law of contracts, torts or property rights, whether arising under statutory law or common law, at law or in equity, with respect to the above-referenced property.  Furthermore, [Seller Name] agrees to Indemnify and hold harmless [Purchaser Name], its subsidiaries, affiliates and parent and all other persons or entities released by [Seller Name] above against the full amount of any liability, loss, claim, damage, or expense (including attorneys’ fees and any judgment required to be paid) in connection with any of the matters it has released in the event any person should assert against such released person or entity a claim under assignment or title derivative from [Seller Name] and in connection with any claims made in connection with or relating to [Seller Name] provision of design, labor, materials, equipment, supplies and/or services on the above-referenced property.

EXECUTED this _________ day of ______________________, 200__.

[Seller Name] ___________________

By:____________________________

Name:__________________________

Print or Type

Title:___________________________

SWORN TO AN SUBSCRIBED BEFORE ME, under my official hand and seal of office on this ____ day of ___________________, 200__.

______________________________

Notary Public in and for

the State of ___________

My Commission Expires:
_____________________

(SEAL)

# AFFIDAVIT

THE STATE OF ________	§

COUNTY OF ___________	§

BEFORE ME, the undersigned Notary Public, on this day personally came and appeared                       known to me to be the individual whose name is subscribed to the foregoing RELEASE OF LIEN and being duly sworn, did state and acknowledge on his oath that he is the                     of                           , is authorized to execute and deliver the foregoing on behalf of                          as an act and deed of that entity for the purposes and consideration therein expressed.

GIVEN UNDER MY HAND AND SEAL OF OFFICE this           day of                 , 200    .

______________________________

Notary Public in and for

the State of ___________.

(SEAL)

My Commission Expires:

_____________________

# CERTIFICATION

This is to certify that all work covered by Invoice No. [__________]  is complete and that the invoice is correct, authentic and the only one issued for the work described therein.

[      NAME OF OFFICER      ]

# A C K N O W L E D G E M E N T

(COUNTRY) [                       ]

(CITY)    [                       ]

Before me, a Notary Public for and in the City of [     CITY     ], [     COUNTRY     ], this [     DATE      ] personally appeared [     NAME OF OFFICER    ], exhibiting to me his Residence Certificate No. [               ] issued at [                    ], [     NAME OF OFFICER    ] on [             ] to be the same person who executed the foregoing Certification acknowledged to me that the same is a free and voluntary act and deed and to me known as the same person who acknowledged this certification.

In witness hereof, I have hereunto set my hand and affixed my notarial seal this [      ] of [          ], 200[---] in

[   NAME OF CITY   ] [     COUNTRY     ].

[       NAME OF NOTARY       ]

Notary Public, State of ______.

My Commission Expires __________

Doc. No. ____________

Page No. ____________

Book No. ____________

Series of 200

# W  I  T  N  E  S  S  :

# [         NAME          ]								[          NAME    ]

EXHIBIT T  NOT USED

EXHIBIT U  NOT USED