ABNORMAL OPERATION REPORT

| Date of Abnormal Operation: | 01-15-02 |
| --- | --- |
| Date of Report: | 01-17-02 |

PERSON SUBMITTING REPORT TO COMPANY REPORTING UNIT

| Name: | Ted Lindblad |
| --- | --- |
| Job Title: | Mechanic |
| Business Telephone: | 651-982-2127 |

LOCATION OF CONDITION

| Region: | Minneapolis |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Location: | North Branch, Mn. |  |  |  |  |  |
| Operating Company: | Northern Natural Gas Co. |  |  |  |  |  |
| Pipeline Name: |  |  |  | Number: |  |  |
| Station or Mile Post: |  |  |  |  |  |  |
| Compressor/Plant: | North Branch Compressor Station |  |  |  |  |  |
| State: | MN. |  |  |  |  |  |
| County/Parish: | Chisago |  |  |  |  |  |
| Section: | Township:35n |  | Range:21w |  |  | Survey: |
| Nearest Road or Street Address (where applicable): |  | Forest Blvd. 420th street |  |  |  |  |

SIGNIFICANT DETAILS OF CONDITION

A BSD occurred because while routine maintenance work was being performed on a compressor (unit #3) the lead line suction valve for that unit was leaking enough in the closed position that when the compressor valve caps were removed, the gas detection system triggered a BSD.

PERSONNEL NOTIFIED

| Control Center: | Bart in gas control was notified. |
| --- | --- |
| Supervision: |  |
| Other Location(s): |  |

PERSONNEL AND EQUIPMENT DISPATCHED

Rick Watts, Jim Deming, Matt Rue, Mike Waldenburg, Randy Coe, and Ted Lindblad.

ACTIONS TAKEN

Jim Deming reset the plant to ready for a engine restart of unit #2. Ted Lindblad, Rick Watts, Randy Coe, Matt Rue, and Mike Waldenburg replaced two compressor valves and caps and vented building, by opening up windows and doors. Ted and Jim started #2 at 11:30 hrs.

ANALYSIS AND POSSIBLE ACTIONS TO PREVENT RECURRENCE

Work is going to be delayed (that portion of MP-2) until we can remove and replace that suction valve. Somehow we have 3 suction valves in service with no grease zerts in them. Contaminants in the system have evide3ntly collected on the ball / sealing area of that valve.

REVIEW PER OP 10.108

| Date:- | 01-17-01 |
| --- | --- |
| Participants: | Team North Branch. |
| Comment(s): |  |