To: Kurt Anderson

From: Russ Leach

Date: 4/12/02

Subject: Another Comparison of Topas 1000 Meter to Turbine kWh Meter

Kurt:

This is a follow up on the last letter dated 4/4/02 where I checked the accuracy of the turbine meter in turbine #32A with a Topas 1000 meter.

I put the Topas on turbine #89 on 4/4/02 at 6:06pm and let it run until 9:21am on 4/11/02. It still looks like the turbine meter is reading ok since I saw only about 1% difference between the two meters. At least it does not explain the very large difference between the turbine meters and the substation meters, which looks to be caused by lost data due to issues with the SCADA system.

When we started the test on 4/4/02 at 6:06pm, the reading from the turbine meter was:

2450242kWh Produced

5134kWh Consumed

When we ended the test on 4/11/02 at 9:21am, the reading from the turbine meter was:

2557272kWh Produced

5174kWh Consumed

The difference between these values is:

107030kWh Produced

40kWh consumed

Subtracting these two leaves 106990kWh for the period. This is the value that is compared to the Topas.

Going to the end of the table below and adding the energy together for the three phases gives 105702.5kWh produced for this time period as seen by the Topas.

As you can see the turbine read higher by 1.2%

Like last time, the actual value is a little closer than this. I learned that when you download data from the Topas, the last data set is logging data and therefore is not downloaded. This caused us to be missing the last 10-minute average from the Topas. Since the turbine was running at full power when we downloaded, 10 minutes at 1500kW gives us 250kWh. Adding this to 105702.5kWh gives 105952.5kWh from the Topas. This gives a difference of .98%.

I hope this helps. Please call if you need any more information.

Thank You

Russ Leach

# Data from Topas 1000 Meter

| Column 1 : Energy Phase1 [Wh] |  |  |  |  |
| --- | --- | --- | --- | --- |
| Column 2 : Energy Phase2 [Wh] |  |  |  |  |
| Column 3 : Energy Phase3 [Wh] |  |  |  |  |
| Time | Column 39813 | Column 1 | Column 2 | Column 3 |
| 04.04.2002 18:10:00 | ,000000 | 0 | 0 | 0 |
| 04.04.2002 18:20:00 | ,000000 | 2338,9 | 1557,24 | 2097,41 |
| 04.04.2002 18:30:00 | ,000000 | 6519,06 | 5014,15 | 6056,57 |
| 04.04.2002 18:40:00 | ,000000 | 11138,3 | 8957,27 | 10461,9 |
| 04.04.2002 18:50:00 | ,000000 | 15896,5 | 13042,1 | 14993,5 |
| 04.04.2002 19:00:00 | ,000000 | 21652,4 | 18140,6 | 20593,8 |
| 04.04.2002 19:10:00 | ,000000 | 23785,6 | 19510 | 22514,5 |
| 04.04.2002 19:20:00 | ,000000 | 29535,8 | 24599 | 28097,6 |
| 04.04.2002 19:30:00 | ,000000 | 34357,6 | 28773,4 | 32720,9 |
| 04.04.2002 19:40:00 | ,000000 | 44717,3 | 38625,7 | 42941,6 |
| 04.04.2002 19:50:00 | ,000000 | 54815,6 | 48283,8 | 52898,7 |
| 04.04.2002 20:00:00 | ,000000 | 66989,4 | 60096,4 | 64946,6 |
| 04.04.2002 20:10:00 | ,000000 | 78078,9 | 70830,6 | 75911,2 |
| 04.04.2002 20:20:00 | ,000000 | 88759,7 | 81204,9 | 86507,3 |
| 04.04.2002 20:30:00 | ,000000 | 99546,9 | 91704,6 | 97251,5 |
| 04.04.2002 20:40:00 | ,000000 | 110506 | 102377 | 108194 |
| 04.04.2002 20:50:00 | ,000000 | 120901 | 112461 | 118536 |
| 04.04.2002 21:00:00 | ,000000 | 132538 | 123816 | 130166 |
| 04.04.2002 21:10:00 | ,000000 | 151532 | 142749 | 149270 |
| 04.04.2002 21:20:00 | ,000000 | 174613 | 165896 | 172500 |
| 04.04.2002 21:30:00 | ,000000 | 209776 | 201342 | 207954 |
| 04.04.2002 21:40:00 | ,000000 | 253234 | 245276 | 251847 |
| 04.04.2002 21:50:00 | ,000000 | 295407 | 287946 | 294450 |
| 04.04.2002 22:00:00 | ,000000 | 341521 | 334616 | 341038 |
| 04.04.2002 22:10:00 | ,000000 | 383335 | 376922 | 383287 |
| 04.04.2002 22:20:00 | ,000000 | 421891 | 415910 | 422238 |
| 04.04.2002 22:30:00 | ,000000 | 461273 | 455722 | 462031 |
| 04.04.2002 22:40:00 | ,000000 | 502578 | 497491 | 503769 |
| 04.04.2002 22:50:00 | ,000000 | 552009 | 547522 | 553712 |
| 04.04.2002 23:00:00 | ,000000 | 608465 | 604878 | 610823 |
| 04.04.2002 23:10:00 | ,000000 | 660382 | 657603 | 663343 |
| 04.04.2002 23:20:00 | ,000000 | 707734 | 705611 | 711229 |
| 04.04.2002 23:30:00 | ,000000 | 743082 | 741317 | 746907 |
| 04.04.2002 23:40:00 | ,000000 | 770918 | 769406 | 775021 |
| 04.04.2002 23:50:00 | ,000000 | 803221 | 802148 | 807721 |
| 05.04.2002 00:00:00 | ,000000 | 842239 | 841796 | 847249 |
| 05.04.2002 00:10:00 | ,000000 | 882725 | 882888 | 888228 |
| 05.04.2002 00:20:00 | ,000000 | 914180 | 914706 | 920018 |
| 05.04.2002 00:30:00 | ,000000 | 936235 | 936977 | 942362 |
| 05.04.2002 00:40:00 | ,000000 | 958361 | 959362 | 964763 |
| 05.04.2002 00:50:00 | ,000000 | 987378 | 988806 | 994084 |
| 05.04.2002 01:00:00 | ,000000 | 1,02126e+06 | 1,02324e+06 | 1,02831e+06 |
| 05.04.2002 01:10:00 | ,000000 | 1,06331e+06 | 1,06607e+06 | 1,07084e+06 |
| 05.04.2002 01:20:00 | ,000000 | 1,098e+06 | 1,10138e+06 | 1,10588e+06 |
| 05.04.2002 01:30:00 | ,000000 | 1,12454e+06 | 1,12836e+06 | 1,13265e+06 |
| 05.04.2002 01:40:00 | ,000000 | 1,16426e+06 | 1,1688e+06 | 1,1728e+06 |
| 05.04.2002 01:50:00 | ,000000 | 1,19263e+06 | 1,19765e+06 | 1,20137e+06 |
| 05.04.2002 02:00:00 | ,000000 | 1,22145e+06 | 1,227e+06 | 1,23043e+06 |
| 05.04.2002 02:10:00 | ,000000 | 1,25035e+06 | 1,25639e+06 | 1,25952e+06 |
| 05.04.2002 02:20:00 | ,000000 | 1,27835e+06 | 1,28485e+06 | 1,28777e+06 |
| 05.04.2002 02:30:00 | ,000000 | 1,30858e+06 | 1,31559e+06 | 1,31832e+06 |
| 05.04.2002 02:40:00 | ,000000 | 1,34251e+06 | 1,35012e+06 | 1,35262e+06 |
| 05.04.2002 02:50:00 | ,000000 | 1,37654e+06 | 1,38483e+06 | 1,38704e+06 |
| 05.04.2002 03:00:00 | ,000000 | 1,41324e+06 | 1,42233e+06 | 1,42416e+06 |
| 05.04.2002 03:10:00 | ,000000 | 1,44217e+06 | 1,45184e+06 | 1,4534e+06 |
| 05.04.2002 03:20:00 | ,000000 | 1,46756e+06 | 1,47776e+06 | 1,47908e+06 |
| 05.04.2002 03:30:00 | ,000000 | 1,49335e+06 | 1,50406e+06 | 1,50517e+06 |
| 05.04.2002 03:40:00 | ,000000 | 1,51876e+06 | 1,52996e+06 | 1,53093e+06 |
| 05.04.2002 03:50:00 | ,000000 | 1,55014e+06 | 1,56194e+06 | 1,56274e+06 |
| 05.04.2002 04:00:00 | ,000000 | 1,58032e+06 | 1,59265e+06 | 1,59325e+06 |
| 05.04.2002 04:10:00 | ,000000 | 1,61385e+06 | 1,62673e+06 | 1,62713e+06 |
| 05.04.2002 04:20:00 | ,000000 | 1,64839e+06 | 1,66188e+06 | 1,66211e+06 |
| 05.04.2002 04:30:00 | ,000000 | 1,67004e+06 | 1,68386e+06 | 1,68403e+06 |
| 05.04.2002 04:40:00 | ,000000 | 1,71806e+06 | 1,73269e+06 | 1,73264e+06 |
| 05.04.2002 04:50:00 | ,000000 | 1,76266e+06 | 1,77807e+06 | 1,77784e+06 |
| 05.04.2002 05:00:00 | ,000000 | 1,81724e+06 | 1,83367e+06 | 1,83312e+06 |
| 05.04.2002 05:10:00 | ,000000 | 1,86871e+06 | 1,8861e+06 | 1,88526e+06 |
| 05.04.2002 05:20:00 | ,000000 | 1,91705e+06 | 1,93532e+06 | 1,93419e+06 |
| 05.04.2002 05:30:00 | ,000000 | 1,9639e+06 | 1,98299e+06 | 1,98156e+06 |
| 05.04.2002 05:40:00 | ,000000 | 2,02188e+06 | 2,04213e+06 | 2,04022e+06 |
| 05.04.2002 05:50:00 | ,000000 | 2,07899e+06 | 2,10036e+06 | 2,09793e+06 |
| 05.04.2002 06:00:00 | ,000000 | 2,14444e+06 | 2,16705e+06 | 2,16401e+06 |
| 05.04.2002 06:10:00 | ,000000 | 2,21653e+06 | 2,2405e+06 | 2,23678e+06 |
| 05.04.2002 06:20:00 | ,000000 | 2,29658e+06 | 2,32205e+06 | 2,31758e+06 |
| 05.04.2002 06:30:00 | ,000000 | 2,37861e+06 | 2,40566e+06 | 2,40037e+06 |
| 05.04.2002 06:40:00 | ,000000 | 2,46079e+06 | 2,48944e+06 | 2,48331e+06 |
| 05.04.2002 06:50:00 | ,000000 | 2,52826e+06 | 2,55808e+06 | 2,55142e+06 |
| 05.04.2002 07:00:00 | ,000000 | 2,53872e+06 | 2,56841e+06 | 2,56191e+06 |
| 05.04.2002 07:10:00 | ,000000 | 2,54239e+06 | 2,57201e+06 | 2,5656e+06 |
| 05.04.2002 07:20:00 | ,000000 | 2,55135e+06 | 2,58065e+06 | 2,57453e+06 |
| 05.04.2002 07:30:00 | ,000000 | 2,56293e+06 | 2,59201e+06 | 2,58614e+06 |
| 05.04.2002 07:40:00 | ,000000 | 2,57513e+06 | 2,60394e+06 | 2,59834e+06 |
| 05.04.2002 07:50:00 | ,000000 | 2,58909e+06 | 2,61769e+06 | 2,61236e+06 |
| 05.04.2002 08:00:00 | ,000000 | 2,59564e+06 | 2,6239e+06 | 2,61892e+06 |
| 05.04.2002 08:10:00 | ,000000 | 2,60407e+06 | 2,63206e+06 | 2,62737e+06 |
| 05.04.2002 08:20:00 | ,000000 | 2,6096e+06 | 2,63727e+06 | 2,6329e+06 |
| 05.04.2002 08:30:00 | ,000000 | 2,62519e+06 | 2,65273e+06 | 2,64858e+06 |
| 05.04.2002 08:40:00 | ,000000 | 2,63122e+06 | 2,65835e+06 | 2,65454e+06 |
| 05.04.2002 08:50:00 | ,000000 | 2,63662e+06 | 2,6633e+06 | 2,65986e+06 |
| 05.04.2002 09:00:00 | ,000000 | 2,644e+06 | 2,67021e+06 | 2,66716e+06 |
| 05.04.2002 09:10:00 | ,000000 | 2,65028e+06 | 2,67603e+06 | 2,67334e+06 |
| 05.04.2002 09:20:00 | ,000000 | 2,65742e+06 | 2,68268e+06 | 2,68033e+06 |
| 05.04.2002 09:30:00 | ,000000 | 2,66306e+06 | 2,68784e+06 | 2,6858e+06 |
| 05.04.2002 09:40:00 | ,000000 | 2,67664e+06 | 2,70115e+06 | 2,69936e+06 |
| 05.04.2002 09:50:00 | ,000000 | 2,7122e+06 | 2,73687e+06 | 2,73517e+06 |
| 05.04.2002 10:00:00 | ,000000 | 2,75543e+06 | 2,78047e+06 | 2,77874e+06 |
| 05.04.2002 10:10:00 | ,000000 | 2,82238e+06 | 2,84828e+06 | 2,84618e+06 |
| 05.04.2002 10:20:00 | ,000000 | 2,87262e+06 | 2,89912e+06 | 2,89685e+06 |
| 05.04.2002 10:30:00 | ,000000 | 2,91745e+06 | 2,94445e+06 | 2,94205e+06 |
| 05.04.2002 10:40:00 | ,000000 | 2,97418e+06 | 3,00193e+06 | 2,99926e+06 |
| 05.04.2002 10:50:00 | ,000000 | 3,02733e+06 | 3,05576e+06 | 3,05283e+06 |
| 05.04.2002 11:00:00 | ,000000 | 3,09321e+06 | 3,12263e+06 | 3,11922e+06 |
| 05.04.2002 11:10:00 | ,000000 | 3,15423e+06 | 3,1845e+06 | 3,18071e+06 |
| 05.04.2002 11:20:00 | ,000000 | 3,20377e+06 | 3,23461e+06 | 3,23061e+06 |
| 05.04.2002 11:30:00 | ,000000 | 3,24764e+06 | 3,2789e+06 | 3,27476e+06 |
| 05.04.2002 11:40:00 | ,000000 | 3,28418e+06 | 3,31566e+06 | 3,31153e+06 |
| 05.04.2002 11:50:00 | ,000000 | 3,30841e+06 | 3,33979e+06 | 3,33584e+06 |
| 05.04.2002 12:00:00 | ,000000 | 3,32365e+06 | 3,35475e+06 | 3,35104e+06 |
| 05.04.2002 12:10:00 | ,000000 | 3,34242e+06 | 3,37341e+06 | 3,3699e+06 |
| 05.04.2002 12:20:00 | ,000000 | 3,35654e+06 | 3,38733e+06 | 3,38408e+06 |
| 05.04.2002 12:30:00 | ,000000 | 3,37521e+06 | 3,4059e+06 | 3,40288e+06 |
| 05.04.2002 12:40:00 | ,000000 | 3,39956e+06 | 3,43023e+06 | 3,42738e+06 |
| 05.04.2002 12:50:00 | ,000000 | 3,42828e+06 | 3,45902e+06 | 3,4563e+06 |
| 05.04.2002 13:00:00 | ,000000 | 3,45674e+06 | 3,4875e+06 | 3,48489e+06 |
| 05.04.2002 13:10:00 | ,000000 | 3,482e+06 | 3,51274e+06 | 3,51031e+06 |
| 05.04.2002 13:20:00 | ,000000 | 3,49211e+06 | 3,52253e+06 | 3,52042e+06 |
| 05.04.2002 13:30:00 | ,000000 | 3,5137e+06 | 3,5441e+06 | 3,5422e+06 |
| 05.04.2002 13:40:00 | ,000000 | 3,55049e+06 | 3,58118e+06 | 3,57936e+06 |
| 05.04.2002 13:50:00 | ,000000 | 3,57758e+06 | 3,60836e+06 | 3,6067e+06 |
| 05.04.2002 14:00:00 | ,000000 | 3,60015e+06 | 3,63092e+06 | 3,62947e+06 |
| 05.04.2002 14:10:00 | ,000000 | 3,63278e+06 | 3,66372e+06 | 3,66242e+06 |
| 05.04.2002 14:20:00 | ,000000 | 3,65804e+06 | 3,68898e+06 | 3,6879e+06 |
| 05.04.2002 14:30:00 | ,000000 | 3,67987e+06 | 3,71066e+06 | 3,70989e+06 |
| 05.04.2002 14:40:00 | ,000000 | 3,70229e+06 | 3,73296e+06 | 3,7325e+06 |
| 05.04.2002 14:50:00 | ,000000 | 3,71635e+06 | 3,74671e+06 | 3,74665e+06 |
| 05.04.2002 15:00:00 | ,000000 | 3,72129e+06 | 3,75104e+06 | 3,75152e+06 |
| 05.04.2002 15:10:00 | ,000000 | 3,72687e+06 | 3,75638e+06 | 3,75714e+06 |
| 05.04.2002 15:20:00 | ,000000 | 3,7321e+06 | 3,76101e+06 | 3,76233e+06 |
| 05.04.2002 15:30:00 | ,000000 | 3,73232e+06 | 3,7609e+06 | 3,76249e+06 |
| 05.04.2002 15:40:00 | ,000000 | 3,73788e+06 | 3,76613e+06 | 3,76806e+06 |
| 05.04.2002 15:50:00 | ,000000 | 3,73974e+06 | 3,76728e+06 | 3,76978e+06 |
| 05.04.2002 16:00:00 | ,000000 | 3,7489e+06 | 3,77591e+06 | 3,77891e+06 |
| 05.04.2002 16:10:00 | ,000000 | 3,76162e+06 | 3,78821e+06 | 3,79171e+06 |
| 05.04.2002 16:20:00 | ,000000 | 3,776e+06 | 3,80218e+06 | 3,80618e+06 |
| 05.04.2002 16:30:00 | ,000000 | 3,78984e+06 | 3,8156e+06 | 3,82009e+06 |
| 05.04.2002 16:40:00 | ,000000 | 3,79949e+06 | 3,82469e+06 | 3,82975e+06 |
| 05.04.2002 16:50:00 | ,000000 | 3,81069e+06 | 3,83541e+06 | 3,84099e+06 |
| 05.04.2002 17:00:00 | ,000000 | 3,82474e+06 | 3,8491e+06 | 3,85513e+06 |
| 05.04.2002 17:10:00 | ,000000 | 3,8425e+06 | 3,86661e+06 | 3,87303e+06 |
| 05.04.2002 17:20:00 | ,000000 | 3,85873e+06 | 3,88255e+06 | 3,88937e+06 |
| 05.04.2002 17:30:00 | ,000000 | 3,8765e+06 | 3,90005e+06 | 3,90729e+06 |
| 05.04.2002 17:40:00 | ,000000 | 3,88575e+06 | 3,90881e+06 | 3,91654e+06 |
| 05.04.2002 17:50:00 | ,000000 | 3,8975e+06 | 3,9202e+06 | 3,92835e+06 |
| 05.04.2002 18:00:00 | ,000000 | 3,90708e+06 | 3,92934e+06 | 3,93795e+06 |
| 05.04.2002 18:10:00 | ,000000 | 3,9122e+06 | 3,9339e+06 | 3,94301e+06 |
| 05.04.2002 18:20:00 | ,000000 | 3,91697e+06 | 3,93807e+06 | 3,94771e+06 |
| 05.04.2002 18:30:00 | ,000000 | 3,92258e+06 | 3,94305e+06 | 3,95323e+06 |
| 05.04.2002 18:40:00 | ,000000 | 3,93255e+06 | 3,95255e+06 | 3,96322e+06 |
| 05.04.2002 18:50:00 | ,000000 | 3,93829e+06 | 3,95772e+06 | 3,96891e+06 |
| 05.04.2002 19:00:00 | ,000000 | 3,94548e+06 | 3,96435e+06 | 3,97608e+06 |
| 05.04.2002 19:10:00 | ,000000 | 3,94982e+06 | 3,9681e+06 | 3,98036e+06 |
| 05.04.2002 19:20:00 | ,000000 | 3,95731e+06 | 3,97509e+06 | 3,98786e+06 |
| 05.04.2002 19:30:00 | ,000000 | 3,96876e+06 | 3,98618e+06 | 3,99939e+06 |
| 05.04.2002 19:40:00 | ,000000 | 3,98059e+06 | 3,9977e+06 | 4,01129e+06 |
| 05.04.2002 19:50:00 | ,000000 | 3,99451e+06 | 4,01142e+06 | 4,02532e+06 |
| 05.04.2002 20:00:00 | ,000000 | 4,00418e+06 | 4,02081e+06 | 4,03501e+06 |
| 05.04.2002 20:10:00 | ,000000 | 4,01939e+06 | 4,03588e+06 | 4,05033e+06 |
| 05.04.2002 20:20:00 | ,000000 | 4,03163e+06 | 4,04788e+06 | 4,06266e+06 |
| 05.04.2002 20:30:00 | ,000000 | 4,04349e+06 | 4,05951e+06 | 4,07464e+06 |
| 05.04.2002 20:40:00 | ,000000 | 4,04967e+06 | 4,06535e+06 | 4,08088e+06 |
| 05.04.2002 20:50:00 | ,000000 | 4,06507e+06 | 4,08062e+06 | 4,09646e+06 |
| 05.04.2002 21:00:00 | ,000000 | 4,08e+06 | 4,09545e+06 | 4,11157e+06 |
| 05.04.2002 21:10:00 | ,000000 | 4,10113e+06 | 4,11660e+06 | 4,13295e+06 |
| 05.04.2002 21:20:00 | ,000000 | 4,11829e+06 | 4,13376e+06 | 4,15034e+06 |
| 05.04.2002 21:30:00 | ,000000 | 4,1433e+06 | 4,15893e+06 | 4,17566e+06 |
| 05.04.2002 21:40:00 | ,000000 | 4,17052e+06 | 4,18637e+06 | 4,20321e+06 |
| 05.04.2002 21:50:00 | ,000000 | 4,19958e+06 | 4,21566e+06 | 4,23259e+06 |
| 05.04.2002 22:00:00 | ,000000 | 4,22676e+06 | 4,243e+06 | 4,26004e+06 |
| 05.04.2002 22:10:00 | ,000000 | 4,25497e+06 | 4,2714e+06 | 4,28855e+06 |
| 05.04.2002 22:20:00 | ,000000 | 4,286e+06 | 4,30273e+06 | 4,31994e+06 |
| 05.04.2002 22:30:00 | ,000000 | 4,30962e+06 | 4,32645e+06 | 4,34383e+06 |
| 05.04.2002 22:40:00 | ,000000 | 4,32716e+06 | 4,34397e+06 | 4,36158e+06 |
| 05.04.2002 22:50:00 | ,000000 | 4,34762e+06 | 4,36446e+06 | 4,3823e+06 |
| 05.04.2002 23:00:00 | ,000000 | 4,37084e+06 | 4,3879e+06 | 4,40584e+06 |
| 05.04.2002 23:10:00 | ,000000 | 4,39832e+06 | 4,41569e+06 | 4,43368e+06 |
| 05.04.2002 23:20:00 | ,000000 | 4,44061e+06 | 4,45863e+06 | 4,47652e+06 |
| 05.04.2002 23:30:00 | ,000000 | 4,48714e+06 | 4,50598e+06 | 4,52366e+06 |
| 05.04.2002 23:40:00 | ,000000 | 4,53911e+06 | 4,55891e+06 | 4,57634e+06 |
| 05.04.2002 23:50:00 | ,000000 | 4,58711e+06 | 4,60776e+06 | 4,62501e+06 |
| 06.04.2002 00:00:00 | ,000000 | 4,62726e+06 | 4,64865e+06 | 4,66574e+06 |
| 06.04.2002 00:10:00 | ,000000 | 4,65622e+06 | 4,67808e+06 | 4,69508e+06 |
| 06.04.2002 00:20:00 | ,000000 | 4,69334e+06 | 4,71593e+06 | 4,73276e+06 |
| 06.04.2002 00:30:00 | ,000000 | 4,72697e+06 | 4,75021e+06 | 4,76686e+06 |
| 06.04.2002 00:40:00 | ,000000 | 4,76086e+06 | 4,78479e+06 | 4,80119e+06 |
| 06.04.2002 00:50:00 | ,000000 | 4,80614e+06 | 4,83102e+06 | 4,8471e+06 |
| 06.04.2002 01:00:00 | ,000000 | 4,84359e+06 | 4,86928e+06 | 4,88509e+06 |
| 06.04.2002 01:10:00 | ,000000 | 4,88081e+06 | 4,90718e+06 | 4,92285e+06 |
| 06.04.2002 01:20:00 | ,000000 | 4,91332e+06 | 4,94027e+06 | 4,95584e+06 |
| 06.04.2002 01:30:00 | ,000000 | 4,9491e+06 | 4,97671e+06 | 4,99213e+06 |
| 06.04.2002 01:40:00 | ,000000 | 4,99721e+06 | 5,02576e+06 | 5,04089e+06 |
| 06.04.2002 01:50:00 | ,000000 | 5,04783e+06 | 5,07732e+06 | 5,09212e+06 |
| 06.04.2002 02:00:00 | ,000000 | 5,08854e+06 | 5,11875e+06 | 5,13331e+06 |
| 06.04.2002 02:10:00 | ,000000 | 5,12779e+06 | 5,15863e+06 | 5,17299e+06 |
| 06.04.2002 02:20:00 | ,000000 | 5,16111e+06 | 5,19246e+06 | 5,20668e+06 |
| 06.04.2002 02:30:00 | ,000000 | 5,18108e+06 | 5,21265e+06 | 5,22688e+06 |
| 06.04.2002 02:40:00 | ,000000 | 5,21081e+06 | 5,24278e+06 | 5,25695e+06 |
| 06.04.2002 02:50:00 | ,000000 | 5,24176e+06 | 5,27419e+06 | 5,28826e+06 |
| 06.04.2002 03:00:00 | ,000000 | 5,28534e+06 | 5,31855e+06 | 5,33237e+06 |
| 06.04.2002 03:10:00 | ,000000 | 5,31978e+06 | 5,35365e+06 | 5,36728e+06 |
| 06.04.2002 03:20:00 | ,000000 | 5,35442e+06 | 5,389e+06 | 5,40246e+06 |
| 06.04.2002 03:30:00 | ,000000 | 5,38511e+06 | 5,42027e+06 | 5,43363e+06 |
| 06.04.2002 03:40:00 | ,000000 | 5,42794e+06 | 5,46389e+06 | 5,47709e+06 |
| 06.04.2002 03:50:00 | ,000000 | 5,46425e+06 | 5,50084e+06 | 5,51393e+06 |
| 06.04.2002 04:00:00 | ,000000 | 5,49521e+06 | 5,53231e+06 | 5,54532e+06 |
| 06.04.2002 04:10:00 | ,000000 | 5,52597e+06 | 5,56359e+06 | 5,57648e+06 |
| 06.04.2002 04:20:00 | ,000000 | 5,5571e+06 | 5,59528e+06 | 5,60801e+06 |
| 06.04.2002 04:30:00 | ,000000 | 5,59326e+06 | 5,63208e+06 | 5,64466e+06 |
| 06.04.2002 04:40:00 | ,000000 | 5,625e+06 | 5,6644e+06 | 5,67682e+06 |
| 06.04.2002 04:50:00 | ,000000 | 5,66792e+06 | 5,70819e+06 | 5,7203e+06 |
| 06.04.2002 05:00:00 | ,000000 | 5,71546e+06 | 5,75677e+06 | 5,76848e+06 |
| 06.04.2002 05:10:00 | ,000000 | 5,77561e+06 | 5,81825e+06 | 5,8294e+06 |
| 06.04.2002 05:20:00 | ,000000 | 5,83931e+06 | 5,88339e+06 | 5,8939e+06 |
| 06.04.2002 05:30:00 | ,000000 | 5,90267e+06 | 5,94816e+06 | 5,95806e+06 |
| 06.04.2002 05:40:00 | ,000000 | 5,97136e+06 | 6,01836e+06 | 6,02756e+06 |
| 06.04.2002 05:50:00 | ,000000 | 6,04136e+06 | 6,08993e+06 | 6,09835e+06 |
| 06.04.2002 06:00:00 | ,000000 | 6,11723e+06 | 6,16745e+06 | 6,17502e+06 |
| 06.04.2002 06:10:00 | ,000000 | 6,19103e+06 | 6,24294e+06 | 6,24963e+06 |
| 06.04.2002 06:20:00 | ,000000 | 6,2613e+06 | 6,31483e+06 | 6,32067e+06 |
| 06.04.2002 06:30:00 | ,000000 | 6,34035e+06 | 6,39569e+06 | 6,40055e+06 |
| 06.04.2002 06:40:00 | ,000000 | 6,42188e+06 | 6,47913e+06 | 6,48292e+06 |
| 06.04.2002 06:50:00 | ,000000 | 6,50312e+06 | 6,56228e+06 | 6,56505e+06 |
| 06.04.2002 07:00:00 | ,000000 | 6,58488e+06 | 6,64593e+06 | 6,64775e+06 |
| 06.04.2002 07:10:00 | ,000000 | 6,66699e+06 | 6,72994e+06 | 6,73086e+06 |
| 06.04.2002 07:20:00 | ,000000 | 6,74901e+06 | 6,81386e+06 | 6,81387e+06 |
| 06.04.2002 07:30:00 | ,000000 | 6,83116e+06 | 6,89786e+06 | 6,89694e+06 |
| 06.04.2002 07:40:00 | ,000000 | 6,91327e+06 | 6,98177e+06 | 6,97996e+06 |
| 06.04.2002 07:50:00 | ,000000 | 6,99541e+06 | 7,06569e+06 | 7,06297e+06 |
| 06.04.2002 08:00:00 | ,000000 | 7,07744e+06 | 7,14958e+06 | 7,14585e+06 |
| 06.04.2002 08:10:00 | ,000000 | 7,15957e+06 | 7,23358e+06 | 7,22887e+06 |
| 06.04.2002 08:20:00 | ,000000 | 7,24167e+06 | 7,31756e+06 | 7,31184e+06 |
| 06.04.2002 08:30:00 | ,000000 | 7,32374e+06 | 7,40149e+06 | 7,39476e+06 |
| 06.04.2002 08:40:00 | ,000000 | 7,4052e+06 | 7,48481e+06 | 7,47709e+06 |
| 06.04.2002 08:50:00 | ,000000 | 7,47321e+06 | 7,55443e+06 | 7,54592e+06 |
| 06.04.2002 09:00:00 | ,000000 | 7,55005e+06 | 7,63304e+06 | 7,62364e+06 |
| 06.04.2002 09:10:00 | ,000000 | 7,62296e+06 | 7,70755e+06 | 7,6974e+06 |
| 06.04.2002 09:20:00 | ,000000 | 7,69164e+06 | 7,7777e+06 | 7,76685e+06 |
| 06.04.2002 09:30:00 | ,000000 | 7,75296e+06 | 7,84033e+06 | 7,82891e+06 |
| 06.04.2002 09:40:00 | ,000000 | 7,82039e+06 | 7,90924e+06 | 7,89719e+06 |
| 06.04.2002 09:50:00 | ,000000 | 7,89527e+06 | 7,98574e+06 | 7,97294e+06 |
| 06.04.2002 10:00:00 | ,000000 | 7,9724e+06 | 8,06449e+06 | 8,05093e+06 |
| 06.04.2002 10:10:00 | ,000000 | 8,04895e+06 | 8,14272e+06 | 8,12834e+06 |
| 06.04.2002 10:20:00 | ,000000 | 8,12518e+06 | 8,22065e+06 | 8,20544e+06 |
| 06.04.2002 10:30:00 | ,000000 | 8,20008e+06 | 8,29722e+06 | 8,28119e+06 |
| 06.04.2002 10:40:00 | ,000000 | 8,26027e+06 | 8,35876e+06 | 8,34213e+06 |
| 06.04.2002 10:50:00 | ,000000 | 8,308e+06 | 8,40758e+06 | 8,3905e+06 |
| 06.04.2002 11:00:00 | ,000000 | 8,36799e+06 | 8,46887e+06 | 8,45127e+06 |
| 06.04.2002 11:10:00 | ,000000 | 8,41152e+06 | 8,51323e+06 | 8,49535e+06 |
| 06.04.2002 11:20:00 | ,000000 | 8,46124e+06 | 8,56393e+06 | 8,5457e+06 |
| 06.04.2002 11:30:00 | ,000000 | 8,51007e+06 | 8,61371e+06 | 8,59518e+06 |
| 06.04.2002 11:40:00 | ,000000 | 8,53111e+06 | 8,63512e+06 | 8,61651e+06 |
| 06.04.2002 11:50:00 | ,000000 | 8,58168e+06 | 8,68661e+06 | 8,66767e+06 |
| 06.04.2002 12:00:00 | ,000000 | 8,62857e+06 | 8,73429e+06 | 8,71516e+06 |
| 06.04.2002 12:10:00 | ,000000 | 8,66062e+06 | 8,76682e+06 | 8,74768e+06 |
| 06.04.2002 12:20:00 | ,000000 | 8,71317e+06 | 8,82031e+06 | 8,80094e+06 |
| 06.04.2002 12:30:00 | ,000000 | 8,74221e+06 | 8,84987e+06 | 8,83046e+06 |
| 06.04.2002 12:40:00 | ,000000 | 8,79949e+06 | 8,90828e+06 | 8,88853e+06 |
| 06.04.2002 12:50:00 | ,000000 | 8,84102e+06 | 8,95066e+06 | 8,9307e+06 |
| 06.04.2002 13:00:00 | ,000000 | 8,89405e+06 | 9,00474e+06 | 8,98444e+06 |
| 06.04.2002 13:10:00 | ,000000 | 8,94752e+06 | 9,05923e+06 | 9,03861e+06 |
| 06.04.2002 13:20:00 | ,000000 | 8,98762e+06 | 9,10008e+06 | 9,07927e+06 |
| 06.04.2002 13:30:00 | ,000000 | 9,01818e+06 | 9,13122e+06 | 9,11033e+06 |
| 06.04.2002 13:40:00 | ,000000 | 9,06111e+06 | 9,17498e+06 | 9,15388e+06 |
| 06.04.2002 13:50:00 | ,000000 | 9,10241e+06 | 9,21713e+06 | 9,19583e+06 |
| 06.04.2002 14:00:00 | ,000000 | 9,15749e+06 | 9,27323e+06 | 9,25166e+06 |
| 06.04.2002 14:10:00 | ,000000 | 9,1994e+06 | 9,31584e+06 | 9,29419e+06 |
| 06.04.2002 14:20:00 | ,000000 | 9,24809e+06 | 9,36539e+06 | 9,34357e+06 |
| 06.04.2002 14:30:00 | ,000000 | 9,28498e+06 | 9,40285e+06 | 9,381e+06 |
| 06.04.2002 14:40:00 | ,000000 | 9,31387e+06 | 9,43208e+06 | 9,4103e+06 |
| 06.04.2002 14:50:00 | ,000000 | 9,36749e+06 | 9,48651e+06 | 9,4646e+06 |
| 06.04.2002 15:00:00 | ,000000 | 9,40633e+06 | 9,52587e+06 | 9,504e+06 |
| 06.04.2002 15:10:00 | ,000000 | 9,45074e+06 | 9,57089e+06 | 9,54896e+06 |
| 06.04.2002 15:20:00 | ,000000 | 9,49469e+06 | 9,61535e+06 | 9,59342e+06 |
| 06.04.2002 15:30:00 | ,000000 | 9,53395e+06 | 9,65499e+06 | 9,63311e+06 |
| 06.04.2002 15:40:00 | ,000000 | 9,56406e+06 | 9,68534e+06 | 9,66357e+06 |
| 06.04.2002 15:50:00 | ,000000 | 9,60335e+06 | 9,72505e+06 | 9,70333e+06 |
| 06.04.2002 16:00:00 | ,000000 | 9,65488e+06 | 9,77728e+06 | 9,75549e+06 |
| 06.04.2002 16:10:00 | ,000000 | 9,69752e+06 | 9,82045e+06 | 9,79863e+06 |
| 06.04.2002 16:20:00 | ,000000 | 9,72566e+06 | 9,84884e+06 | 9,82714e+06 |
| 06.04.2002 16:30:00 | ,000000 | 9,75491e+06 | 9,87845e+06 | 9,85679e+06 |
| 06.04.2002 16:40:00 | ,000000 | 9,7968e+06 | 9,9209e+06 | 9,8992e+06 |
| 06.04.2002 16:50:00 | ,000000 | 9,83025e+06 | 9,95467e+06 | 9,93303e+06 |
| 06.04.2002 17:00:00 | ,000000 | 9,85555e+06 | 9,98015e+06 | 9,95865e+06 |
| 06.04.2002 17:10:00 | ,000000 | 9,88409e+06 | 1,0009e+07 | 9,98756e+06 |
| 06.04.2002 17:20:00 | ,000000 | 9,91708e+06 | 1,00423e+07 | 1,0021e+07 |
| 06.04.2002 17:30:00 | ,000000 | 9,94667e+06 | 1,00723e+07 | 1,0051e+07 |
| 06.04.2002 17:40:00 | ,000000 | 9,99242e+06 | 1,01187e+07 | 1,00973e+07 |
| 06.04.2002 17:50:00 | ,000000 | 1,00405e+07 | 1,01676e+07 | 1,0146e+07 |
| 06.04.2002 18:00:00 | ,000000 | 1,00843e+07 | 1,0212e+07 | 1,01903e+07 |
| 06.04.2002 18:10:00 | ,000000 | 1,01383e+07 | 1,0267e+07 | 1,02451e+07 |
| 06.04.2002 18:20:00 | ,000000 | 1,01713e+07 | 1,03005e+07 | 1,02786e+07 |
| 06.04.2002 18:30:00 | ,000000 | 1,02206e+07 | 1,03508e+07 | 1,03286e+07 |
| 06.04.2002 18:40:00 | ,000000 | 1,02902e+07 | 1,04217e+07 | 1,03989e+07 |
| 06.04.2002 18:50:00 | ,000000 | 1,03223e+07 | 1,04544e+07 | 1,04316e+07 |
| 06.04.2002 19:00:00 | ,000000 | 1,03584e+07 | 1,04912e+07 | 1,04681e+07 |
| 06.04.2002 19:10:00 | ,000000 | 1,04086e+07 | 1,05422e+07 | 1,05189e+07 |
| 06.04.2002 19:20:00 | ,000000 | 1,04654e+07 | 1,06001e+07 | 1,05764e+07 |
| 06.04.2002 19:30:00 | ,000000 | 1,05148e+07 | 1,06505e+07 | 1,06264e+07 |
| 06.04.2002 19:40:00 | ,000000 | 1,05828e+07 | 1,07199e+07 | 1,06952e+07 |
| 06.04.2002 19:50:00 | ,000000 | 1,06501e+07 | 1,07886e+07 | 1,07633e+07 |
| 06.04.2002 20:00:00 | ,000000 | 1,0707e+07 | 1,08466e+07 | 1,08209e+07 |
| 06.04.2002 20:10:00 | ,000000 | 1,07561e+07 | 1,08966e+07 | 1,08706e+07 |
| 06.04.2002 20:20:00 | ,000000 | 1,08217e+07 | 1,09634e+07 | 1,09368e+07 |
| 06.04.2002 20:30:00 | ,000000 | 1,08593e+07 | 1,10016e+07 | 1,09748e+07 |
| 06.04.2002 20:40:00 | ,000000 | 1,09041e+07 | 1,10472e+07 | 1,10202e+07 |
| 06.04.2002 20:50:00 | ,000000 | 1,0946e+07 | 1,109e+07 | 1,10626e+07 |
| 06.04.2002 21:00:00 | ,000000 | 1,1005e+07 | 1,11503e+07 | 1,11224e+07 |
| 06.04.2002 21:10:00 | ,000000 | 1,10831e+07 | 1,123e+07 | 1,12012e+07 |
| 06.04.2002 21:20:00 | ,000000 | 1,11651e+07 | 1,13139e+07 | 1,12841e+07 |
| 06.04.2002 21:30:00 | ,000000 | 1,12472e+07 | 1,13977e+07 | 1,13669e+07 |
| 06.04.2002 21:40:00 | ,000000 | 1,13293e+07 | 1,14817e+07 | 1,14499e+07 |
| 06.04.2002 21:50:00 | ,000000 | 1,14114e+07 | 1,15657e+07 | 1,15328e+07 |
| 06.04.2002 22:00:00 | ,000000 | 1,14936e+07 | 1,16497e+07 | 1,16157e+07 |
| 06.04.2002 22:10:00 | ,000000 | 1,15757e+07 | 1,17338e+07 | 1,16986e+07 |
| 06.04.2002 22:20:00 | ,000000 | 1,16578e+07 | 1,18178e+07 | 1,17815e+07 |
| 06.04.2002 22:30:00 | ,000000 | 1,17399e+07 | 1,19018e+07 | 1,18644e+07 |
| 06.04.2002 22:40:00 | ,000000 | 1,18219e+07 | 1,19858e+07 | 1,19473e+07 |
| 06.04.2002 22:50:00 | ,000000 | 1,1904e+07 | 1,20698e+07 | 1,20302e+07 |
| 06.04.2002 23:00:00 | ,000000 | 1,1986e+07 | 1,21538e+07 | 1,2113e+07 |
| 06.04.2002 23:10:00 | ,000000 | 1,20681e+07 | 1,22379e+07 | 1,21959e+07 |
| 06.04.2002 23:20:00 | ,000000 | 1,21501e+07 | 1,23219e+07 | 1,22787e+07 |
| 06.04.2002 23:30:00 | ,000000 | 1,22323e+07 | 1,2406e+07 | 1,23617e+07 |
| 06.04.2002 23:40:00 | ,000000 | 1,23142e+07 | 1,24899e+07 | 1,24445e+07 |
| 06.04.2002 23:50:00 | ,000000 | 1,23963e+07 | 1,25739e+07 | 1,25273e+07 |
| 07.04.2002 00:00:00 | ,000000 | 1,24785e+07 | 1,2658e+07 | 1,26104e+07 |
| 07.04.2002 00:10:00 | ,000000 | 1,25605e+07 | 1,27419e+07 | 1,26932e+07 |
| 07.04.2002 00:20:00 | ,000000 | 1,26426e+07 | 1,28259e+07 | 1,27761e+07 |
| 07.04.2002 00:30:00 | ,000000 | 1,27248e+07 | 1,291e+07 | 1,28591e+07 |
| 07.04.2002 00:40:00 | ,000000 | 1,28068e+07 | 1,29938e+07 | 1,29419e+07 |
| 07.04.2002 00:50:00 | ,000000 | 1,28875e+07 | 1,30763e+07 | 1,30234e+07 |
| 07.04.2002 01:00:00 | ,000000 | 1,29672e+07 | 1,31577e+07 | 1,31039e+07 |
| 07.04.2002 01:10:00 | ,000000 | 1,30495e+07 | 1,32417e+07 | 1,31869e+07 |
| 07.04.2002 01:20:00 | ,000000 | 1,31316e+07 | 1,33257e+07 | 1,32699e+07 |
| 07.04.2002 01:30:00 | ,000000 | 1,32129e+07 | 1,34086e+07 | 1,33519e+07 |
| 07.04.2002 01:40:00 | ,000000 | 1,32918e+07 | 1,34892e+07 | 1,34316e+07 |
| 07.04.2002 01:50:00 | ,000000 | 1,33581e+07 | 1,35568e+07 | 1,34985e+07 |
| 07.04.2002 02:00:00 | ,000000 | 1,34216e+07 | 1,36215e+07 | 1,35627e+07 |
| 07.04.2002 02:10:00 | ,000000 | 1,34699e+07 | 1,36707e+07 | 1,36116e+07 |
| 07.04.2002 02:20:00 | ,000000 | 1,35216e+07 | 1,37232e+07 | 1,36638e+07 |
| 07.04.2002 02:30:00 | ,000000 | 1,35623e+07 | 1,37645e+07 | 1,3705e+07 |
| 07.04.2002 02:40:00 | ,000000 | 1,35897e+07 | 1,3792e+07 | 1,37327e+07 |
| 07.04.2002 02:50:00 | ,000000 | 1,36077e+07 | 1,38101e+07 | 1,37509e+07 |
| 07.04.2002 03:00:00 | ,000000 | 1,36243e+07 | 1,38268e+07 | 1,37678e+07 |
| 07.04.2002 03:10:00 | ,000000 | 1,36432e+07 | 1,38459e+07 | 1,37869e+07 |
| 07.04.2002 03:20:00 | ,000000 | 1,36634e+07 | 1,38663e+07 | 1,38073e+07 |
| 07.04.2002 03:30:00 | ,000000 | 1,36932e+07 | 1,38966e+07 | 1,38374e+07 |
| 07.04.2002 03:40:00 | ,000000 | 1,37205e+07 | 1,39242e+07 | 1,38649e+07 |
| 07.04.2002 03:50:00 | ,000000 | 1,37445e+07 | 1,39486e+07 | 1,38892e+07 |
| 07.04.2002 04:00:00 | ,000000 | 1,37727e+07 | 1,39771e+07 | 1,39177e+07 |
| 07.04.2002 04:10:00 | ,000000 | 1,38172e+07 | 1,40224e+07 | 1,39626e+07 |
| 07.04.2002 04:20:00 | ,000000 | 1,38791e+07 | 1,40856e+07 | 1,40252e+07 |
| 07.04.2002 04:30:00 | ,000000 | 1,39508e+07 | 1,41589e+07 | 1,40976e+07 |
| 07.04.2002 04:40:00 | ,000000 | 1,40308e+07 | 1,42406e+07 | 1,41784e+07 |
| 07.04.2002 04:50:00 | ,000000 | 1,41127e+07 | 1,43243e+07 | 1,4261e+07 |
| 07.04.2002 05:00:00 | ,000000 | 1,41948e+07 | 1,44083e+07 | 1,4344e+07 |
| 07.04.2002 05:10:00 | ,000000 | 1,42769e+07 | 1,44923e+07 | 1,44269e+07 |
| 07.04.2002 05:20:00 | ,000000 | 1,4359e+07 | 1,45762e+07 | 1,45098e+07 |
| 07.04.2002 05:30:00 | ,000000 | 1,44412e+07 | 1,46602e+07 | 1,45927e+07 |
| 07.04.2002 05:40:00 | ,000000 | 1,45232e+07 | 1,47442e+07 | 1,46756e+07 |
| 07.04.2002 05:50:00 | ,000000 | 1,46052e+07 | 1,4828e+07 | 1,47584e+07 |
| 07.04.2002 06:00:00 | ,000000 | 1,46869e+07 | 1,49114e+07 | 1,48409e+07 |
| 07.04.2002 06:10:00 | ,000000 | 1,47327e+07 | 1,49578e+07 | 1,48872e+07 |
| 07.04.2002 06:20:00 | ,000000 | 1,47371e+07 | 1,49619e+07 | 1,48918e+07 |
| 07.04.2002 06:30:00 | ,000000 | 1,47382e+07 | 1,49628e+07 | 1,48929e+07 |
| 07.04.2002 06:40:00 | ,000000 | 1,47416e+07 | 1,49659e+07 | 1,48963e+07 |
| 07.04.2002 06:50:00 | ,000000 | 1,47527e+07 | 1,49769e+07 | 1,49075e+07 |
| 07.04.2002 07:00:00 | ,000000 | 1,47824e+07 | 1,50069e+07 | 1,49376e+07 |
| 07.04.2002 07:10:00 | ,000000 | 1,48464e+07 | 1,50721e+07 | 1,50023e+07 |
| 07.04.2002 07:20:00 | ,000000 | 1,49283e+07 | 1,51556e+07 | 1,5085e+07 |
| 07.04.2002 07:30:00 | ,000000 | 1,50103e+07 | 1,52393e+07 | 1,51679e+07 |
| 07.04.2002 07:40:00 | ,000000 | 1,50924e+07 | 1,53231e+07 | 1,52508e+07 |
| 07.04.2002 07:50:00 | ,000000 | 1,51745e+07 | 1,5407e+07 | 1,53338e+07 |
| 07.04.2002 08:00:00 | ,000000 | 1,52566e+07 | 1,54908e+07 | 1,54167e+07 |
| 07.04.2002 08:10:00 | ,000000 | 1,53388e+07 | 1,55748e+07 | 1,54998e+07 |
| 07.04.2002 08:20:00 | ,000000 | 1,5421e+07 | 1,56588e+07 | 1,55828e+07 |
| 07.04.2002 08:30:00 | ,000000 | 1,55032e+07 | 1,57428e+07 | 1,56659e+07 |
| 07.04.2002 08:40:00 | ,000000 | 1,55854e+07 | 1,58269e+07 | 1,57489e+07 |
| 07.04.2002 08:50:00 | ,000000 | 1,56676e+07 | 1,59109e+07 | 1,58319e+07 |
| 07.04.2002 09:00:00 | ,000000 | 1,57498e+07 | 1,5995e+07 | 1,59149e+07 |
| 07.04.2002 09:10:00 | ,000000 | 1,5832e+07 | 1,60791e+07 | 1,59979e+07 |
| 07.04.2002 09:20:00 | ,000000 | 1,59142e+07 | 1,61631e+07 | 1,60809e+07 |
| 07.04.2002 09:30:00 | ,000000 | 1,59962e+07 | 1,62471e+07 | 1,61637e+07 |
| 07.04.2002 09:40:00 | ,000000 | 1,60784e+07 | 1,63311e+07 | 1,62466e+07 |
| 07.04.2002 09:50:00 | ,000000 | 1,61605e+07 | 1,64152e+07 | 1,63295e+07 |
| 07.04.2002 10:00:00 | ,000000 | 1,62428e+07 | 1,64993e+07 | 1,64126e+07 |
| 07.04.2002 10:10:00 | ,000000 | 1,63249e+07 | 1,65833e+07 | 1,64956e+07 |
| 07.04.2002 10:20:00 | ,000000 | 1,64071e+07 | 1,66675e+07 | 1,65786e+07 |
| 07.04.2002 10:30:00 | ,000000 | 1,64884e+07 | 1,67507e+07 | 1,66607e+07 |
| 07.04.2002 10:40:00 | ,000000 | 1,65707e+07 | 1,68349e+07 | 1,67438e+07 |
| 07.04.2002 10:50:00 | ,000000 | 1,66528e+07 | 1,6919e+07 | 1,68268e+07 |
| 07.04.2002 11:00:00 | ,000000 | 1,67344e+07 | 1,70026e+07 | 1,69092e+07 |
| 07.04.2002 11:10:00 | ,000000 | 1,68166e+07 | 1,70867e+07 | 1,69922e+07 |
| 07.04.2002 11:20:00 | ,000000 | 1,68984e+07 | 1,71706e+07 | 1,70749e+07 |
| 07.04.2002 11:30:00 | ,000000 | 1,69806e+07 | 1,72547e+07 | 1,71579e+07 |
| 07.04.2002 11:40:00 | ,000000 | 1,7058e+07 | 1,7334e+07 | 1,72362e+07 |
| 07.04.2002 11:50:00 | ,000000 | 1,71383e+07 | 1,74163e+07 | 1,73173e+07 |
| 07.04.2002 12:00:00 | ,000000 | 1,72112e+07 | 1,74909e+07 | 1,73909e+07 |
| 07.04.2002 12:10:00 | ,000000 | 1,72909e+07 | 1,75724e+07 | 1,74714e+07 |
| 07.04.2002 12:20:00 | ,000000 | 1,73725e+07 | 1,76560e+07 | 1,75538e+07 |
| 07.04.2002 12:30:00 | ,000000 | 1,74548e+07 | 1,77403e+07 | 1,76368e+07 |
| 07.04.2002 12:40:00 | ,000000 | 1,75328e+07 | 1,78202e+07 | 1,77156e+07 |
| 07.04.2002 12:50:00 | ,000000 | 1,76148e+07 | 1,79041e+07 | 1,77984e+07 |
| 07.04.2002 13:00:00 | ,000000 | 1,76949e+07 | 1,7986e+07 | 1,78792e+07 |
| 07.04.2002 13:10:00 | ,000000 | 1,77655e+07 | 1,80583e+07 | 1,79505e+07 |
| 07.04.2002 13:20:00 | ,000000 | 1,78301e+07 | 1,81245e+07 | 1,80159e+07 |
| 07.04.2002 13:30:00 | ,000000 | 1,78915e+07 | 1,81872e+07 | 1,80779e+07 |
| 07.04.2002 13:40:00 | ,000000 | 1,79587e+07 | 1,82559e+07 | 1,81457e+07 |
| 07.04.2002 13:50:00 | ,000000 | 1,8013e+07 | 1,83114e+07 | 1,82005e+07 |
| 07.04.2002 14:00:00 | ,000000 | 1,80799e+07 | 1,83799e+07 | 1,82681e+07 |
| 07.04.2002 14:10:00 | ,000000 | 1,81333e+07 | 1,84345e+07 | 1,8322e+07 |
| 07.04.2002 14:20:00 | ,000000 | 1,81738e+07 | 1,84759e+07 | 1,8363e+07 |
| 07.04.2002 14:30:00 | ,000000 | 1,82123e+07 | 1,85152e+07 | 1,84019e+07 |
| 07.04.2002 14:40:00 | ,000000 | 1,82545e+07 | 1,85583e+07 | 1,84447e+07 |
| 07.04.2002 14:50:00 | ,000000 | 1,82953e+07 | 1,85998e+07 | 1,84859e+07 |
| 07.04.2002 15:00:00 | ,000000 | 1,83193e+07 | 1,86243e+07 | 1,85102e+07 |
| 07.04.2002 15:10:00 | ,000000 | 1,83361e+07 | 1,86414e+07 | 1,85273e+07 |
| 07.04.2002 15:20:00 | ,000000 | 1,84115e+07 | 1,87185e+07 | 1,86034e+07 |
| 07.04.2002 15:30:00 | ,000000 | 1,84735e+07 | 1,8782e+07 | 1,86661e+07 |
| 07.04.2002 15:40:00 | ,000000 | 1,85161e+07 | 1,88256e+07 | 1,87092e+07 |
| 07.04.2002 15:50:00 | ,000000 | 1,85577e+07 | 1,88682e+07 | 1,87512e+07 |
| 07.04.2002 16:00:00 | ,000000 | 1,85571e+07 | 1,88677e+07 | 1,87507e+07 |
| 07.04.2002 16:10:00 | ,000000 | 1,86232e+07 | 1,89352e+07 | 1,88175e+07 |
| 07.04.2002 16:20:00 | ,000000 | 1,87055e+07 | 1,90192e+07 | 1,89006e+07 |
| 07.04.2002 16:30:00 | ,000000 | 1,8766e+07 | 1,90809e+07 | 1,89618e+07 |
| 07.04.2002 16:40:00 | ,000000 | 1,87796e+07 | 1,90946e+07 | 1,89757e+07 |
| 07.04.2002 16:50:00 | ,000000 | 1,88302e+07 | 1,91462e+07 | 1,90269e+07 |
| 07.04.2002 17:00:00 | ,000000 | 1,88804e+07 | 1,91974e+07 | 1,90776e+07 |
| 07.04.2002 17:10:00 | ,000000 | 1,89049e+07 | 1,92221e+07 | 1,91024e+07 |
| 07.04.2002 17:20:00 | ,000000 | 1,89146e+07 | 1,92317e+07 | 1,91122e+07 |
| 07.04.2002 17:30:00 | ,000000 | 1,89194e+07 | 1,92362e+07 | 1,91171e+07 |
| 07.04.2002 17:40:00 | ,000000 | 1,89253e+07 | 1,92418e+07 | 1,91231e+07 |
| 07.04.2002 17:50:00 | ,000000 | 1,8927e+07 | 1,92433e+07 | 1,91249e+07 |
| 07.04.2002 18:00:00 | ,000000 | 1,89267e+07 | 1,9243e+07 | 1,91246e+07 |
| 07.04.2002 18:10:00 | ,000000 | 1,89264e+07 | 1,92428e+07 | 1,91243e+07 |
| 07.04.2002 18:20:00 | ,000000 | 1,89262e+07 | 1,92427e+07 | 1,91241e+07 |
| 07.04.2002 18:30:00 | ,000000 | 1,8926e+07 | 1,92426e+07 | 1,9124e+07 |
| 07.04.2002 18:40:00 | ,000000 | 1,89315e+07 | 1,92479e+07 | 1,91296e+07 |
| 07.04.2002 18:50:00 | ,000000 | 1,89363e+07 | 1,92524e+07 | 1,91343e+07 |
| 07.04.2002 19:00:00 | ,000000 | 1,89373e+07 | 1,92529e+07 | 1,91352e+07 |
| 07.04.2002 19:10:00 | ,000000 | 1,8937e+07 | 1,92526e+07 | 1,9135e+07 |
| 07.04.2002 19:20:00 | ,000000 | 1,89417e+07 | 1,92568e+07 | 1,91395e+07 |
| 07.04.2002 19:30:00 | ,000000 | 1,89509e+07 | 1,92657e+07 | 1,91487e+07 |
| 07.04.2002 19:40:00 | ,000000 | 1,89564e+07 | 1,92709e+07 | 1,91541e+07 |
| 07.04.2002 19:50:00 | ,000000 | 1,89683e+07 | 1,92826e+07 | 1,9166e+07 |
| 07.04.2002 20:00:00 | ,000000 | 1,89731e+07 | 1,92873e+07 | 1,91709e+07 |
| 07.04.2002 20:10:00 | ,000000 | 1,89781e+07 | 1,9292e+07 | 1,91758e+07 |
| 07.04.2002 20:20:00 | ,000000 | 1,89842e+07 | 1,92978e+07 | 1,9182e+07 |
| 07.04.2002 20:30:00 | ,000000 | 1,89861e+07 | 1,92994e+07 | 1,9184e+07 |
| 07.04.2002 20:40:00 | ,000000 | 1,89925e+07 | 1,93056e+07 | 1,91905e+07 |
| 07.04.2002 20:50:00 | ,000000 | 1,89966e+07 | 1,93095e+07 | 1,91947e+07 |
| 07.04.2002 21:00:00 | ,000000 | 1,89979e+07 | 1,93103e+07 | 1,91959e+07 |
| 07.04.2002 21:10:00 | ,000000 | 1,8999e+07 | 1,93109e+07 | 1,9197e+07 |
| 07.04.2002 21:20:00 | ,000000 | 1,90004e+07 | 1,93118e+07 | 1,91984e+07 |
| 07.04.2002 21:30:00 | ,000000 | 1,9002e+07 | 1,93128e+07 | 1,91999e+07 |
| 07.04.2002 21:40:00 | ,000000 | 1,90018e+07 | 1,93125e+07 | 1,91998e+07 |
| 07.04.2002 21:50:00 | ,000000 | 1,90031e+07 | 1,93134e+07 | 1,9201e+07 |
| 07.04.2002 22:00:00 | ,000000 | 1,90151e+07 | 1,93254e+07 | 1,92132e+07 |
| 07.04.2002 22:10:00 | ,000000 | 1,90421e+07 | 1,93526e+07 | 1,92404e+07 |
| 07.04.2002 22:20:00 | ,000000 | 1,90666e+07 | 1,93773e+07 | 1,92651e+07 |
| 07.04.2002 22:30:00 | ,000000 | 1,90943e+07 | 1,94053e+07 | 1,92931e+07 |
| 07.04.2002 22:40:00 | ,000000 | 1,91294e+07 | 1,94408e+07 | 1,93286e+07 |
| 07.04.2002 22:50:00 | ,000000 | 1,91599e+07 | 1,94716e+07 | 1,93592e+07 |
| 07.04.2002 23:00:00 | ,000000 | 1,91862e+07 | 1,94981e+07 | 1,93857e+07 |
| 07.04.2002 23:10:00 | ,000000 | 1,92187e+07 | 1,9531e+07 | 1,94185e+07 |
| 07.04.2002 23:20:00 | ,000000 | 1,92652e+07 | 1,95782e+07 | 1,94655e+07 |
| 07.04.2002 23:30:00 | ,000000 | 1,93131e+07 | 1,96268e+07 | 1,95139e+07 |
| 07.04.2002 23:40:00 | ,000000 | 1,93549e+07 | 1,96691e+07 | 1,95561e+07 |
| 07.04.2002 23:50:00 | ,000000 | 1,93863e+07 | 1,97008e+07 | 1,95878e+07 |
| 08.04.2002 00:00:00 | ,000000 | 1,94195e+07 | 1,97344e+07 | 1,96213e+07 |
| 08.04.2002 00:10:00 | ,000000 | 1,94454e+07 | 1,97606e+07 | 1,96474e+07 |
| 08.04.2002 00:20:00 | ,000000 | 1,94451e+07 | 1,97604e+07 | 1,96471e+07 |
| 08.04.2002 00:30:00 | ,000000 | 1,94882e+07 | 1,98042e+07 | 1,96907e+07 |
| 08.04.2002 00:40:00 | ,000000 | 1,95405e+07 | 1,98572e+07 | 1,97433e+07 |
| 08.04.2002 00:50:00 | ,000000 | 1,95925e+07 | 1,991e+07 | 1,97958e+07 |
| 08.04.2002 01:00:00 | ,000000 | 1,9646e+07 | 1,99643e+07 | 1,98497e+07 |
| 08.04.2002 01:10:00 | ,000000 | 1,96968e+07 | 2,00159e+07 | 1,9901e+07 |
| 08.04.2002 01:20:00 | ,000000 | 1,97561e+07 | 2,00763e+07 | 1,99608e+07 |
| 08.04.2002 01:30:00 | ,000000 | 1,98196e+07 | 2,01409e+07 | 2,00249e+07 |
| 08.04.2002 01:40:00 | ,000000 | 1,98858e+07 | 2,02083e+07 | 2,00917e+07 |
| 08.04.2002 01:50:00 | ,000000 | 1,99599e+07 | 2,02838e+07 | 2,01664e+07 |
| 08.04.2002 02:00:00 | ,000000 | 2,00263e+07 | 2,03514e+07 | 2,02335e+07 |
| 08.04.2002 02:10:00 | ,000000 | 2,00899e+07 | 2,04162e+07 | 2,02978e+07 |
| 08.04.2002 02:20:00 | ,000000 | 2,01587e+07 | 2,04862e+07 | 2,03672e+07 |
| 08.04.2002 02:30:00 | ,000000 | 2,02287e+07 | 2,05575e+07 | 2,04378e+07 |
| 08.04.2002 02:40:00 | ,000000 | 2,02945e+07 | 2,06245e+07 | 2,05043e+07 |
| 08.04.2002 02:50:00 | ,000000 | 2,03712e+07 | 2,07026e+07 | 2,05817e+07 |
| 08.04.2002 03:00:00 | ,000000 | 2,04525e+07 | 2,07855e+07 | 2,06638e+07 |
| 08.04.2002 03:10:00 | ,000000 | 2,0522e+07 | 2,08564e+07 | 2,07339e+07 |
| 08.04.2002 03:20:00 | ,000000 | 2,05746e+07 | 2,09101e+07 | 2,07872e+07 |
| 08.04.2002 03:30:00 | ,000000 | 2,0601e+07 | 2,0937e+07 | 2,08137e+07 |
| 08.04.2002 03:40:00 | ,000000 | 2,06338e+07 | 2,09705e+07 | 2,08469e+07 |
| 08.04.2002 03:50:00 | ,000000 | 2,0659e+07 | 2,09962e+07 | 2,08723e+07 |
| 08.04.2002 04:00:00 | ,000000 | 2,06774e+07 | 2,10148e+07 | 2,08909e+07 |
| 08.04.2002 04:10:00 | ,000000 | 2,0696e+07 | 2,10337e+07 | 2,09096e+07 |
| 08.04.2002 04:20:00 | ,000000 | 2,07292e+07 | 2,10676e+07 | 2,09432e+07 |
| 08.04.2002 04:30:00 | ,000000 | 2,07563e+07 | 2,10952e+07 | 2,09705e+07 |
| 08.04.2002 04:40:00 | ,000000 | 2,07853e+07 | 2,11246e+07 | 2,09998e+07 |
| 08.04.2002 04:50:00 | ,000000 | 2,08228e+07 | 2,11627e+07 | 2,10377e+07 |
| 08.04.2002 05:00:00 | ,000000 | 2,08427e+07 | 2,11827e+07 | 2,10577e+07 |
| 08.04.2002 05:10:00 | ,000000 | 2,08619e+07 | 2,1202e+07 | 2,1077e+07 |
| 08.04.2002 05:20:00 | ,000000 | 2,08841e+07 | 2,12243e+07 | 2,10994e+07 |
| 08.04.2002 05:30:00 | ,000000 | 2,09041e+07 | 2,12444e+07 | 2,11195e+07 |
| 08.04.2002 05:40:00 | ,000000 | 2,09298e+07 | 2,12701e+07 | 2,11454e+07 |
| 08.04.2002 05:50:00 | ,000000 | 2,09476e+07 | 2,12878e+07 | 2,11632e+07 |
| 08.04.2002 06:00:00 | ,000000 | 2,09618e+07 | 2,13018e+07 | 2,11775e+07 |
| 08.04.2002 06:10:00 | ,000000 | 2,0977e+07 | 2,13167e+07 | 2,11926e+07 |
| 08.04.2002 06:20:00 | ,000000 | 2,09907e+07 | 2,13302e+07 | 2,12063e+07 |
| 08.04.2002 06:30:00 | ,000000 | 2,10024e+07 | 2,13416e+07 | 2,1218e+07 |
| 08.04.2002 06:40:00 | ,000000 | 2,10173e+07 | 2,13564e+07 | 2,12329e+07 |
| 08.04.2002 06:50:00 | ,000000 | 2,10295e+07 | 2,13684e+07 | 2,12451e+07 |
| 08.04.2002 07:00:00 | ,000000 | 2,10414e+07 | 2,138e+07 | 2,12571e+07 |
| 08.04.2002 07:10:00 | ,000000 | 2,10534e+07 | 2,13918e+07 | 2,1269e+07 |
| 08.04.2002 07:20:00 | ,000000 | 2,10634e+07 | 2,14015e+07 | 2,12791e+07 |
| 08.04.2002 07:30:00 | ,000000 | 2,10732e+07 | 2,14109e+07 | 2,12888e+07 |
| 08.04.2002 07:40:00 | ,000000 | 2,10815e+07 | 2,14187e+07 | 2,12971e+07 |
| 08.04.2002 07:50:00 | ,000000 | 2,10888e+07 | 2,14254e+07 | 2,13043e+07 |
| 08.04.2002 08:00:00 | ,000000 | 2,10944e+07 | 2,14304e+07 | 2,13098e+07 |
| 08.04.2002 08:10:00 | ,000000 | 2,11009e+07 | 2,14363e+07 | 2,13162e+07 |
| 08.04.2002 08:20:00 | ,000000 | 2,11096e+07 | 2,14446e+07 | 2,1325e+07 |
| 08.04.2002 08:30:00 | ,000000 | 2,11227e+07 | 2,14572e+07 | 2,13381e+07 |
| 08.04.2002 08:40:00 | ,000000 | 2,11319e+07 | 2,14659e+07 | 2,13472e+07 |
| 08.04.2002 08:50:00 | ,000000 | 2,11395e+07 | 2,14731e+07 | 2,13548e+07 |
| 08.04.2002 09:00:00 | ,000000 | 2,11488e+07 | 2,14819e+07 | 2,13641e+07 |
| 08.04.2002 09:10:00 | ,000000 | 2,11571e+07 | 2,14897e+07 | 2,13723e+07 |
| 08.04.2002 09:20:00 | ,000000 | 2,11683e+07 | 2,15004e+07 | 2,13834e+07 |
| 08.04.2002 09:30:00 | ,000000 | 2,11749e+07 | 2,15064e+07 | 2,13898e+07 |
| 08.04.2002 09:40:00 | ,000000 | 2,118e+07 | 2,15108e+07 | 2,13947e+07 |
| 08.04.2002 09:50:00 | ,000000 | 2,11847e+07 | 2,15149e+07 | 2,13993e+07 |
| 08.04.2002 10:00:00 | ,000000 | 2,11859e+07 | 2,15158e+07 | 2,14004e+07 |
| 08.04.2002 10:10:00 | ,000000 | 2,11884e+07 | 2,15176e+07 | 2,14027e+07 |
| 08.04.2002 10:20:00 | ,000000 | 2,11899e+07 | 2,15189e+07 | 2,14042e+07 |
| 08.04.2002 10:30:00 | ,000000 | 2,11924e+07 | 2,1521e+07 | 2,14065e+07 |
| 08.04.2002 10:40:00 | ,000000 | 2,1198e+07 | 2,15261e+07 | 2,1412e+07 |
| 08.04.2002 10:50:00 | ,000000 | 2,12082e+07 | 2,15359e+07 | 2,14221e+07 |
| 08.04.2002 11:00:00 | ,000000 | 2,12195e+07 | 2,15465e+07 | 2,14333e+07 |
| 08.04.2002 11:10:00 | ,000000 | 2,12289e+07 | 2,15552e+07 | 2,14426e+07 |
| 08.04.2002 11:20:00 | ,000000 | 2,12406e+07 | 2,15664e+07 | 2,14542e+07 |
| 08.04.2002 11:30:00 | ,000000 | 2,12451e+07 | 2,15703e+07 | 2,14586e+07 |
| 08.04.2002 11:40:00 | ,000000 | 2,12516e+07 | 2,15762e+07 | 2,1465e+07 |
| 08.04.2002 11:50:00 | ,000000 | 2,12625e+07 | 2,15865e+07 | 2,14758e+07 |
| 08.04.2002 12:00:00 | ,000000 | 2,12819e+07 | 2,16057e+07 | 2,14953e+07 |
| 08.04.2002 12:10:00 | ,000000 | 2,1299e+07 | 2,16225e+07 | 2,15124e+07 |
| 08.04.2002 12:20:00 | ,000000 | 2,13173e+07 | 2,16405e+07 | 2,15308e+07 |
| 08.04.2002 12:30:00 | ,000000 | 2,13322e+07 | 2,16552e+07 | 2,15458e+07 |
| 08.04.2002 12:40:00 | ,000000 | 2,13663e+07 | 2,16895e+07 | 2,15802e+07 |
| 08.04.2002 12:50:00 | ,000000 | 2,14028e+07 | 2,17262e+07 | 2,16169e+07 |
| 08.04.2002 13:00:00 | ,000000 | 2,14307e+07 | 2,17543e+07 | 2,1645e+07 |
| 08.04.2002 13:10:00 | ,000000 | 2,14602e+07 | 2,17838e+07 | 2,16747e+07 |
| 08.04.2002 13:20:00 | ,000000 | 2,14859e+07 | 2,18096e+07 | 2,17006e+07 |
| 08.04.2002 13:30:00 | ,000000 | 2,15169e+07 | 2,18408e+07 | 2,17318e+07 |
| 08.04.2002 13:40:00 | ,000000 | 2,1546e+07 | 2,187e+07 | 2,17611e+07 |
| 08.04.2002 13:50:00 | ,000000 | 2,15792e+07 | 2,19033e+07 | 2,17944e+07 |
| 08.04.2002 14:00:00 | ,000000 | 2,16099e+07 | 2,19342e+07 | 2,18253e+07 |
| 08.04.2002 14:10:00 | ,000000 | 2,16399e+07 | 2,19645e+07 | 2,18556e+07 |
| 08.04.2002 14:20:00 | ,000000 | 2,1677e+07 | 2,20019e+07 | 2,18929e+07 |
| 08.04.2002 14:30:00 | ,000000 | 2,17074e+07 | 2,20326e+07 | 2,19235e+07 |
| 08.04.2002 14:40:00 | ,000000 | 2,17409e+07 | 2,20664e+07 | 2,19573e+07 |
| 08.04.2002 14:50:00 | ,000000 | 2,177e+07 | 2,20956e+07 | 2,19865e+07 |
| 08.04.2002 15:00:00 | ,000000 | 2,1802e+07 | 2,21278e+07 | 2,20187e+07 |
| 08.04.2002 15:10:00 | ,000000 | 2,18342e+07 | 2,21604e+07 | 2,20511e+07 |
| 08.04.2002 15:20:00 | ,000000 | 2,18624e+07 | 2,21889e+07 | 2,20796e+07 |
| 08.04.2002 15:30:00 | ,000000 | 2,18939e+07 | 2,22208e+07 | 2,21113e+07 |
| 08.04.2002 15:40:00 | ,000000 | 2,19255e+07 | 2,22526e+07 | 2,21431e+07 |
| 08.04.2002 15:50:00 | ,000000 | 2,19641e+07 | 2,22917e+07 | 2,21821e+07 |
| 08.04.2002 16:00:00 | ,000000 | 2,19815e+07 | 2,2309e+07 | 2,21994e+07 |
| 08.04.2002 16:10:00 | ,000000 | 2,20031e+07 | 2,23306e+07 | 2,22211e+07 |
| 08.04.2002 16:20:00 | ,000000 | 2,20327e+07 | 2,23605e+07 | 2,22509e+07 |
| 08.04.2002 16:30:00 | ,000000 | 2,2063e+07 | 2,2391e+07 | 2,22815e+07 |
| 08.04.2002 16:40:00 | ,000000 | 2,20904e+07 | 2,24185e+07 | 2,2309e+07 |
| 08.04.2002 16:50:00 | ,000000 | 2,21096e+07 | 2,24376e+07 | 2,23283e+07 |
| 08.04.2002 17:00:00 | ,000000 | 2,2138e+07 | 2,24661e+07 | 2,23569e+07 |
| 08.04.2002 17:10:00 | ,000000 | 2,2167e+07 | 2,24952e+07 | 2,23861e+07 |
| 08.04.2002 17:20:00 | ,000000 | 2,21876e+07 | 2,25158e+07 | 2,24069e+07 |
| 08.04.2002 17:30:00 | ,000000 | 2,22103e+07 | 2,25385e+07 | 2,24298e+07 |
| 08.04.2002 17:40:00 | ,000000 | 2,22336e+07 | 2,25619e+07 | 2,24532e+07 |
| 08.04.2002 17:50:00 | ,000000 | 2,22608e+07 | 2,25892e+07 | 2,24805e+07 |
| 08.04.2002 18:00:00 | ,000000 | 2,23045e+07 | 2,26335e+07 | 2,25246e+07 |
| 08.04.2002 18:10:00 | ,000000 | 2,23335e+07 | 2,26628e+07 | 2,25538e+07 |
| 08.04.2002 18:20:00 | ,000000 | 2,23641e+07 | 2,26937e+07 | 2,25847e+07 |
| 08.04.2002 18:30:00 | ,000000 | 2,23934e+07 | 2,27234e+07 | 2,26143e+07 |
| 08.04.2002 18:40:00 | ,000000 | 2,24111e+07 | 2,2741e+07 | 2,26321e+07 |
| 08.04.2002 18:50:00 | ,000000 | 2,24234e+07 | 2,27531e+07 | 2,26444e+07 |
| 08.04.2002 19:00:00 | ,000000 | 2,24305e+07 | 2,27597e+07 | 2,26514e+07 |
| 08.04.2002 19:10:00 | ,000000 | 2,2439e+07 | 2,2768e+07 | 2,266e+07 |
| 08.04.2002 19:20:00 | ,000000 | 2,24435e+07 | 2,27721e+07 | 2,26645e+07 |
| 08.04.2002 19:30:00 | ,000000 | 2,24475e+07 | 2,27756e+07 | 2,26684e+07 |
| 08.04.2002 19:40:00 | ,000000 | 2,2453e+07 | 2,27806e+07 | 2,26739e+07 |
| 08.04.2002 19:50:00 | ,000000 | 2,24577e+07 | 2,27849e+07 | 2,26785e+07 |
| 08.04.2002 20:00:00 | ,000000 | 2,24623e+07 | 2,2789e+07 | 2,26831e+07 |
| 08.04.2002 20:10:00 | ,000000 | 2,24648e+07 | 2,2791e+07 | 2,26855e+07 |
| 08.04.2002 20:20:00 | ,000000 | 2,24668e+07 | 2,27925e+07 | 2,26875e+07 |
| 08.04.2002 20:30:00 | ,000000 | 2,24704e+07 | 2,27956e+07 | 2,26911e+07 |
| 08.04.2002 20:40:00 | ,000000 | 2,24714e+07 | 2,27961e+07 | 2,26921e+07 |
| 08.04.2002 20:50:00 | ,000000 | 2,24735e+07 | 2,27978e+07 | 2,26942e+07 |
| 08.04.2002 21:00:00 | ,000000 | 2,24799e+07 | 2,28038e+07 | 2,27006e+07 |
| 08.04.2002 21:10:00 | ,000000 | 2,24885e+07 | 2,28123e+07 | 2,27094e+07 |
| 08.04.2002 21:20:00 | ,000000 | 2,24945e+07 | 2,28179e+07 | 2,27154e+07 |
| 08.04.2002 21:30:00 | ,000000 | 2,24948e+07 | 2,28178e+07 | 2,27157e+07 |
| 08.04.2002 21:40:00 | ,000000 | 2,24952e+07 | 2,28178e+07 | 2,27161e+07 |
| 08.04.2002 21:50:00 | ,000000 | 2,24953e+07 | 2,28175e+07 | 2,27162e+07 |
| 08.04.2002 22:00:00 | ,000000 | 2,24979e+07 | 2,28198e+07 | 2,27188e+07 |
| 08.04.2002 22:10:00 | ,000000 | 2,25022e+07 | 2,28239e+07 | 2,27232e+07 |
| 08.04.2002 22:20:00 | ,000000 | 2,25101e+07 | 2,28316e+07 | 2,27312e+07 |
| 08.04.2002 22:30:00 | ,000000 | 2,25177e+07 | 2,28389e+07 | 2,27388e+07 |
| 08.04.2002 22:40:00 | ,000000 | 2,25269e+07 | 2,2848e+07 | 2,27482e+07 |
| 08.04.2002 22:50:00 | ,000000 | 2,2536e+07 | 2,2857e+07 | 2,27574e+07 |
| 08.04.2002 23:00:00 | ,000000 | 2,25447e+07 | 2,28655e+07 | 2,27662e+07 |
| 08.04.2002 23:10:00 | ,000000 | 2,25533e+07 | 2,28738e+07 | 2,27748e+07 |
| 08.04.2002 23:20:00 | ,000000 | 2,25662e+07 | 2,28868e+07 | 2,27878e+07 |
| 08.04.2002 23:30:00 | ,000000 | 2,2583e+07 | 2,29036e+07 | 2,28048e+07 |
| 08.04.2002 23:40:00 | ,000000 | 2,26e+07 | 2,29207e+07 | 2,28219e+07 |
| 08.04.2002 23:50:00 | ,000000 | 2,26126e+07 | 2,29332e+07 | 2,28346e+07 |
| 09.04.2002 00:00:00 | ,000000 | 2,26288e+07 | 2,29496e+07 | 2,28509e+07 |
| 09.04.2002 00:10:00 | ,000000 | 2,26573e+07 | 2,29784e+07 | 2,28796e+07 |
| 09.04.2002 00:20:00 | ,000000 | 2,26778e+07 | 2,2999e+07 | 2,29002e+07 |
| 09.04.2002 00:30:00 | ,000000 | 2,26913e+07 | 2,30126e+07 | 2,29138e+07 |
| 09.04.2002 00:40:00 | ,000000 | 2,2703e+07 | 2,30242e+07 | 2,29256e+07 |
| 09.04.2002 00:50:00 | ,000000 | 2,27163e+07 | 2,30375e+07 | 2,29389e+07 |
| 09.04.2002 01:00:00 | ,000000 | 2,27259e+07 | 2,3047e+07 | 2,29486e+07 |
| 09.04.2002 01:10:00 | ,000000 | 2,27351e+07 | 2,30562e+07 | 2,29579e+07 |
| 09.04.2002 01:20:00 | ,000000 | 2,2746e+07 | 2,3067e+07 | 2,29688e+07 |
| 09.04.2002 01:30:00 | ,000000 | 2,27601e+07 | 2,30813e+07 | 2,29831e+07 |
| 09.04.2002 01:40:00 | ,000000 | 2,27778e+07 | 2,30991e+07 | 2,3001e+07 |
| 09.04.2002 01:50:00 | ,000000 | 2,27938e+07 | 2,31152e+07 | 2,30171e+07 |
| 09.04.2002 02:00:00 | ,000000 | 2,28087e+07 | 2,31302e+07 | 2,30322e+07 |
| 09.04.2002 02:10:00 | ,000000 | 2,28234e+07 | 2,3145e+07 | 2,30469e+07 |
| 09.04.2002 02:20:00 | ,000000 | 2,28398e+07 | 2,31614e+07 | 2,30634e+07 |
| 09.04.2002 02:30:00 | ,000000 | 2,28514e+07 | 2,31729e+07 | 2,3075e+07 |
| 09.04.2002 02:40:00 | ,000000 | 2,28621e+07 | 2,31835e+07 | 2,30858e+07 |
| 09.04.2002 02:50:00 | ,000000 | 2,28757e+07 | 2,31971e+07 | 2,30996e+07 |
| 09.04.2002 03:00:00 | ,000000 | 2,28984e+07 | 2,32201e+07 | 2,31226e+07 |
| 09.04.2002 03:10:00 | ,000000 | 2,29358e+07 | 2,3258e+07 | 2,31605e+07 |
| 09.04.2002 03:20:00 | ,000000 | 2,29631e+07 | 2,32858e+07 | 2,31882e+07 |
| 09.04.2002 03:30:00 | ,000000 | 2,2989e+07 | 2,3312e+07 | 2,32144e+07 |
| 09.04.2002 03:40:00 | ,000000 | 2,30216e+07 | 2,33452e+07 | 2,32475e+07 |
| 09.04.2002 03:50:00 | ,000000 | 2,30662e+07 | 2,33906e+07 | 2,32927e+07 |
| 09.04.2002 04:00:00 | ,000000 | 2,311e+07 | 2,34352e+07 | 2,33372e+07 |
| 09.04.2002 04:10:00 | ,000000 | 2,31454e+07 | 2,34711e+07 | 2,3373e+07 |
| 09.04.2002 04:20:00 | ,000000 | 2,3171e+07 | 2,3497e+07 | 2,3399e+07 |
| 09.04.2002 04:30:00 | ,000000 | 2,31937e+07 | 2,352e+07 | 2,34221e+07 |
| 09.04.2002 04:40:00 | ,000000 | 2,32133e+07 | 2,35397e+07 | 2,3442e+07 |
| 09.04.2002 04:50:00 | ,000000 | 2,32274e+07 | 2,35538e+07 | 2,34563e+07 |
| 09.04.2002 05:00:00 | ,000000 | 2,32408e+07 | 2,35672e+07 | 2,34699e+07 |
| 09.04.2002 05:10:00 | ,000000 | 2,32527e+07 | 2,35791e+07 | 2,34821e+07 |
| 09.04.2002 05:20:00 | ,000000 | 2,32673e+07 | 2,35937e+07 | 2,34968e+07 |
| 09.04.2002 05:30:00 | ,000000 | 2,32893e+07 | 2,3616e+07 | 2,35192e+07 |
| 09.04.2002 05:40:00 | ,000000 | 2,33127e+07 | 2,36397e+07 | 2,35429e+07 |
| 09.04.2002 05:50:00 | ,000000 | 2,33369e+07 | 2,36642e+07 | 2,35674e+07 |
| 09.04.2002 06:00:00 | ,000000 | 2,33657e+07 | 2,36933e+07 | 2,35965e+07 |
| 09.04.2002 06:10:00 | ,000000 | 2,33998e+07 | 2,37277e+07 | 2,3631e+07 |
| 09.04.2002 06:20:00 | ,000000 | 2,34363e+07 | 2,37647e+07 | 2,3668e+07 |
| 09.04.2002 06:30:00 | ,000000 | 2,34712e+07 | 2,38001e+07 | 2,37034e+07 |
| 09.04.2002 06:40:00 | ,000000 | 2,35048e+07 | 2,3834e+07 | 2,37373e+07 |
| 09.04.2002 06:50:00 | ,000000 | 2,35396e+07 | 2,38692e+07 | 2,37725e+07 |
| 09.04.2002 07:00:00 | ,000000 | 2,35737e+07 | 2,39037e+07 | 2,3807e+07 |
| 09.04.2002 07:10:00 | ,000000 | 2,3605e+07 | 2,39351e+07 | 2,38386e+07 |
| 09.04.2002 07:20:00 | ,000000 | 2,36273e+07 | 2,39574e+07 | 2,38612e+07 |
| 09.04.2002 07:30:00 | ,000000 | 2,36478e+07 | 2,39779e+07 | 2,38819e+07 |
| 09.04.2002 07:40:00 | ,000000 | 2,36636e+07 | 2,39937e+07 | 2,3898e+07 |
| 09.04.2002 07:50:00 | ,000000 | 2,36768e+07 | 2,40067e+07 | 2,39113e+07 |
| 09.04.2002 08:00:00 | ,000000 | 2,36942e+07 | 2,4024e+07 | 2,39289e+07 |
| 09.04.2002 08:10:00 | ,000000 | 2,3708e+07 | 2,40376e+07 | 2,39428e+07 |
| 09.04.2002 08:20:00 | ,000000 | 2,37201e+07 | 2,40495e+07 | 2,3955e+07 |
| 09.04.2002 08:30:00 | ,000000 | 2,37353e+07 | 2,40646e+07 | 2,39703e+07 |
| 09.04.2002 08:40:00 | ,000000 | 2,37491e+07 | 2,40781e+07 | 2,39842e+07 |
| 09.04.2002 08:50:00 | ,000000 | 2,37669e+07 | 2,40958e+07 | 2,40021e+07 |
| 09.04.2002 09:00:00 | ,000000 | 2,37871e+07 | 2,4116e+07 | 2,40225e+07 |
| 09.04.2002 09:10:00 | ,000000 | 2,38007e+07 | 2,41294e+07 | 2,40363e+07 |
| 09.04.2002 09:20:00 | ,000000 | 2,38136e+07 | 2,4142e+07 | 2,40493e+07 |
| 09.04.2002 09:30:00 | ,000000 | 2,3828e+07 | 2,41562e+07 | 2,40638e+07 |
| 09.04.2002 09:40:00 | ,000000 | 2,3841e+07 | 2,41689e+07 | 2,40769e+07 |
| 09.04.2002 09:50:00 | ,000000 | 2,38498e+07 | 2,41775e+07 | 2,40859e+07 |
| 09.04.2002 10:00:00 | ,000000 | 2,38658e+07 | 2,41934e+07 | 2,4102e+07 |
| 09.04.2002 10:10:00 | ,000000 | 2,38738e+07 | 2,4201e+07 | 2,411e+07 |
| 09.04.2002 10:20:00 | ,000000 | 2,38782e+07 | 2,4205e+07 | 2,41145e+07 |
| 09.04.2002 10:30:00 | ,000000 | 2,38841e+07 | 2,42104e+07 | 2,41203e+07 |
| 09.04.2002 10:40:00 | ,000000 | 2,38904e+07 | 2,42163e+07 | 2,41267e+07 |
| 09.04.2002 10:50:00 | ,000000 | 2,3894e+07 | 2,42194e+07 | 2,41303e+07 |
| 09.04.2002 11:00:00 | ,000000 | 2,39009e+07 | 2,42259e+07 | 2,41372e+07 |
| 09.04.2002 11:10:00 | ,000000 | 2,39074e+07 | 2,42319e+07 | 2,41437e+07 |
| 09.04.2002 11:20:00 | ,000000 | 2,39131e+07 | 2,42371e+07 | 2,41494e+07 |
| 09.04.2002 11:30:00 | ,000000 | 2,39193e+07 | 2,42428e+07 | 2,41555e+07 |
| 09.04.2002 11:40:00 | ,000000 | 2,39219e+07 | 2,42448e+07 | 2,41582e+07 |
| 09.04.2002 11:50:00 | ,000000 | 2,39266e+07 | 2,42491e+07 | 2,41629e+07 |
| 09.04.2002 12:00:00 | ,000000 | 2,39305e+07 | 2,42525e+07 | 2,41668e+07 |
| 09.04.2002 12:10:00 | ,000000 | 2,39382e+07 | 2,42597e+07 | 2,41745e+07 |
| 09.04.2002 12:20:00 | ,000000 | 2,39517e+07 | 2,4273e+07 | 2,41882e+07 |
| 09.04.2002 12:30:00 | ,000000 | 2,39617e+07 | 2,42826e+07 | 2,41982e+07 |
| 09.04.2002 12:40:00 | ,000000 | 2,39679e+07 | 2,42884e+07 | 2,42045e+07 |
| 09.04.2002 12:50:00 | ,000000 | 2,39724e+07 | 2,42924e+07 | 2,42088e+07 |
| 09.04.2002 13:00:00 | ,000000 | 2,39784e+07 | 2,42979e+07 | 2,42148e+07 |
| 09.04.2002 13:10:00 | ,000000 | 2,39811e+07 | 2,43001e+07 | 2,42174e+07 |
| 09.04.2002 13:20:00 | ,000000 | 2,39877e+07 | 2,43063e+07 | 2,42241e+07 |
| 09.04.2002 13:30:00 | ,000000 | 2,39927e+07 | 2,43107e+07 | 2,42289e+07 |
| 09.04.2002 13:40:00 | ,000000 | 2,40011e+07 | 2,43188e+07 | 2,42374e+07 |
| 09.04.2002 13:50:00 | ,000000 | 2,40066e+07 | 2,43238e+07 | 2,42429e+07 |
| 09.04.2002 14:00:00 | ,000000 | 2,40079e+07 | 2,43245e+07 | 2,42441e+07 |
| 09.04.2002 14:10:00 | ,000000 | 2,40092e+07 | 2,43254e+07 | 2,42453e+07 |
| 09.04.2002 14:20:00 | ,000000 | 2,40092e+07 | 2,43252e+07 | 2,42453e+07 |
| 09.04.2002 14:30:00 | ,000000 | 2,40106e+07 | 2,4326e+07 | 2,42466e+07 |
| 09.04.2002 14:40:00 | ,000000 | 2,40124e+07 | 2,43272e+07 | 2,42484e+07 |
| 09.04.2002 14:50:00 | ,000000 | 2,40125e+07 | 2,4327e+07 | 2,42485e+07 |
| 09.04.2002 15:00:00 | ,000000 | 2,40128e+07 | 2,43271e+07 | 2,42487e+07 |
| 09.04.2002 15:10:00 | ,000000 | 2,40137e+07 | 2,43277e+07 | 2,42496e+07 |
| 09.04.2002 15:20:00 | ,000000 | 2,40191e+07 | 2,43326e+07 | 2,42549e+07 |
| 09.04.2002 15:30:00 | ,000000 | 2,40214e+07 | 2,43342e+07 | 2,4257e+07 |
| 09.04.2002 15:40:00 | ,000000 | 2,40246e+07 | 2,43369e+07 | 2,42601e+07 |
| 09.04.2002 15:50:00 | ,000000 | 2,40275e+07 | 2,43392e+07 | 2,42629e+07 |
| 09.04.2002 16:00:00 | ,000000 | 2,40293e+07 | 2,43406e+07 | 2,42646e+07 |
| 09.04.2002 16:10:00 | ,000000 | 2,40319e+07 | 2,43428e+07 | 2,42672e+07 |
| 09.04.2002 16:20:00 | ,000000 | 2,40335e+07 | 2,4344e+07 | 2,42688e+07 |
| 09.04.2002 16:30:00 | ,000000 | 2,40344e+07 | 2,43447e+07 | 2,42696e+07 |
| 09.04.2002 16:40:00 | ,000000 | 2,40361e+07 | 2,43461e+07 | 2,42712e+07 |
| 09.04.2002 16:50:00 | ,000000 | 2,40375e+07 | 2,43471e+07 | 2,42725e+07 |
| 09.04.2002 17:00:00 | ,000000 | 2,40403e+07 | 2,43494e+07 | 2,42752e+07 |
| 09.04.2002 17:10:00 | ,000000 | 2,40431e+07 | 2,43517e+07 | 2,42779e+07 |
| 09.04.2002 17:20:00 | ,000000 | 2,40444e+07 | 2,43526e+07 | 2,42791e+07 |
| 09.04.2002 17:30:00 | ,000000 | 2,40476e+07 | 2,43554e+07 | 2,42823e+07 |
| 09.04.2002 17:40:00 | ,000000 | 2,40517e+07 | 2,43591e+07 | 2,42864e+07 |
| 09.04.2002 17:50:00 | ,000000 | 2,40524e+07 | 2,43592e+07 | 2,42869e+07 |
| 09.04.2002 18:00:00 | ,000000 | 2,40525e+07 | 2,43592e+07 | 2,42871e+07 |
| 09.04.2002 18:10:00 | ,000000 | 2,40547e+07 | 2,43609e+07 | 2,42892e+07 |
| 09.04.2002 18:20:00 | ,000000 | 2,40574e+07 | 2,43629e+07 | 2,42918e+07 |
| 09.04.2002 18:30:00 | ,000000 | 2,40594e+07 | 2,43642e+07 | 2,42937e+07 |
| 09.04.2002 18:40:00 | ,000000 | 2,40631e+07 | 2,43674e+07 | 2,42975e+07 |
| 09.04.2002 18:50:00 | ,000000 | 2,40693e+07 | 2,43731e+07 | 2,43037e+07 |
| 09.04.2002 19:00:00 | ,000000 | 2,40732e+07 | 2,43765e+07 | 2,43075e+07 |
| 09.04.2002 19:10:00 | ,000000 | 2,40792e+07 | 2,43821e+07 | 2,43136e+07 |
| 09.04.2002 19:20:00 | ,000000 | 2,4081e+07 | 2,43833e+07 | 2,43153e+07 |
| 09.04.2002 19:30:00 | ,000000 | 2,40837e+07 | 2,43855e+07 | 2,43179e+07 |
| 09.04.2002 19:40:00 | ,000000 | 2,40878e+07 | 2,43891e+07 | 2,4322e+07 |
| 09.04.2002 19:50:00 | ,000000 | 2,40918e+07 | 2,43925e+07 | 2,43259e+07 |
| 09.04.2002 20:00:00 | ,000000 | 2,40952e+07 | 2,43954e+07 | 2,43292e+07 |
| 09.04.2002 20:10:00 | ,000000 | 2,41006e+07 | 2,44004e+07 | 2,43346e+07 |
| 09.04.2002 20:20:00 | ,000000 | 2,41071e+07 | 2,44066e+07 | 2,4341e+07 |
| 09.04.2002 20:30:00 | ,000000 | 2,41136e+07 | 2,44127e+07 | 2,43475e+07 |
| 09.04.2002 20:40:00 | ,000000 | 2,41202e+07 | 2,4419e+07 | 2,43541e+07 |
| 09.04.2002 20:50:00 | ,000000 | 2,41274e+07 | 2,44259e+07 | 2,43613e+07 |
| 09.04.2002 21:00:00 | ,000000 | 2,41347e+07 | 2,44328e+07 | 2,43685e+07 |
| 09.04.2002 21:10:00 | ,000000 | 2,41437e+07 | 2,44415e+07 | 2,43775e+07 |
| 09.04.2002 21:20:00 | ,000000 | 2,41546e+07 | 2,44521e+07 | 2,43884e+07 |
| 09.04.2002 21:30:00 | ,000000 | 2,41705e+07 | 2,44679e+07 | 2,44045e+07 |
| 09.04.2002 21:40:00 | ,000000 | 2,41877e+07 | 2,44849e+07 | 2,44218e+07 |
| 09.04.2002 21:50:00 | ,000000 | 2,42064e+07 | 2,45037e+07 | 2,44407e+07 |
| 09.04.2002 22:00:00 | ,000000 | 2,42208e+07 | 2,45181e+07 | 2,44553e+07 |
| 09.04.2002 22:10:00 | ,000000 | 2,4231e+07 | 2,45282e+07 | 2,44656e+07 |
| 09.04.2002 22:20:00 | ,000000 | 2,42402e+07 | 2,45373e+07 | 2,44749e+07 |
| 09.04.2002 22:30:00 | ,000000 | 2,42492e+07 | 2,45462e+07 | 2,4484e+07 |
| 09.04.2002 22:40:00 | ,000000 | 2,42597e+07 | 2,45566e+07 | 2,44946e+07 |
| 09.04.2002 22:50:00 | ,000000 | 2,427e+07 | 2,45668e+07 | 2,4505e+07 |
| 09.04.2002 23:00:00 | ,000000 | 2,42814e+07 | 2,45782e+07 | 2,45166e+07 |
| 09.04.2002 23:10:00 | ,000000 | 2,42941e+07 | 2,4591e+07 | 2,45295e+07 |
| 09.04.2002 23:20:00 | ,000000 | 2,43064e+07 | 2,46033e+07 | 2,45419e+07 |
| 09.04.2002 23:30:00 | ,000000 | 2,43239e+07 | 2,4621e+07 | 2,45598e+07 |
| 09.04.2002 23:40:00 | ,000000 | 2,43383e+07 | 2,46355e+07 | 2,45744e+07 |
| 09.04.2002 23:50:00 | ,000000 | 2,43549e+07 | 2,46522e+07 | 2,45912e+07 |
| 10.04.2002 00:00:00 | ,000000 | 2,43719e+07 | 2,46694e+07 | 2,46085e+07 |
| 10.04.2002 00:10:00 | ,000000 | 2,43883e+07 | 2,46861e+07 | 2,46252e+07 |
| 10.04.2002 00:20:00 | ,000000 | 2,44066e+07 | 2,47047e+07 | 2,46438e+07 |
| 10.04.2002 00:30:00 | ,000000 | 2,44379e+07 | 2,47365e+07 | 2,46754e+07 |
| 10.04.2002 00:40:00 | ,000000 | 2,44644e+07 | 2,47636e+07 | 2,47022e+07 |
| 10.04.2002 00:50:00 | ,000000 | 2,4487e+07 | 2,47867e+07 | 2,47252e+07 |
| 10.04.2002 01:00:00 | ,000000 | 2,45099e+07 | 2,481e+07 | 2,47485e+07 |
| 10.04.2002 01:10:00 | ,000000 | 2,45349e+07 | 2,48354e+07 | 2,47738e+07 |
| 10.04.2002 01:20:00 | ,000000 | 2,45706e+07 | 2,48719e+07 | 2,48101e+07 |
| 10.04.2002 01:30:00 | ,000000 | 2,46213e+07 | 2,49236e+07 | 2,48615e+07 |
| 10.04.2002 01:40:00 | ,000000 | 2,46668e+07 | 2,497e+07 | 2,49077e+07 |
| 10.04.2002 01:50:00 | ,000000 | 2,47083e+07 | 2,50123e+07 | 2,49498e+07 |
| 10.04.2002 02:00:00 | ,000000 | 2,47564e+07 | 2,50613e+07 | 2,49986e+07 |
| 10.04.2002 02:10:00 | ,000000 | 2,48055e+07 | 2,51113e+07 | 2,50484e+07 |
| 10.04.2002 02:20:00 | ,000000 | 2,48624e+07 | 2,51694e+07 | 2,51062e+07 |
| 10.04.2002 02:30:00 | ,000000 | 2,49259e+07 | 2,52342e+07 | 2,51707e+07 |
| 10.04.2002 02:40:00 | ,000000 | 2,49761e+07 | 2,52853e+07 | 2,52216e+07 |
| 10.04.2002 02:50:00 | ,000000 | 2,5021e+07 | 2,53311e+07 | 2,52672e+07 |
| 10.04.2002 03:00:00 | ,000000 | 2,50698e+07 | 2,53808e+07 | 2,53166e+07 |
| 10.04.2002 03:10:00 | ,000000 | 2,51176e+07 | 2,54296e+07 | 2,53652e+07 |
| 10.04.2002 03:20:00 | ,000000 | 2,51659e+07 | 2,54789e+07 | 2,54142e+07 |
| 10.04.2002 03:30:00 | ,000000 | 2,5219e+07 | 2,55331e+07 | 2,54681e+07 |
| 10.04.2002 03:40:00 | ,000000 | 2,52651e+07 | 2,55803e+07 | 2,5515e+07 |
| 10.04.2002 03:50:00 | ,000000 | 2,5307e+07 | 2,5623e+07 | 2,55575e+07 |
| 10.04.2002 04:00:00 | ,000000 | 2,53395e+07 | 2,56562e+07 | 2,55905e+07 |
| 10.04.2002 04:10:00 | ,000000 | 2,53627e+07 | 2,56798e+07 | 2,56141e+07 |
| 10.04.2002 04:20:00 | ,000000 | 2,53977e+07 | 2,57157e+07 | 2,56497e+07 |
| 10.04.2002 04:30:00 | ,000000 | 2,54279e+07 | 2,57466e+07 | 2,56803e+07 |
| 10.04.2002 04:40:00 | ,000000 | 2,54633e+07 | 2,57829e+07 | 2,57162e+07 |
| 10.04.2002 04:50:00 | ,000000 | 2,55132e+07 | 2,5834e+07 | 2,57669e+07 |
| 10.04.2002 05:00:00 | ,000000 | 2,55811e+07 | 2,59035e+07 | 2,58356e+07 |
| 10.04.2002 05:10:00 | ,000000 | 2,56623e+07 | 2,59864e+07 | 2,59176e+07 |
| 10.04.2002 05:20:00 | ,000000 | 2,57426e+07 | 2,60684e+07 | 2,59988e+07 |
| 10.04.2002 05:30:00 | ,000000 | 2,58242e+07 | 2,61518e+07 | 2,60813e+07 |
| 10.04.2002 05:40:00 | ,000000 | 2,59055e+07 | 2,62348e+07 | 2,61635e+07 |
| 10.04.2002 05:50:00 | ,000000 | 2,59872e+07 | 2,63183e+07 | 2,62461e+07 |
| 10.04.2002 06:00:00 | ,000000 | 2,60667e+07 | 2,63993e+07 | 2,63265e+07 |
| 10.04.2002 06:10:00 | ,000000 | 2,61396e+07 | 2,64737e+07 | 2,64002e+07 |
| 10.04.2002 06:20:00 | ,000000 | 2,62077e+07 | 2,6543e+07 | 2,64691e+07 |
| 10.04.2002 06:30:00 | ,000000 | 2,62432e+07 | 2,65791e+07 | 2,6505e+07 |
| 10.04.2002 06:40:00 | ,000000 | 2,62825e+07 | 2,6619e+07 | 2,65447e+07 |
| 10.04.2002 06:50:00 | ,000000 | 2,63162e+07 | 2,66531e+07 | 2,65787e+07 |
| 10.04.2002 07:00:00 | ,000000 | 2,63477e+07 | 2,66851e+07 | 2,66106e+07 |
| 10.04.2002 07:10:00 | ,000000 | 2,63936e+07 | 2,67317e+07 | 2,6657e+07 |
| 10.04.2002 07:20:00 | ,000000 | 2,64479e+07 | 2,67871e+07 | 2,6712e+07 |
| 10.04.2002 07:30:00 | ,000000 | 2,65289e+07 | 2,68696e+07 | 2,67938e+07 |
| 10.04.2002 07:40:00 | ,000000 | 2,66111e+07 | 2,69534e+07 | 2,68768e+07 |
| 10.04.2002 07:50:00 | ,000000 | 2,66932e+07 | 2,70371e+07 | 2,69598e+07 |
| 10.04.2002 08:00:00 | ,000000 | 2,67756e+07 | 2,71211e+07 | 2,7043e+07 |
| 10.04.2002 08:10:00 | ,000000 | 2,68578e+07 | 2,72049e+07 | 2,7126e+07 |
| 10.04.2002 08:20:00 | ,000000 | 2,69401e+07 | 2,72888e+07 | 2,7209e+07 |
| 10.04.2002 08:30:00 | ,000000 | 2,70224e+07 | 2,73725e+07 | 2,7292e+07 |
| 10.04.2002 08:40:00 | ,000000 | 2,71046e+07 | 2,74563e+07 | 2,73750e+07 |
| 10.04.2002 08:50:00 | ,000000 | 2,7187e+07 | 2,75402e+07 | 2,74581e+07 |
| 10.04.2002 09:00:00 | ,000000 | 2,72691e+07 | 2,76238e+07 | 2,7541e+07 |
| 10.04.2002 09:10:00 | ,000000 | 2,73482e+07 | 2,77043e+07 | 2,76208e+07 |
| 10.04.2002 09:20:00 | ,000000 | 2,74145e+07 | 2,77717e+07 | 2,76878e+07 |
| 10.04.2002 09:30:00 | ,000000 | 2,74857e+07 | 2,78441e+07 | 2,77597e+07 |
| 10.04.2002 09:40:00 | ,000000 | 2,75479e+07 | 2,79072e+07 | 2,78225e+07 |
| 10.04.2002 09:50:00 | ,000000 | 2,75972e+07 | 2,79573e+07 | 2,78723e+07 |
| 10.04.2002 10:00:00 | ,000000 | 2,76289e+07 | 2,79891e+07 | 2,79041e+07 |
| 10.04.2002 10:10:00 | ,000000 | 2,76522e+07 | 2,80125e+07 | 2,79276e+07 |
| 10.04.2002 10:20:00 | ,000000 | 2,76799e+07 | 2,80402e+07 | 2,79554e+07 |
| 10.04.2002 10:30:00 | ,000000 | 2,77068e+07 | 2,80672e+07 | 2,79825e+07 |
| 10.04.2002 10:40:00 | ,000000 | 2,77255e+07 | 2,80856e+07 | 2,80012e+07 |
| 10.04.2002 10:50:00 | ,000000 | 2,77516e+07 | 2,81118e+07 | 2,80275e+07 |
| 10.04.2002 11:00:00 | ,000000 | 2,77766e+07 | 2,81367e+07 | 2,80526e+07 |
| 10.04.2002 11:10:00 | ,000000 | 2,77809e+07 | 2,8141e+07 | 2,8057e+07 |
| 10.04.2002 11:20:00 | ,000000 | 2,77888e+07 | 2,8149e+07 | 2,80649e+07 |
| 10.04.2002 11:30:00 | ,000000 | 2,78072e+07 | 2,81672e+07 | 2,80834e+07 |
| 10.04.2002 11:40:00 | ,000000 | 2,7821e+07 | 2,81806e+07 | 2,80972e+07 |
| 10.04.2002 11:50:00 | ,000000 | 2,78359e+07 | 2,81952e+07 | 2,8112e+07 |
| 10.04.2002 12:00:00 | ,000000 | 2,78491e+07 | 2,82079e+07 | 2,81251e+07 |
| 10.04.2002 12:10:00 | ,000000 | 2,78606e+07 | 2,8219e+07 | 2,81365e+07 |
| 10.04.2002 12:20:00 | ,000000 | 2,78663e+07 | 2,82242e+07 | 2,81421e+07 |
| 10.04.2002 12:30:00 | ,000000 | 2,78743e+07 | 2,82316e+07 | 2,815e+07 |
| 10.04.2002 12:40:00 | ,000000 | 2,78802e+07 | 2,8237e+07 | 2,81557e+07 |
| 10.04.2002 12:50:00 | ,000000 | 2,78868e+07 | 2,8243e+07 | 2,81622e+07 |
| 10.04.2002 13:00:00 | ,000000 | 2,78965e+07 | 2,82522e+07 | 2,81718e+07 |
| 10.04.2002 13:10:00 | ,000000 | 2,79044e+07 | 2,82594e+07 | 2,81795e+07 |
| 10.04.2002 13:20:00 | ,000000 | 2,79106e+07 | 2,82651e+07 | 2,81856e+07 |
| 10.04.2002 13:30:00 | ,000000 | 2,79216e+07 | 2,82755e+07 | 2,81964e+07 |
| 10.04.2002 13:40:00 | ,000000 | 2,79258e+07 | 2,82791e+07 | 2,82005e+07 |
| 10.04.2002 13:50:00 | ,000000 | 2,79336e+07 | 2,82863e+07 | 2,82081e+07 |
| 10.04.2002 14:00:00 | ,000000 | 2,79411e+07 | 2,82933e+07 | 2,82155e+07 |
| 10.04.2002 14:10:00 | ,000000 | 2,79487e+07 | 2,83003e+07 | 2,82229e+07 |
| 10.04.2002 14:20:00 | ,000000 | 2,79576e+07 | 2,83086e+07 | 2,82316e+07 |
| 10.04.2002 14:30:00 | ,000000 | 2,79705e+07 | 2,83211e+07 | 2,82445e+07 |
| 10.04.2002 14:40:00 | ,000000 | 2,79799e+07 | 2,833e+07 | 2,82538e+07 |
| 10.04.2002 14:50:00 | ,000000 | 2,79856e+07 | 2,8335e+07 | 2,82592e+07 |
| 10.04.2002 15:00:00 | ,000000 | 2,79941e+07 | 2,83428e+07 | 2,82675e+07 |
| 10.04.2002 15:10:00 | ,000000 | 2,80002e+07 | 2,83482e+07 | 2,82734e+07 |
| 10.04.2002 15:20:00 | ,000000 | 2,80089e+07 | 2,83564e+07 | 2,8282e+07 |
| 10.04.2002 15:30:00 | ,000000 | 2,80182e+07 | 2,83652e+07 | 2,82911e+07 |
| 10.04.2002 15:40:00 | ,000000 | 2,80271e+07 | 2,83735e+07 | 2,82999e+07 |
| 10.04.2002 15:50:00 | ,000000 | 2,80322e+07 | 2,83779e+07 | 2,83047e+07 |
| 10.04.2002 16:00:00 | ,000000 | 2,80375e+07 | 2,83825e+07 | 2,83098e+07 |
| 10.04.2002 16:10:00 | ,000000 | 2,80433e+07 | 2,83877e+07 | 2,83154e+07 |
| 10.04.2002 16:20:00 | ,000000 | 2,80463e+07 | 2,839e+07 | 2,83181e+07 |
| 10.04.2002 16:30:00 | ,000000 | 2,80549e+07 | 2,83981e+07 | 2,83266e+07 |
| 10.04.2002 16:40:00 | ,000000 | 2,80648e+07 | 2,84076e+07 | 2,83363e+07 |
| 10.04.2002 16:50:00 | ,000000 | 2,80756e+07 | 2,84179e+07 | 2,8347e+07 |
| 10.04.2002 17:00:00 | ,000000 | 2,8089e+07 | 2,84309e+07 | 2,83603e+07 |
| 10.04.2002 17:10:00 | ,000000 | 2,81004e+07 | 2,84417e+07 | 2,83715e+07 |
| 10.04.2002 17:20:00 | ,000000 | 2,81103e+07 | 2,84512e+07 | 2,83812e+07 |
| 10.04.2002 17:30:00 | ,000000 | 2,81176e+07 | 2,84581e+07 | 2,83883e+07 |
| 10.04.2002 17:40:00 | ,000000 | 2,81298e+07 | 2,84699e+07 | 2,84004e+07 |
| 10.04.2002 17:50:00 | ,000000 | 2,81466e+07 | 2,84866e+07 | 2,84172e+07 |
| 10.04.2002 18:00:00 | ,000000 | 2,81631e+07 | 2,8503e+07 | 2,84337e+07 |
| 10.04.2002 18:10:00 | ,000000 | 2,81816e+07 | 2,85213e+07 | 2,84522e+07 |
| 10.04.2002 18:20:00 | ,000000 | 2,82029e+07 | 2,85426e+07 | 2,84735e+07 |
| 10.04.2002 18:30:00 | ,000000 | 2,8224e+07 | 2,85637e+07 | 2,84946e+07 |
| 10.04.2002 18:40:00 | ,000000 | 2,82507e+07 | 2,85905e+07 | 2,85215e+07 |
| 10.04.2002 18:50:00 | ,000000 | 2,82875e+07 | 2,86276e+07 | 2,85585e+07 |
| 10.04.2002 19:00:00 | ,000000 | 2,83261e+07 | 2,86667e+07 | 2,85974e+07 |
| 10.04.2002 19:10:00 | ,000000 | 2,83598e+07 | 2,87007e+07 | 2,86313e+07 |
| 10.04.2002 19:20:00 | ,000000 | 2,83883e+07 | 2,87295e+07 | 2,86601e+07 |
| 10.04.2002 19:30:00 | ,000000 | 2,84169e+07 | 2,87584e+07 | 2,86888e+07 |
| 10.04.2002 19:40:00 | ,000000 | 2,84568e+07 | 2,87987e+07 | 2,8729e+07 |
| 10.04.2002 19:50:00 | ,000000 | 2,85044e+07 | 2,8847e+07 | 2,8777e+07 |
| 10.04.2002 20:00:00 | ,000000 | 2,85673e+07 | 2,89108e+07 | 2,88404e+07 |
| 10.04.2002 20:10:00 | ,000000 | 2,8628e+07 | 2,89725e+07 | 2,89016e+07 |
| 10.04.2002 20:20:00 | ,000000 | 2,86915e+07 | 2,9037e+07 | 2,89656e+07 |
| 10.04.2002 20:30:00 | ,000000 | 2,87584e+07 | 2,91051e+07 | 2,9033e+07 |
| 10.04.2002 20:40:00 | ,000000 | 2,88343e+07 | 2,91826e+07 | 2,91096e+07 |
| 10.04.2002 20:50:00 | ,000000 | 2,89086e+07 | 2,92583e+07 | 2,91844e+07 |
| 10.04.2002 21:00:00 | ,000000 | 2,89821e+07 | 2,93334e+07 | 2,92585e+07 |
| 10.04.2002 21:10:00 | ,000000 | 2,90489e+07 | 2,94017e+07 | 2,9326e+07 |
| 10.04.2002 21:20:00 | ,000000 | 2,91221e+07 | 2,94766e+07 | 2,93998e+07 |
| 10.04.2002 21:30:00 | ,000000 | 2,92027e+07 | 2,95589e+07 | 2,9481e+07 |
| 10.04.2002 21:40:00 | ,000000 | 2,92849e+07 | 2,96429e+07 | 2,9564e+07 |
| 10.04.2002 21:50:00 | ,000000 | 2,93671e+07 | 2,9727e+07 | 2,96469e+07 |
| 10.04.2002 22:00:00 | ,000000 | 2,94493e+07 | 2,98111e+07 | 2,97298e+07 |
| 10.04.2002 22:10:00 | ,000000 | 2,95316e+07 | 2,98952e+07 | 2,98128e+07 |
| 10.04.2002 22:20:00 | ,000000 | 2,96139e+07 | 2,99794e+07 | 2,98959e+07 |
| 10.04.2002 22:30:00 | ,000000 | 2,96961e+07 | 3,00636e+07 | 2,99788e+07 |
| 10.04.2002 22:40:00 | ,000000 | 2,97783e+07 | 3,01478e+07 | 3,00617e+07 |
| 10.04.2002 22:50:00 | ,000000 | 2,98604e+07 | 3,02319e+07 | 3,01446e+07 |
| 10.04.2002 23:00:00 | ,000000 | 2,99426e+07 | 3,03162e+07 | 3,02276e+07 |
| 10.04.2002 23:10:00 | ,000000 | 3,00246e+07 | 3,04003e+07 | 3,03105e+07 |
| 10.04.2002 23:20:00 | ,000000 | 3,01068e+07 | 3,04846e+07 | 3,03934e+07 |
| 10.04.2002 23:30:00 | ,000000 | 3,01889e+07 | 3,05688e+07 | 3,04764e+07 |
| 10.04.2002 23:40:00 | ,000000 | 3,02711e+07 | 3,0653e+07 | 3,05594e+07 |
| 10.04.2002 23:50:00 | ,000000 | 3,03533e+07 | 3,07372e+07 | 3,06423e+07 |
| 11.04.2002 00:00:00 | ,000000 | 3,04355e+07 | 3,08214e+07 | 3,07252e+07 |
| 11.04.2002 00:10:00 | ,000000 | 3,05178e+07 | 3,09058e+07 | 3,08083e+07 |
| 11.04.2002 00:20:00 | ,000000 | 3,06001e+07 | 3,09901e+07 | 3,08913e+07 |
| 11.04.2002 00:30:00 | ,000000 | 3,06824e+07 | 3,10744e+07 | 3,09743e+07 |
| 11.04.2002 00:40:00 | ,000000 | 3,07647e+07 | 3,11587e+07 | 3,10573e+07 |
| 11.04.2002 00:50:00 | ,000000 | 3,08469e+07 | 3,1243e+07 | 3,11403e+07 |
| 11.04.2002 01:00:00 | ,000000 | 3,09291e+07 | 3,13272e+07 | 3,12233e+07 |
| 11.04.2002 01:10:00 | ,000000 | 3,10113e+07 | 3,14114e+07 | 3,13063e+07 |
| 11.04.2002 01:20:00 | ,000000 | 3,10935e+07 | 3,14956e+07 | 3,13892e+07 |
| 11.04.2002 01:30:00 | ,000000 | 3,11756e+07 | 3,15798e+07 | 3,14722e+07 |
| 11.04.2002 01:40:00 | ,000000 | 3,12578e+07 | 3,16641e+07 | 3,15551e+07 |
| 11.04.2002 01:50:00 | ,000000 | 3,13399e+07 | 3,17482e+07 | 3,16381e+07 |
| 11.04.2002 02:00:00 | ,000000 | 3,14221e+07 | 3,18325e+07 | 3,17211e+07 |
| 11.04.2002 02:10:00 | ,000000 | 3,15043e+07 | 3,19167e+07 | 3,1804e+07 |
| 11.04.2002 02:20:00 | ,000000 | 3,15864e+07 | 3,20008e+07 | 3,1887e+07 |
| 11.04.2002 02:30:00 | ,000000 | 3,16686e+07 | 3,20851e+07 | 3,197e+07 |
| 11.04.2002 02:40:00 | ,000000 | 3,17508e+07 | 3,21693e+07 | 3,20531e+07 |
| 11.04.2002 02:50:00 | ,000000 | 3,1833e+07 | 3,22535e+07 | 3,21361e+07 |
| 11.04.2002 03:00:00 | ,000000 | 3,19152e+07 | 3,23377e+07 | 3,22191e+07 |
| 11.04.2002 03:10:00 | ,000000 | 3,19974e+07 | 3,24219e+07 | 3,23021e+07 |
| 11.04.2002 03:20:00 | ,000000 | 3,20795e+07 | 3,25061e+07 | 3,23851e+07 |
| 11.04.2002 03:30:00 | ,000000 | 3,21618e+07 | 3,25904e+07 | 3,24682e+07 |
| 11.04.2002 03:40:00 | ,000000 | 3,22441e+07 | 3,26747e+07 | 3,25513e+07 |
| 11.04.2002 03:50:00 | ,000000 | 3,23263e+07 | 3,27589e+07 | 3,26343e+07 |
| 11.04.2002 04:00:00 | ,000000 | 3,24086e+07 | 3,28432e+07 | 3,27174e+07 |
| 11.04.2002 04:10:00 | ,000000 | 3,24908e+07 | 3,29275e+07 | 3,28005e+07 |
| 11.04.2002 04:20:00 | ,000000 | 3,25731e+07 | 3,30118e+07 | 3,28835e+07 |
| 11.04.2002 04:30:00 | ,000000 | 3,26553e+07 | 3,3096e+07 | 3,29666e+07 |
| 11.04.2002 04:40:00 | ,000000 | 3,27375e+07 | 3,31803e+07 | 3,30496e+07 |
| 11.04.2002 04:50:00 | ,000000 | 3,28198e+07 | 3,32645e+07 | 3,31326e+07 |
| 11.04.2002 05:00:00 | ,000000 | 3,29021e+07 | 3,33487e+07 | 3,32158e+07 |
| 11.04.2002 05:10:00 | ,000000 | 3,29845e+07 | 3,34330e+07 | 3,32989e+07 |
| 11.04.2002 05:20:00 | ,000000 | 3,30666e+07 | 3,35172e+07 | 3,33819e+07 |
| 11.04.2002 05:30:00 | ,000000 | 3,3149e+07 | 3,36015e+07 | 3,34651e+07 |
| 11.04.2002 05:40:00 | ,000000 | 3,32312e+07 | 3,36857e+07 | 3,35481e+07 |
| 11.04.2002 05:50:00 | ,000000 | 3,33133e+07 | 3,37698e+07 | 3,36311e+07 |
| 11.04.2002 06:00:00 | ,000000 | 3,33956e+07 | 3,3854e+07 | 3,37141e+07 |
| 11.04.2002 06:10:00 | ,000000 | 3,34781e+07 | 3,39382e+07 | 3,37973e+07 |
| 11.04.2002 06:20:00 | ,000000 | 3,35604e+07 | 3,40224e+07 | 3,38804e+07 |
| 11.04.2002 06:30:00 | ,000000 | 3,36428e+07 | 3,41066e+07 | 3,39635e+07 |
| 11.04.2002 06:40:00 | ,000000 | 3,37252e+07 | 3,41908e+07 | 3,40466e+07 |
| 11.04.2002 06:50:00 | ,000000 | 3,38075e+07 | 3,42748e+07 | 3,41296e+07 |
| 11.04.2002 07:00:00 | ,000000 | 3,38897e+07 | 3,4359e+07 | 3,42127e+07 |
| 11.04.2002 07:10:00 | ,000000 | 3,39719e+07 | 3,4443e+07 | 3,42957e+07 |
| 11.04.2002 07:20:00 | ,000000 | 3,40541e+07 | 3,4527e+07 | 3,43787e+07 |
| 11.04.2002 07:30:00 | ,000000 | 3,41363e+07 | 3,4611e+07 | 3,44617e+07 |
| 11.04.2002 07:40:00 | ,000000 | 3,42186e+07 | 3,46951e+07 | 3,45447e+07 |
| 11.04.2002 07:50:00 | ,000000 | 3,43009e+07 | 3,47791e+07 | 3,46277e+07 |
| 11.04.2002 08:00:00 | ,000000 | 3,43832e+07 | 3,48632e+07 | 3,47108e+07 |
| 11.04.2002 08:10:00 | ,000000 | 3,44655e+07 | 3,49473e+07 | 3,47938e+07 |
| 11.04.2002 08:20:00 | ,000000 | 3,45477e+07 | 3,50313e+07 | 3,48767e+07 |
| 11.04.2002 08:30:00 | ,000000 | 3,46299e+07 | 3,51154e+07 | 3,49596e+07 |
| 11.04.2002 08:40:00 | ,000000 | 3,47121e+07 | 3,51994e+07 | 3,50426e+07 |
| 11.04.2002 08:50:00 | ,000000 | 3,47944e+07 | 3,52835e+07 | 3,51256e+07 |
| 11.04.2002 09:00:00 | ,000000 | 3,48766e+07 | 3,53677e+07 | 3,52086e+07 |
| 11.04.2002 09:10:00 | ,000000 | 3,4959e+07 | 3,54519e+07 | 3,52916e+07 |