## Slide 1
8/8/01
1
S. Motzko
BAAQMD Generator Rules
August 8, 2001
Update
Notes: 1

## Slide 2
8/8/01
2
S. Motzko
With the current energy crisis in California, many people are looking toward emergency generators to help their businesses cope with the potential of rolling blackouts.
A clean diesel emergency generator emits more than 20 times as much NOx as a new well-controlled power plant.
Diesel particulate has been identified as a toxic air contaminant with a potency that results in cancer risks from engines operated for as little as 30 hours per year.
BAAQMD Rule Management Summary
Notes: 3

## Slide 3
8/8/01
3
S. Motzko
Emergency standby engines have been exempt from permitting as an emissions source only if used for 100 hours or less testing and 200 hours or less of emergency use per year.
There is a new BAAQMD regulation (August 1, 2001) where the permit exemption will be eliminated for standby engines of 50HP and greater.
Mobile sources are not addressed by BAAQMD, provided they are at a location less than 72 consecutive hours, but fall under the state of California rules (CARB).
Background - Diesel Standby Generators
BAAQMD Generator Proposal
Notes: 2

## Slide 4
8/8/01
4
S. Motzko
Proposed Regulation was approved (Passed 13 to 4) at the BAAQMD board meeting on Wednesday, August 1, 2001.
The regulation is effective August 1, 2001 and the permitting process will be announced in a letter to those thought to possibly have generators.
Lists used for the notification of permitting include:
  permit holders of diesel storage tanks (from CUPAs)
  facilities with BAAQMD permits
  trade organizations
  also working with engine suppliers
Operators will be required to submit applications within 90 days of being contacted by BAAQMD.
BAAQMD Generator Rules Timing
Notes: 3

## Slide 5
8/8/01
5
S. Motzko
Permit required for existing and new engines > 50hp
A limit of 100 hours/year for testing, maintenance and “reliability” (which could include bridging time between announced and actual blackout); 200 hours for Essential Public Service
Unlimited run time during actual power outage “emergencies”
  Emergency is now defined as rolling blackout at your facility.
Existing sources would be exempt from New Source Review
  To meet existing criteria, they must be on-site before 8/1/01.
  New and replacement engines subject to risk management criteria based on characteristics of engine and installation analysis (BAAQMD).
Sources installed on or after May 17, 2000 would be subject to existing risk management policies.
BAAQMD Generator Proposal
Notes: 4

## Slide 6
8/8/01
6
S. Motzko
BAAQMD will send out letters notifying the need for permits within three months of adoption of the amendments.
Loss of exemption (existing generators) permits will be processed and issued automatically.
New source review permits (including replacement generators) will be reviewed by a team of permit engineers.
  Must meet BACT combustion control (NOx & Particulate Emmissions)
The proposed cost of the permits (to be revisited):
  $120/year annual fee for small engine
  ~$550 for replacement or new engine permit/application
Standby Generator Application Instructions Online
<http://www.baaqmd.gov/permit/standby.htm>
BAAQMD Generator Permit Process
Notes: 3

## Slide 7
8/8/01
7
S. Motzko
Non-resettable totalizing meter that measures hours of operation required.
Records must be kept for at least 2 years and must be available for inspection by BAAQMD staff upon request.
Monthly log of usage shall include:
  Hours of operation (total)
  Hours of operation (emergency)
  For each emergency, the nature of the emergency condition
BAAQMD Monitoring Requirements
Notes: 3

## Slide 8
8/8/01
8
S. Motzko
This option in the original proposal allowed conversion of emergency generators to discretionary use, provided certain criteria were met.
This option in the original proposal was eliminated.
Generators for discretionary (non-standby emergency) use will now go through the normal process with risk assessmment process and resulting use limitations.
BAAQMD Generator Conversion
Notes: 3